## CCT Codes Comparison Import ON
Code Year | Province/Territory | Code Book | National Division | National Sentence Number | National Article Title | National Sentence Text | P/T Document | P/T Division | P/T Sentence Number | P/T Article Title | P/T Sentence Text | Text Difference Tracked | Difference Type | Variation | Variation Label | Exception | Comments | Difference Type Updated | Exception Updated | Variation Updated
2015 | ON | NBC | Div B | 1.1.1.1.(1) | 1.1.1.1. Application | This Part applies to all buildings covered in this Code. (See Article 1.1.1.1..) | obc2019_divb | Div B | 1.1.1.1.(1) | 1.1.1.1. Application | This Part applies to all buildings covered in this Code. |  | Common Sentence | No
2015 | ON | NBC | Div B | 1.1.3.1.(1) | 1.1.3.1. Climatic and Seismic Values | The climatic and seismic values required for the design of buildings under this Code shall be in conformance with the values established by the authority having jurisdiction or, in the absence of such data, with Sentence 1.1.3.1.(2) and the climatic and seismic values in Appendix C . (See Note A-1.1.3.1.(1).) | obc2019_divb | Div B | 1.1.2.1.(1) | 1.1.2.1. Climatic and Seismic Values | The climatic and seismic values required for the design of buildings under this Code shall be in conformance with the values established by the climatic and seismic values provided in MMAH Supplementary Standard SB-1, "Climatic and Seismic Data". |  | Common Sentence | Yes
2015 | ON | NBC | Div B | 1.1.3.1.(2) | 1.1.3.1. Climatic and Seismic Values | The outside winter design temperatures determined from Appendix C shall be those listed for the January 2.5% values. (See Note A-1.1.3.1.(2).) | obc2019_divb | Div B | 1.1.2.1.(2) | 1.1.2.1. Climatic and Seismic Values | The outside winter design temperatures determined from MMAH Supplementary Standard SB-1, "Climatic and Seismic Data", shall be those listed for the January 2.5% values. (SeeAppendix A.)) |  | Common Sentence | Yes
2015 | ON | NBC | Div B | 1.3.1.2.(1) | 1.3.1.2 Applicable Editions | Where documents are referenced in this Code, they shall be the editions designated in Table 1.3.1.2. | obc2019_divb | Div B | 1.3.1.2.(1) | 1.3.1.1. Applicable Editions | Where documents are referenced in this Code, they shall be the editions designated in Column 2 of Table 1.3.1.2. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.1.1.(1) | Scope | The scope of this Part shall be as described in Subsection 1.3.3. of Division A. | obc2019_divb | Div B | 3.1.1.1.(1) | 3.1.1.1. Scope | The scope of this Part shall be as described in Subsection 1.1.2. of Division A. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.10.1.(1) | Prevention of Firewall Collapse | Except as permitted by Sentence 3.1.10.1.(2), the connections and supports for structural framing members that are connected to or supported on a firewall and have a fire-resistance rating less than that required for the firewall, shall be designed so that the failure of the framing systems during a fire will not affect the integrity of the firewall during the fire. | obc2019_divb | Div B | 3.1.10.1.(1) | 3.1.10.1. Prevention of Firewall Collapse | Except as permitted by Sentence (2), the connections and supports for structural framing members that are connected to or supported on a firewall and have a fire-resistance rating less than that required for the firewall, shall be designed so that the failure of the framing systems during a fire will not affect the integrity of the firewall during the fire. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.10.1.(2) | Prevention of Firewall Collapse | Sentence 3.1.10.1.(1) does not apply to a firewall consisting of two separate wall assemblies each tied to its respective building frame but not to each other, provided each wall assembly is a fire separation having one half of the fire-resistance rating required for the firewall by Sentences 3.1.10.2.(1) and 3.1.10.2.(2), and designed so that the collapse of one wall assembly will not cause collapse of the other. | obc2019_divb | Div B | 3.1.10.1.(2) | 3.1.10.1. Prevention of Firewall Collapse | Sentence (1) does not apply to a firewall consisting of two separate wall assemblies each tied to its respective building frame but not to each other, provided each wall assembly is, a fire separation having one-half of the fire-resistance rating required for the firewall by Sentences 3.1.10.2.(1) and (2), and designed so that the collapse of one wall assembly will not cause the collapse of the other. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.10.1.(3) | Prevention of Firewall Collapse | A firewall is permitted to be supported on the structural frame of a building of noncombustible construction provided the supporting frame has a fire-resistance rating not less than that required for the firewall. | obc2019_divb | Div B | 3.1.10.1.(3) | 3.1.10.1. Prevention of Firewall Collapse | A firewall is permitted to be supported on the structural frame of a building of noncombustible construction provided the supporting frame has a fire-resistance rating not less than that required for the firewall. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.10.1.(4) | Prevention of Firewall Collapse | Piping, ducts and totally enclosed noncombustible raceways shall be installed so that their collapse will not cause collapse of the firewall. | obc2019_divb | Div B | 3.1.10.1.(4) | 3.1.10.1. Prevention of Firewall Collapse | Piping, ducts and totally enclosed noncombustible raceways shall be installed so that their collapse will not cause the collapse of the firewall. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.10.2.(1) | Rating of Firewalls | A firewall that separates a building or buildings with floor areas containing a Group E or a Group F, Division 1 or 2 major occupancy shall be constructed as a fire separation of noncombustible construction having a fire-resistance rating not less than 4 h, except that where the upper portion of a firewall separates floor areas containing other than Group E or Group F, Division 1 or 2 major occupancies, the fire-resistance rating of the upper portion of the firewall is permitted to be not less than 2 h. | obc2019_divb | Div B | 3.1.10.2.(1) | 3.1.10.2. Rating of Firewalls | A firewall that separates a building or buildings with floor areas containing a Group E or a Group F, Division 1 or 2 major occupancy shall be constructed as a fire separation of noncombustible construction having a fire-resistance rating not less than 4 h, except that where the upper portion of a firewall separates floor areas containing other than Group E or Group F, Division 1 or 2 major occupancies, the fire-resistance rating of the upper portion of the firewall is permitted to be not less than 2 h. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.10.2.(2) | Rating of Firewalls | A firewall that separates a building or buildings with floor areas containing major occupancies other than Group E or Group F, Division 1 or 2 shall be constructed as a fire separation of noncombustible construction having a fire-resistance rating not less than 2 h. | obc2019_divb | Div B | 3.1.10.2.(2) | 3.1.10.2. Rating of Firewalls | A firewall that separates a building or buildings with floor areas containing major occupancies other than Group E or Group F, Division 1 or 2 shall be constructed as a fire separation of noncombustible construction having a fire-resistance rating not less than 2 h. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.10.2.(3) | Rating of Firewalls | Except as permitted by Sentence 3.1.10.2.(4), the required fire-resistance rating of a firewall, except for closures, shall be provided by masonry or concrete. | obc2019_divb | Div B | 3.1.10.2.(3) | 3.1.10.2. Rating of Firewalls | Except as permitted by Sentence (4), the required fire-resistance rating of a firewall, except for closures, shall be provided by masonry or concrete. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.10.2.(4) | Rating of Firewalls | A firewall permitted to have a fire-resistance rating not more than 2 h need not be constructed of masonry or concrete, provided (a) the assembly providing the fire-resistance rating is protected against damage that would compromise the integrity of the assembly, and (b) the design conforms to Article 4.1.5.17. (See Note A-3.1.10.2.(4).) | obc2019_divb | Div B | 3.1.10.2.(4) | 3.1.10.2. Rating of Firewalls | A firewall permitted to have a fire-resistance rating not more than 2 h need not be constructed of masonry or concrete provided, the assembly providing the fire-resistance rating is protected against damage that would compromise the integrity of the assembly, the design conforms to Article 4.1.5.17., the level of performance of the firewall is not less than of masonry or concrete in the areas of, performance during fire conditions, mechanical damage during the normal use of the building, and resistance to damage from moisture, the firewall separates buildings or buildings with floor areas that do not contain, a Group B, Division 1 major occupancy, or a Group B, Division 2 major occupancy, and the firewall does not separate a building regulated by the provisions of Subsection 3.2.6. or a building within the scope of Article 3.2.2.43A. or 3.2.2.50A. from another building unless the buildings on both sides of the firewall are sprinklered. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.1.10.3.(1) | Continuity of Firewalls | A firewall shall extend from the ground continuously through, or adjacent to, all storeys of a building or buildings so separated, except that a firewall located above a basement storage garage conforming to Article 3.2.1.2. is permitted to commence at the floor assembly immediately above the storage garage. (See also Sentence 3.1.10.1.(3).) | obc2019_divb | Div B | 3.1.10.3.(1) | 3.1.10.3. Continuity of Firewalls | A firewall shall extend from the ground continuously through, or adjacent to, all storeys of a building or buildings so separated, except that a firewall located above a basement storage garage conforming to Article 3.2.1.2. is permitted to commence at the floor assembly immediately above the storage garage. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.10.3.(2) | Continuity of Firewalls | A firewall is permitted to terminate on the underside of a reinforced concrete roof slab, provided the roof slab on both sides of the firewall has a fire-resistance rating not less than 1 h if the firewall is required to have a fire-resistance rating not less than 2 h, or 2 h if the firewall is required to have a fire-resistance rating not less than 4 h, and there are no concealed spaces within the roof slab in that portion immediately above the firewall. | obc2019_divb | Div B | 3.1.10.3.(2) | 3.1.10.3. Continuity of Firewalls | A firewall is permitted to terminate on the underside of a reinforced concrete roof slab provided, the roof slab on both sides of the firewall has a fire-resistance rating not less than, 1 h if the firewall is required to have a fire-resistance rating not less than 2 h, or 2 h if the firewall is required to have a fire-resistance rating not less than 4 h, and there are no concealed spaces within the roof slab in that portion immediately above the firewall. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.10.4.(1) | Parapets | Except as permitted by Sentences 3.1.10.4.(2) and 3.1.10.3.(2), a firewall shall extend above the roof surface to form a parapet not less than 150 mm high for a firewall required to have a fire-resistance rating not less than 2 h, and 900 mm high for a firewall required to have a fire-resistance rating not less than 4 h. | obc2019_divb | Div B | 3.1.10.4.(1) | 3.1.10.4. Parapets | Except as permitted by Sentences (2) and 3.1.10.3.(2), a firewall shall extend above the roof surface to form a parapet not less than, 150 mm high for a firewall required to have a fire-resistance rating not less than 2 h, and 900 mm high for a firewall required to have a fire-resistance rating not less than 4 h. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.10.4.(2) | Parapets | A firewall that separates 2 buildings with roofs at different elevations need not extend above the upper roof surface to form a parapet, provided the difference in elevation between the roofs is more than 3 m. | obc2019_divb | Div B | 3.1.10.4.(2) | 3.1.10.4. Parapets | A firewall that separates two buildings with roofs at different elevations need not extend above the upper roof surface to form a parapet, provided the difference in elevation between the roofs is more than 3 m. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.10.5.(1) | Maximum Openings | Openings in a firewall shall conform to the size limits described in Article 3.1.8.6. and the aggregate width of openings shall be not more than 25% of the entire length of the firewall. | obc2019_divb | Div B | 3.1.10.5.(1) | 3.1.10.5. Maximum Openings | Openings in a firewall shall conform to the size limits described in Article 3.1.8.6. and the aggregate width of openings shall be not more than 25% of the entire length of the firewall. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.10.6.(1) | Exposure Protection for Adjacent Walls | The requirements of Article 3.2.3.14. shall apply to the external walls of 2 buildings that meet at a firewall at an angle less than 135Â°. | obc2019_divb | Div B | 3.1.10.6.(1) | 3.1.10.6. Exposure Protection for Adjacent Walls | The requirements of Article 3.2.3.14. shall apply to the external walls of two buildings that meet at a firewall at an angle less than 135Ã¯â€šÂ°. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.10.7.(1) | Combustible Projections | Combustible material shall not extend across the end of a firewall but is permitted to extend across a roof above a firewall that is terminated in conformance with Sentence 3.1.10.3.(2). | obc2019_divb | Div B | 3.1.10.7.(1) | 3.1.10.7. Combustible Projections | Combustible material shall not extend across the end of a firewall but is permitted to extend across a roof above a firewall that is terminated in conformance with Sentence 3.1.10.3.(2). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.10.7.(2) | Combustible Projections | If buildings are separated by a firewall, combustible projections on the exterior of one building, including balconies, platforms, canopies, eave projections and stairs, that extend outward beyond the end of the firewall, shall not be permitted within 2.4 m of combustible projections and window or door openings of the adjacent building. (See also Article 3.2.3.6.) | obc2019_divb | Div B | 3.1.10.7.(2) | 3.1.10.7. Combustible Projections | If buildings are separated by a firewall, combustible projections on the exterior of one building, including balconies, platforms, canopies, eave projections and stairs, that extend outward beyond the end of the firewall, shall not be permitted within 2.4 m of combustible projections and window or door openings of the adjacent building. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.11.1.(1) | Separation of Concealed Spaces | Concealed spaces in interior wall, ceiling and crawl spaces shall be separated from concealed spaces in exterior walls and attic or roof spaces by fire blocks conforming to Article 3.1.11.7. | obc2019_divb | Div B | 3.1.11.1.(1) | 3.1.11.1. Separation of Concealed Spaces | Concealed spaces in interior wall, ceiling and crawl spaces shall be separated from concealed spaces in exterior walls and attic or roof spaces by fire blocks conforming to Article 3.1.11.7. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.11.2.(1) | Fire Blocks in Wall Assemblies | Except as permitted by Sentence 3.1.11.2.(2), fire blocks conforming to Article 3.1.11.7. shall be provided to block off concealed spaces within a wall assembly at every floor level, at every ceiling level where the ceiling forms part of an assembly required to have a fire-resistance rating, and so that the maximum horizontal dimension is not more than 20 m and the maximum vertical dimension is not more than 3 m. | obc2019_divb | Div B | 3.1.11.2.(1) | 3.1.11.2. Fire Blocks in Wall Assemblies | Except as permitted by Sentence (2), fire blocks conforming to Article 3.1.11.7. shall be provided to block off concealed spaces within a wall assembly, at every floor level, at every ceiling level where the ceiling forms part of an assembly required to have a fire-resistance rating, and so that the maximum horizontal dimension is not more than 20 m and the maximum vertical dimension is not more than 3 m. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.11.2.(2) | Fire Blocks in Wall Assemblies | Fire blocks conforming to Sentence 3.1.11.2.(1) are not required, provided the wall space is filled with insulation, the exposed construction materials and any insulation within the wall space are noncombustible, the exposed materials within the space, including insulation but not including wiring, piping or similar services, have a flame-spread rating not more than 25 on any exposed surface, or on any surface that would be exposed by cutting through the material in any direction, and fire blocks are installed so that the vertical distance between them is not more than 10 m, or the insulated wall assembly contains not more than one concealed air space, and the horizontal thickness of that air space is not more than 25 mm. | obc2019_divb | Div B | 3.1.11.2.(2) | 3.1.11.2. Fire Blocks in Wall Assemblies | Fire blocks conforming to Sentence (1) are not required provided, the wall space is filled with insulation, the exposed construction materials and any insulation within the wall space are noncombustible, the exposed materials within the wall space, including insulation but not including wiring, piping or similar services, have a flame-spread rating not more than 25 on any exposed surface, or on any surface that would be exposed by cutting through the material in any direction, and fire blocks are installed so that the vertical distance between them is not more than 10 m, or the insulated wall assembly contains not more than one concealed air space and the horizontal thickness of that air space is not more than 25 mm. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.11.3.(1) | Fire Blocks between Nailing and Supporting Elements | In a building required to be of noncombustible construction, a concealed space in which there is an exposed ceiling finish with a flame-spread rating more than 25 shall be provided with fire blocks conforming to Article 3.1.11.7. between wood nailing elements so that the maximum area of the concealed space is not more than 2 m2. | obc2019_divb | Div B | 3.1.11.3.(1) | 3.1.11.3. Fire Blocks Between Nailing and Supporting Elements | In a building required to be of noncombustible construction, a concealed space in which there is an exposed ceiling finish with a flame-spread rating more than 25, shall be provided with fire blocks conforming to Article 3.1.11.7. between wood nailing elements, so that the maximum area of the concealed space is not more than 2 m2. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.11.3.(2) | Fire Blocks between Nailing and Supporting Elements | In a building required to be of noncombustible construction, fire blocks conforming to Article 3.1.11.7. shall be provided in the concealed spaces created by the wood members permitted by Sentence 3.1.5.10.(2) so that the maximum area of a concealed space is not more than 10 m 2 . | obc2019_divb | Div B | 3.1.11.3.(2) | 3.1.11.3. Fire Blocks Between Nailing and Supporting Elements | In a building required to be of noncombustible construction, fire blocks conforming to Article 3.1.11.7. shall be provided in the concealed spaces created by the wood members permitted by Sentence 3.1.5.8.(2), so that the maximum area of a concealed space is not more than 10 m2. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.11.4.(1) | Fire Blocks between Vertical and Horizontal Spaces | Fire blocks conforming to Article 3.1.11.7. shall be provided at all interconnections between concealed vertical and horizontal spaces in interior coved ceilings, drop ceilings and soffits in which the exposed construction materials within the space have a flame-spread rating more than 25, and at the end of each run and at each floor level in concealed spaces between stair stringers in which the exposed construction materials within the space have a flame-spread rating more than 25. | obc2019_divb | Div B | 3.1.11.4.(1) | 3.1.11.4. Fire Blocks Between Vertical and Horizontal Spaces | Fire blocks conforming to Article 3.1.11.7. shall be provided, at all interconnections between concealed vertical and horizontal spaces in interior coved ceilings, drop ceilings and soffits in which the exposed construction materials within the space have a flame spread rating more than 25, and at the end of each run and at each floor level in concealed spaces between stair stringers in which the exposed construction materials within the space have a flame spread rating more than 25. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.11.5.(1) | Fire Blocks in Horizontal Concealed Spaces | Except for crawl spaces conforming to Sentence 3.1.11.6.(1) and as required in Sentence 3.1.11.5.(3) , horizontal concealed spaces within a floor assembly or roof assembly of combustible construction, in which sprinklers are not installed, shall be separated by construction conforming to Article 3.1.11.7. into compartments not more than 600 m2 in area with no dimension more than 60 m if the exposed construction materials within the space have a flame-spread rating not more than 25, and not more than 300 m2 in area with no dimension more than 20 m if the exposed construction materials within the space have a flame-spread rating more than 25. | obc2019_divb | Div B | 3.1.11.5.(1) | 3.1.11.5. Fire Blocks in Horizontal Concealed Spaces | Except for a crawl space conforming to Sentence 3.1.11.6.(1), a horizontal concealed space within a floor assembly or roof assembly of combustible construction, in which sprinklers are not installed, shall be separated by construction conforming to Article 3.1.11.7. into compartments not more than, 600 m2 in area with no dimension more than 60 m, if the exposed construction materials within the space have a flame-spread rating not more than 25, and 300 m2 in area with no dimension more than 20 m, if the exposed construction materials within the space have a flame-spread rating more than 25. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.11.5.(2) | Fire Blocks in Horizontal Concealed Spaces | A concealed space in an exterior cornice, a mansard-style roof, a balcony or a canopy in which exposed construction materials within the space have a flame-spread rating more than 25, shall be separated by construction conforming to Article 3.1.11.7. at locations where the concealed space extends across the ends of required vertical fire separations, and so that the maximum dimension in the concealed space is not more than 20 m. | obc2019_divb | Div B | 3.1.11.5.(2) | 3.1.11.5. Fire Blocks in Horizontal Concealed Spaces | A concealed space in an exterior cornice, a mansard style roof, a balcony or a canopy in which exposed construction materials within the space have a flame spread rating more than 25, shall be separated by construction conforming to Article 3.1.11.7., at locations where the concealed space extends across the ends of required vertical fire separations, and so that the maximum dimension in the concealed space is not more than 20 m. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.11.5.(3) | Fire Blocks in Horizontal Concealed Spaces | Except as provided in Sentence 3.1.11.5.(4), in buildings conforming to Article 3.2.2.50.or 3.2.2.58., horizontal concealed spaces within a floor assembly or roof assembly of combustible construction shall be separated by construction conforming to Article 3.1.11.7. into compartments that are not more than 600 m2 in area with no dimension more than 60 m, if the exposed construction materials within the space have a flame-spread rating not more than 25, and not more than 300 m2 in area with no dimension more than 20 m, if the exposed construction materials within the space have a flame-spread rating more than 25. (See Note A-3.1.11.5.(3).) | obc2019_divb | Div B | 3.1.11.5.(3) | 3.1.11.5. Fire Blocks in Horizontal Concealed Spaces | Except as provided by Sentence (4), a horizontal concealed space within a floor assembly or roof assembly of combustible construction in a building within the scope of Article 3.2.2.43A. or 3.2.2.50A. shall be separated by construction conforming to Article 3.1.11.7. into compartments not more than, 600 m2 in area with no dimension more than 60 m, if the exposed construction materials within the space have a flame-spread rating not more than 25, and 300 m2 in area with no dimension more than 20 m, if the exposed construction materials within the space have a flame-spread rating more than 25. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.11.5.(4) | Fire Blocks in Horizontal Concealed Spaces | Fire blocks conforming to Sentence 3.1.11.5.(3) are not required where the horizontal concealed space within the floor or roof assembly is entirely filled with noncombustible insulation such that any air gap between the top of the insulation and the floor or roof deck does not exceed 50 mm. | obc2019_divb | Div B | 3.1.11.5.(4) | 3.1.11.5. Fire Blocks in Horizontal Concealed Spaces | Sentence (3) does not apply if the horizontal concealed space within the floor assembly or roof assembly is entirely filled with noncombustible insulation such that any air gap between the top of the insulation and the underside of the floor or roof deck does not exceed 50 mm. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.11.6.(1) | Fire Blocks in Crawl Spaces | A crawl space that is not considered as a basement by Article 3.2.2.9. and in which sprinklers are not installed, shall be separated by construction conforming to Article 3.1.11.7. into compartments not more than 600 m2 in area with no dimension more than 30 m. | obc2019_divb | Div B | 3.1.11.6.(1) | 3.1.11.6. Fire Blocks in Crawl Spaces | A crawl space that is not considered as a basement by Article 3.2.2.9. and in which sprinklers are not installed, shall be separated by construction conforming to Article 3.1.11.7. into compartments not more than 600 m2 in area with no dimension more than 30 m. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.11.7.(1) | Fire Block Materials | Except as permitted by Sentences 3.1.11.7.(2) to 3.1.11.7.(4) and 3.1.11.7.(7), fire blocks shall remain in place and prevent the passage of flames for not less than 15 min when subjected to the standard fire exposure in ULC CAN/ULC-S101-14 Fire Endurance Tests of Building Construction and Materials | obc2019_divb | Div B | 3.1.11.7.(1) | 3.1.11.7. Fire Block Materials | Except as permitted by Sentences (2) to (4) and (7) fire blocks shall remain in place and prevent the passage of flames for not less than 15 min when subjected to the standard fire exposure in CAN/ULC-S101, "Fire Endurance Tests of Building Construction and Materials". |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.11.7.(2) | Fire Block Materials | Gypsum board not less than 12.7 mm thick and sheet steel not less than 0.38 mm thick need not be tested in conformance with Sentence 3.1.11.7.(1), provided all joints have continuous support. | obc2019_divb | Div B | 3.1.11.7.(2) | 3.1.11.7. Fire Block Materials | Gypsum board not less than 12.7 mm thick and sheet steel not less than 0.38 mm thick need not be tested in conformance with Sentence (1) provided all joints have continuous support. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.11.7.(3) | Fire Block Materials | In a building required to be of noncombustible construction, wood nailing elements described in Article 3.1.5.8. need not be tested in conformance with Sentence 3.1.11.7.(1). | obc2019_divb | Div B | 3.1.11.7.(3) | 3.1.11.7. Fire Block Materials | In a building required to be of noncombustible construction, wood nailing elements described in Article 3.1.5.6. need not be tested in conformance with Sentence (1). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.11.7.(4) | Fire Block Materials | In a building permitted to be of combustible construction, in a combustible roof system permitted by Sentence 3.1.5.3.(2), and in a raised platform permitted by Sentence 3.1.5.10.(2), fire blocks are permitted to be solid lumber or a structural composite lumber product conforming to ASTM D 5456-10a Evaluation of Structural Composite Lumber Products not less than 38 mm thick, phenolic bonded plywood, waferboard, or oriented strandboard not less than 12.5 mm thick with joints supported, or two thicknesses of lumber or a structural composite lumber product conforming to ASTM D 5456-10a Evaluation of Structural Composite Lumber Products each not less than 19 mm thick with joints staggered, where the width or height of the concealed space requires more than one piece of lumber or structural composite lumber product not less than 38 mm thick to block off the space. | obc2019_divb | Div B | 3.1.11.7.(4) | 3.1.11.7. Fire Block Materials | In a building permitted to be of combustible construction, in a combustible roof system permitted by Sentence 3.1.5.3.(2), and in a raised platform permitted by Sentence 3.1.5.8.(2), fire blocks are permitted to be, solid lumber or a structural composite lumber product conforming to ASTM D5456, "Evaluation of Structural Composite Lumber Products", not less than 38 mm thick, phenolic bonded plywood, OSB or waferboard not less than 12.5 mm thick with joints supported, or two thicknesses of lumber or a structural composite lumber product conforming to ASTM D5456, "Evaluation of Structural Composite Lumber Products", each not less than 19 mm thick with joints staggered, where the width or height of the concealed space requires more than one piece of lumber or structural composite lumber product not less than 38 mm thick to block off the space. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.11.7.(5) | Fire Block Materials | Openings through materials referred to in Sentences 3.1.11.7.(1) to 3.1.11.7.(4) shall be protected to maintain the integrity of the construction. | obc2019_divb | Div B | 3.1.11.7.(5) | 3.1.11.7. Fire Block Materials | Openings through fire blocks shall be protected to maintain the integrity of the construction. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.11.7.(6) | Fire Block Materials | Where materials referred to in Sentences 3.1.11.7.(1) to 3.1.11.7.(4) are penetrated by construction elements or by service equipment, a fire stop shall be used to seal the penetration. (See Note A-3.1.11.7.(6).) | obc2019_divb | Div B | 3.1.11.7.(6) | 3.1.11.7. Fire Block Materials | Where fire blocks are penetrated by construction elements or by service equipment, a fire stop shall be used to seal the penetration. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.11.7.(7) | Fire Block Materials | In buildings permitted to be of combustible construction, semi-rigid fibre insulation board produced from glass, rock or slag is permitted to be used to block the vertical space in a double stud wall assembly formed at the intersection of the floor assembly and the walls, provided the width of the vertical space does not exceed 25 mm and the insulation board has a density not less than 45 kg/m3, is securely fastened to one set of studs, extends from below the bottom of the top plates in the lower storey to above the top of the bottom plate in the upper storey, and completely fills the portion of the vertical space between the headers and between the wall plates. (See Note A-3.1.11.7.(7).) | obc2019_divb | Div B | 3.1.11.7.(7) | 3.1.11.7. Fire Block Materials | In a building permitted to be of combustible construction, semi-rigid fibre insulation board, produced from glass, rock or slag, is permitted to be used to block the vertical space in a double wythe wall assembly formed at the intersection of the floor assembly and the walls, provided the insulation board, has a density not less than 45 kg/m3, is securely fastened to one set of studs, extends from below the bottom of the top plates in the lower storey to above the top of the bottom plate in the upper storey, and completely fills the portion of the vertical space between the headers and between the wall plates. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.12.1.(1) | Determination of Ratings | Except as required by Sentence 3.1.12.1.(2) and as permitted by Sentence 3.1.12.1.(3), the flame-spread rating and smoke developed classification of a material, assembly, or structural member shall be determined on the basis of not less than three tests conducted in conformance with ULC CAN/ULC-S102-10 Test for Surface Burning Characteristics of Building Materials and Assemblies | obc2019_divb | Div B | 3.1.12.1.(1) | 3.1.12.1. Determination of Ratings | Except as required by Sentence (2) and as permitted by Sentence (3), the flame-spread rating and smoke developed classification of a material, assembly, or structural member shall be determined on the basis of no fewer than three tests conducted in conformance with CAN/ULC-S102, "Test for Surface Burning Characteristics of Building Materials and Assemblies". |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.12.1.(2) | Determination of Ratings | The flame-spread rating and smoke developed classification of a material or assembly shall be determined on the basis of not less than three tests conducted in conformance with ULC CAN/ULC-S102.2-10 Test for Surface Burning Characteristics of Flooring, Floor Coverings, and Miscellaneous Materials and Assemblies if the material or assembly is designed for use in a relatively horizontal position with only its top surface exposed to air, cannot be tested in conformance with Sentence 3.1.12.1.(1) without the use of supporting material that is not representative of the intended installation, or is thermoplastic. | obc2019_divb | Div B | 3.1.12.1.(2) | 3.1.12.1. Determination of Ratings | The flame-spread rating and smoke developed classification of a material or assembly shall be determined on the basis of no fewer than three tests conducted in conformance with CAN/ULC-S102.2, "Test for Surface Burning Characteristics of Flooring, Floor Coverings, and Miscellaneous Materials and Assemblies", if the material or assembly, is designed for use in a relatively horizontal position with only its top surface exposed to air, cannot be tested in conformance with Sentence (1) without the use of supporting material that is not representative of the intended installation, or is thermoplastic. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.12.1.(3) | Determination of Ratings | A material, assembly, or structural member is permitted to be assigned a flame-spread rating and smoke developed classification on the basis of . | obc2019_divb | Div B | 3.1.12.1.(3) | 3.1.12.1. Determination of Ratings | A material, assembly, or structural member is permitted to be assigned a flame-spread rating and smoke developed classification on the basis of MMAH Supplementary Standard SB-2, "Fire Performance Ratings". |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.1.13.1.(2) | Interior Finishes, Furnishings and Decorative Materials | Interior finish material shall include any material that forms part of the interior surface of a floor, wall, partition or ceiling, including interior cladding of plaster, wood or tile, surfacing of fabric, paint, plastic, veneer or wallpaper, doors, windows and trim, lighting elements such as light diffusers and lenses forming part of the finished surface of the ceiling, and carpet material that overlies a floor that is not intended as the finished floor. | obc2019_divb | Div B | 3.1.13.1.(1) | 3.1.13.1. Interior Finish Description | Interior finish material shall include any material that forms part of the interior surface of a floor, wall, partition or ceiling, including, interior cladding of plaster, wood or tile, surfacing of fabric, paint, plastic, veneer or wallpaper, doors, windows and trim, lighting elements, such as light diffusers and lenses forming part of the finished surface of the ceiling, and carpet material that overlies a floor that is not intended as the finished floor. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.13.10.(1) | Exterior Exit Passageway | The wall and ceiling finishes of an exterior exit passageway that provides the only means of egress from the rooms or suites it serves, including the soffit beneath and the guard on the passageway, shall have a flame-spread rating not more than 25, except that a flame-spread rating not more than 150 is permitted for up to 10% of the total wall area and for up to 10% of the total ceiling area. | obc2019_divb | Div B | 3.1.13.10.(1) | 3.1.13.10. Exterior Exit Passageway | The wall and ceiling finishes of an exterior exit passageway that provides the only means of egress from the rooms or suites it serves, including the soffit beneath and the guard on the passageway, shall have a flame-spread rating not more than 25, except that a flame-spread rating not more than 150 is permitted for up to 10% of the total wall area and for up to 10% of the total ceiling area. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.13.11.(1) | Elevator Cars | The wall and ceiling surfaces of elevator cars shall have a flame-spread rating not more than 75. | obc2019_divb | Div B | 3.1.13.11.(1) | 3.1.13.11. Elevator Cars | The wall and ceiling surfaces of elevator cars shall have a flame-spread rating not more than 75. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.13.11.(2) | Elevator Cars | The wall, ceiling and floor surfaces of elevator cars shall have a smoke developed classification not more than 450. | obc2019_divb | Div B | 3.1.13.11.(2) | 3.1.13.11. Elevator Cars | The wall, ceiling and floor surfaces of elevator cars shall have a smoke developed classification not more than 450. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.13.2.(1) | Flame-Spread Rating | Except as otherwise required or permitted by this Subsection, the flame-spread rating of interior wall and ceiling finishes, including glazing and skylights, shall be not more than 150 and shall conform to Table 3.1.13.2. | obc2019_divb | Div B | 3.1.13.2.(1) | 3.1.13.2. Flame-Spread Rating | Except as otherwise required or permitted by this Subsection, the flame-spread rating of interior wall and ceiling finishes, including glazing and skylights, shall be not more than 150 and shall conform to Table 3.1.13.2. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.13.2.(2) | Flame-Spread Rating | Except as permitted by Sentence 3.1.13.2.(3), doors, other than those in Group A, Division 1 occupancies, need not conform to Sentence 3.1.13.2.(1) provided they have a flame-spread rating not more than 200. (See Note A-3.1.13.2.(2).) (See Note A-3.1.13.2.(2).) | obc2019_divb | Div B | 3.1.13.2.(2) | 3.1.13.2. Flame-Spread Rating | Except as permitted by Sentence (3), doors, other than those in Group A, Division 1 occupancies, need not conform to Sentence (1) provided they have a flame-spread rating not more than 200. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.13.2.(3) | Flame-Spread Rating | Doors within a dwelling unit need not conform to Sentences 3.1.13.2.(1)and 3.1.13.2.(2). | obc2019_divb | Div B | 3.1.13.2.(3) | 3.1.13.2. Flame-Spread Rating | Doors within a dwelling unit need not conform to Sentences (1) and (2). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.13.2.(4) | Flame-Spread Rating | Up to 10% of the total wall area and 10% of the total ceiling area of a wall or ceiling finish that is required by Sentence 3.1.13.2.(1) to have a flame-spread rating less than 150 is permitted to have a flame-spread rating not more than 150, except that up to 25% of the total wall area of lobbies described in Sentence 3.4.4.2.(2) is permitted to have a flame-spread rating not more than 150. | obc2019_divb | Div B | 3.1.13.2.(4) | 3.1.13.2. Flame-Spread Rating | Up to 10% of the total wall area and 10% of the total ceiling area of a wall or ceiling finish that is required by Sentence (1) to have a flame-spread rating less than 150 is permitted to have a flame-spread rating not more than 150, except that up to 25% of the total wall area of lobbies described in Sentence 3.4.4.2.(2) is permitted to have a flame-spread rating not more than 150. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.13.2.(5) | Flame-Spread Rating | Except in the case of Group A, Division 1 occupancies, combustible doors, skylights, glazing and light diffusers and lenses shall not be considered in the calculation of wall and ceiling areas described in Sentence 3.1.13.2.(4). | obc2019_divb | Div B | 3.1.13.2.(5) | 3.1.13.2. Flame-Spread Rating | Except in the case of Group A, Division 1 occupancies, combustible doors, skylights, glazing and light diffusers and lenses shall not be considered in the calculation of wall and ceiling areas described in Sentence (4). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.13.3.(1) | Bathrooms in Residential Suites | The flame-spread rating of interior wall and ceiling finishes for a bathroom within a suite of residential occupancy shall be not more than 200. | obc2019_divb | Div B | 3.1.13.3.(1) | 3.1.13.3. Plumbing Fixtures and Bathrooms Finishes | The flame-spread rating of interior wall and ceiling finishes for a bathroom in a suite of residential occupancy shall be not more than 200. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.13.4.(1) | Light Diffusers and Lenses | The flame-spread rating of combustible light diffusers and lenses in all occupancies other than Group A, Division 1 is permitted to be more than the flame-spread rating limits required elsewhere in this Subsection, provided the light diffusers and lenses have a flame-spread rating not more than 250 and a smoke developed classification not more than 600 when tested in conformance with ULC CAN/ULC-S102.2-10 Test for Surface Burning Characteristics of Flooring, Floor Coverings, and Miscellaneous Materials and Assemblies fall to the bottom of the test apparatus before igniting when tested in conformance with ULC CAN/ULC-S102.3-07 Fire Test of Light Diffusers and Lenses are not prevented from falling from the ceiling by construction located beneath the elements, and are not used in a corridor that is required to be separated from the remainder of the building by a fire separation or in an exit shaft unless individual diffusers or lenses are not more than 1 m2 in area and are not less than 1.2 m apart. | obc2019_divb | Div B | 3.1.13.4.(1) | 3.1.13.4. Light Diffusers and Lenses | The flame-spread rating of combustible light diffusers and lenses in all occupancies other than Group A, Division 1 is permitted to be more than the flame-spread rating limits required elsewhere in this Subsection, provided the light diffusers and lenses, have a flame-spread rating not more than 250 and a smoke developed classification not more than 600 when tested in conformance with CAN/ULC-S102.2, "Test for Surface Burning Characteristics of Flooring, Floor Coverings, and Miscellaneous Materials and Assemblies", fall to the bottom of the test apparatus before igniting when tested in conformance with ULC-S102.3, "Fire Test of Light Diffusers and Lenses", are not prevented from falling from the ceiling by construction located beneath the elements, and are not used in a corridor that is required to be separated from the remainder of the building by a fire separation or in an exit shaft unless individual diffusers or lenses are not more than 1 m2 in area and are not less than 1.2 m apart. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.13.5.(1) | Skylights | Individual combustible skylights in a corridor that is required to be separated from the remainder of the building by a fire separation shall be not more than 1 m2 in area and not less than 1.2 m apart. | obc2019_divb | Div B | 3.1.13.5.(1) | 3.1.13.5. Skylights | Individual combustible skylights in a corridor that is required to be separated from the remainder of the storey by a fire separation shall be not more than 1 m2 in area and not less than 1.2 m apart. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.13.6.(1) | Corridors | Except as permitted by Sentences (2) and (3), the flame-spread rating shall be not more than 75 for the interior wall finish of (a) a public corridor, (b) a corridor used by the public in an assembly occupancy, or (c) a corridor serving classrooms. | obc2019_divb | Div B | 3.1.13.6.(1) | 3.1.13.6. Corridors | Except as permitted by Sentences (2) and (3), the flame-spread rating shall be not more than 75 for the interior wall finish of, (a) a public corridor, (b) a corridor used by the public in, (i) an assembly occupancy, or (ii) a care, care and treatment or detention occupancy, (c) a corridor serving classrooms, or (d) a corridor serving sleeping rooms in a care, care and treatment or detention occupancy. |  | Common Sentence | Yes | Construction Materials
2015 | ON | NBC | Div B | 3.1.13.6.(2) | Corridors | The flame-spread rating for corridors specified in Sentence 3.1.13.6.(1) is permitted to be waived, provided the flame-spread rating is not more than 25 on the upper half of the wall, and 150 on the lower half of the wall. | obc2019_divb | Div B | 3.1.13.6.(2) | 3.1.13.6. Corridors | The flame-spread rating limit specified in Sentence (1) does not apply to corridors referred to in Sentence (1) provided the flame-spread rating is not more than, 25 on the upper half of the wall, and 150 on the lower half of the wall. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.13.6.(2) | Corridors | The flame-spread rating for corridors specified in Sentence 3.1.13.6.(1) is permitted to be waived, provided the flame-spread rating is not more than 25 on the upper half of the wall, and 150 on the lower half of the wall. | obc2019_divb | Div B | 3.1.13.6.(6) | 3.1.13.6. Corridors | The flame-spread rating limits specified in Sentence (5) do not apply to a corridor in which the flame-spread rating is not more than 150 provided the floor area is sprinklered. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.13.6.(3) | Corridors | Where the floor area is sprinklered throughout, the flame-spread ratings for corridors specified in Sentences (1) and (2) shall be not more than 150. | obc2019_divb | Div B | 3.1.13.6.(3) | 3.1.13.6. Corridors | The flame-spread rating limits specified in Sentences (1) and (2) for corridors referred to in Sentence (1) do not apply to a corridor in which the flame-spread rating is not more than 150 provided the floor area is sprinklered. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.13.6.(4) | Corridors | The flame-spread ratings specified in Sentences 3.1.13.6.(1) , 3.1.13.6.(2) and 3.1.13.6.(3) apply to occupancies in the corridor as well as to the corridor itself. | obc2019_divb | Div B | 3.1.13.6.(4) | 3.1.13.6. Corridors | The flame-spread rating limits specified in Sentences (1) to (3) apply to occupancies in the corridor as well as to the corridor itself. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.13.6.(5) | Corridors | Except as provided in Sentence 3.1.13.6.(6), the interior ceiling finish of corridors and occupancies referred to in Sentences 3.1.13.6.(1) and 3.1.13.6.(4) shall have a flame-spread rating not more than 25. | obc2019_divb | Div B | 3.1.13.6.(5) | 3.1.13.6. Corridors | Except in a floor area that is sprinklered and as permitted in Sentence (6), the interior ceiling finish of corridors and occupancies referred to in Sentences (1) and (4) shall have a flame-spread rating not more than 25. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.13.7.(1) | High Buildings | Except as permitted by Sentences 3.1.13.7.(2) to 3.1.13.7.(4), the interior wall, ceiling and floor finishes in a building regulated by the provisions of part 3. shall conform to the flame-spread rating requirements in Articles 3.1.13.2. and 3.1.13.11. and to the flame-spread rating and smoke developed classification values in Table 3.1.13.7. | obc2019_divb | Div B | 3.1.13.7.(1) | 3.1.13.7. High Buildings | Except as permitted by Sentences (2) and (3), the interior wall, ceiling and floor finishes in a building regulated by the provisions of Subsection 3.2.6. shall conform to the flame-spread rating requirements in Articles 3.1.13.2. to 3.1.13.6. and to the flame-spread rating and smoke developed classification values in Table 3.1.13.7. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.13.7.(2) | High Buildings | Except for a building of Group B major occupancy and elevator cars, the flame-spread rating and smoke developed classification of interior wall, floor and ceiling finishes need not conform to the values in Table 3.1.13.7., provided the building is sprinklered. | obc2019_divb | Div B | 3.1.13.7.(2) | 3.1.13.7. High Buildings | Except for a building of Group B major occupancy and elevator cars, the flame-spread rating and smoke developed classification of interior wall, floor and ceiling finishes need not conform to the values in Table 3.1.13.7., provided the building is sprinklered and the sprinkler system is electrically supervised in conformance with Sentences 3.2.4.10.(3) and 3.2.4.17.(1). |  | Common Sentence | Yes | High Buildings
2015 | ON | NBC | Div B | 3.1.13.7.(3) | High Buildings | Trim and millwork in an exit stairway, a vestibule to an exit stairway, a lobby described in Sentence 3.4.4.2.(2), or a corridor not within a suite need not conform to the flame-spread rating and smoke developed classification requirements of Sentence 3.1.13.7.(1) provided they have (a) a flame-spread rating not more than 150, (b) a smoke developed classification not more than 300, and (c) an aggregate area not more than 10% of the area of the wall or ceiling on which they occur. A door serving an exit stairway, a vestibule to an exit stairway, a lobby described in Sentence 3.4.4.2.(2), or a corridor not within a suite need not conform to the flame-spread rating andsmoke developed classification requirements of Sentence (1) provided (a) it has a flame-spread rating not more than 200, (b) it has a smoke developed classification not more than 300, and (c) the aggregate area of all doors is not more than 10%of the area of thewall in which they are located. | obc2019_divb | Div B | 3.1.13.7.(3) | 3.1.13.7. High Buildings | Trim, millwork and doors in an exit stairway, a vestibule to an exit stairway, a lobby described in Sentence 3.4.4.2.(2), or a corridor not within a suite need not conform to the flame-spread rating and smoke developed classification requirements of Sentence (1), provided they have, a flame-spread rating not more than 150, a smoke developed classification not more than 300, and an aggregate area not more than 10% of the area of the wall or ceiling on which they occur. |  | Common Sentence | Yes | Construction Materials
2015 | ON | NBC | Div B | 3.1.13.8.(1) | Noncombustible Construction | In a building required to be of noncombustible construction, the flame-spread ratings required by part 3. shall apply in addition to the requirements in this Subsection, and the flame-spread ratings for exits in this Subsection shall also apply to any surface in the exit that would be exposed by cutting through the material in any direction, except that this requirement does not apply to doors, heavy timber construction in a sprinklered building and fire-retardant-treated wood. | obc2019_divb | Div B | 3.1.13.8.(1) | 3.1.13.8. Noncombustible Construction | In a building required to be of noncombustible construction, the flame-spread ratings required by Subsection 3.1.5. shall apply in addition to the requirements in this Subsection, and the flame-spread ratings for exits in this Subsection shall also apply to any surface in the exit that would be exposed by cutting through the material in any direction, except that this requirement does not apply to doors, heavy timber construction in a sprinklered building and fire-retardant treated wood. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.13.9.(1) | Underground Walkways | Except for paint, the interior wall and ceiling finishes of an underground walkway shall be of noncombustible materials. | obc2019_divb | Div B | 3.1.13.9.(1) | 3.1.13.9. Underground Walkways | Except for paint, the interior wall and ceiling finishes of an underground walkway shall be of noncombustible materials. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.14.1.(1) | Fire-Retardant-Treated Wood Roof Systems | If a fire-retardant-treated wood roof system is used to comply with the requirements of part 3., the roof deck assembly shall meet the conditions of acceptance of ULC CAN/ULC-S126-14 Test for Fire Spread Under Roof-Deck Assemblies | obc2019_divb | Div B | 3.1.14.1.(1) | 3.1.14.1. Fire-Retardant Treated Wood Roof Systems | If a fire-retardant treated wood roof system is used to comply with the requirements of Subsection 3.2.2., the roof deck assembly shall meet the conditions of acceptance of CAN/ULC-S126, "Test for Fire Spread Under Roof-Deck Assemblies". |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.14.1.(2) | Fire-Retardant-Treated Wood Roof Systems | Supports for the roof deck assembly referred to in Sentence 3.1.14.1.(1) shall consist of fire-retardant-treated wood, heavy timber construction, noncombustible construction, or a combination thereof. | obc2019_divb | Div B | 3.1.14.1.(2) | 3.1.14.1. Fire-Retardant Treated Wood Roof Systems | Supports for the roof deck assembly referred to in Sentence (1) shall consist of, fire-retardant treated wood, heavy timber construction, noncombustible construction, or a combination of the items described in Clauses (a) to (c). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.14.2.(1) | Metal Roof Deck Assemblies | Except as permitted by Sentence 3.1.14.2.(2), a metal roof deck assembly shall meet the conditions of acceptance of ULC CAN/ULC-S126-14 Test for Fire Spread Under Roof-Deck Assemblies if it supports a combustible material above the deck that could propagate a fire beneath the roof deck assembly, and the deck is used to comply with the requirements of Sentences 3.2.2.25.(2), Sentence 3.2.2.32.(2), Sentence 3.2.2.60.(2), Sentence 3.2.2.66.(2), Sentence 3.2.2.76.(2) and 3.2.2.83.(2) for noncombustible construction. | obc2019_divb | Div B | 3.1.14.2.(1) | 3.1.14.2. Metal Roof Deck Assemblies | Except as permitted by Sentence (2), a metal roof deck assembly shall meet the conditions of acceptance of CAN/ULC-S126, "Test for Fire Spread Under Roof-Deck Assemblies", if, it supports a combustible material above the deck that could propagate a fire beneath the roof deck assembly, and the deck is used to comply with the requirements of Sentences 3.2.2.25.(2), 3.2.2.32.(2), 3.2.2.53.(2), 3.2.2.59.(2), 3.2.2.70.(2) and 3.2.2.76.(2) for noncombustible construction. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.14.2.(2) | Metal Roof Deck Assemblies | The requirements of Sentence 3.1.14.2.(1) are waived provided the combustible material above the roof deck is protected by not less than 12.7 mm thick gypsum board, mechanically fastened to a supporting assembly if located beneath the roof deck, or by a thermal barrier conforming to one of Clauses 3.1.5.15.(2) to 3.1.5.15.(2) that is located on the underside of the combustible material, or beneath the roof deck, the building is sprinklered throughout, or the roof assembly has a fire-resistance rating not less than 45 min. | obc2019_divb | Div B | 3.1.14.2.(2) | 3.1.14.2. Metal Roof Deck Assemblies | The requirements of Sentence (1) are waived provided, the combustible material above the roof deck is protected, by not less than 12.7 mm thick gypsum board, mechanically fastened to a supporting assembly if located beneath the roof deck, or by a thermal barrier conforming to Clause 3.1.5.12.(4)(c) or (d) that is located on the underside of the combustible material or beneath the roof deck, the building is sprinklered, or the roof assembly has a fire-resistance rating not less than 45 min. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.15.1.(1) | Roof Covering Classification | A roof covering classification shall be determined in conformance with ULC CAN/ULC-S107-10 Fire Tests of Roof Coverings | obc2019_divb | Div B | 3.1.15.1.(1) | 3.1.15.1. Roof Covering Classification | A roof covering classification shall be determined in conformance with CAN/ULC-S107, "Fire Tests of Roof Coverings". (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.15.2.(1) | Roof Coverings | Except as provided in Sentences 3.1.15.2.(2) and 3.1.15.2.(3) , every roof covering shall have a Class A, B or C classification as determined in accordance with Article 3.1.15.1. | obc2019_divb | Div B | 3.1.15.2.(1) | 3.1.15.2. Roof Coverings | Except as provided by Sentences (2) and (3), every roof covering shall have a Class A, B or C classification as determined in accordance with Article 3.1.15.1. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.15.2.(2) | Roof Coverings | A roof covering is not required to have a Class A, B or C classification for a tent, an air-supported structure, a building of Group A, Division 2 occupancy not more than 2 storeys in building height and not more than 1?000 m2 in building area provided the roof covering is underlaid with noncombustible material, or a steel building system referred to in Article 4.3.4.3., provided the roof covering consists of brick, masonry, concrete, metal sheets or metal shingles. | obc2019_divb | Div B | 3.1.15.2.(2) | 3.1.15.2. Roof Coverings | A roof covering is not required to have a Class A, B or C classification for, a tent, an air-supported structure, a building of Group A, Division 2 occupancy not more than 2 storeys in building height and not more than 1 000 m2 in building area, provided the roof covering is underlaid with noncombustible material, or a steel building system described in Article 4.3.4.3., provided the roof covering consists of metal sheets, metal shingles or other noncombustible roofing materials. |  | Common Sentence | Yes | Construction Materials
2015 | ON | NBC | Div B | 3.1.15.2.(3) | Roof Covering Classification | Except as provided in Sentence (4), roof coverings on buildings conforming to Article 3.2.2.50. or 3.2.2.58. shall have a Class A classification where the roof height is greater than 25m measured from the floor of the first storey to the highest point of the roof. | obc2019_divb | Div B | 3.1.15.2.(3) | 3.1.15.2. Roof Coverings | Combustible roof coverings on buildings within the scope of Article 3.2.2.43A. or 3.2.2.50A. shall have a Class A classification. |  | Common Sentence | Yes | Mid-rise Wood
2015 | ON | NBC | Div B | 3.1.16.1.(1) | Fabric Canopies and Marquees | Fabrics used as part of an awning, canopy or marquee that is located within or attached to a building of any type of construction shall conform to ULC CAN/ULC-S109-14 Flame Tests of Flame-Resistant Fabrics and Films | obc2019_divb | Div B | 3.1.16.1.(1) | 3.1.16.1. Fabric Awnings, Canopies and Marquees | Fabrics used as part of an awning, canopy or marquee that is located within or attached to a building of any type of construction shall conform to CAN/ULC-S109, "Flame Tests of Flame-Resistant Fabrics and Films". |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.17.1.(1) | Occupant Load Determination | The occupant load of a floor area or part of a floor area shall be based on the number of seats in an assembly occupancy having fixed seats, 2 persons per sleeping room in a dwelling unit, or the number of persons for which the area is designed, but not less than that determined from Table 3.1.17.1. for occupancies other than those described in Clauses 3.1.17.1.(1) and 3.1.17.1.(1), unless it can be shown that the area will be occupied by fewer persons. | obc2019_divb | Div B | 3.1.17.1.(1) | 3.1.17.1. Occupant Load Determination | The occupant load of a floor area or part of a floor area, or of a building or part of a building not having a floor area, shall be based on, the number of seats in an assembly occupancy having fixed seats, two persons per sleeping room or sleeping area in a dwelling unit or suite, or the number of persons, for which the area is designed, or determined from Table 3.1.17.1. for occupancies other than those described in Clauses (a) and (b). |  | Common Sentence | Yes | Occupant Load
2015 | ON | NBC | Div B | 3.1.17.1.(2) | Occupant Load Determination | If a floor area or part thereof has been designed for an occupant load other than that determined from Table 3.1.17.1., a permanent sign indicating that occupant load shall be posted in a conspicuous location. | obc2019_divb | Div B | 3.1.17.1.(2) | 3.1.17.1. Occupant Load Determination | If a floor area or part of it has been designed for an occupant load other than that determined from Table 3.1.17.1., a permanent sign indicating that occupant load shall be posted in a conspicuous location. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.17.1.(3) | Occupant Load Determination | For the purposes of this Article, mezzanines, tiers and balconies shall be regarded as part of the floor area. | obc2019_divb | Div B | 3.1.17.1.(3) | 3.1.17.1. Occupant Load Determination | For the purposes of this Article, mezzanines, tiers and balconies shall be regarded as part of the floor area. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.17.1.(4) | Occupant Load Determination | If a room or group of rooms is intended for different occupancies at different times, the value to be used from Table 3.1.17.1. shall be the value which gives the greatest number of persons for the occupancies concerned. | obc2019_divb | Div B | 3.1.17.1.(4) | 3.1.17.1. Occupant Load Determination | If a room or group of rooms is intended for different occupancies at different times, the value to be used from Table 3.1.17.1. shall be the value that gives the greatest number of persons for the occupancies concerned. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.2.1.(1) | Classification of Buildings | Except as permitted by Articles 3.1.2.3. to 3.1.2.5., every building or part thereof shall be classified according to its major occupancy as belonging to one of the Groups or Divisions described in Table 3.1.2.1. (See Note A-3.1.2.1.(1).) | obc2019_divb | Div B | 3.1.2.1.(1) | 3.1.2.1. Classification of Buildings | Except as provided by Articles 3.1.2.3. to 3.1.2.7., every building or part of it shall be classified according to its major occupancy as belonging to one of the Groups or Divisions described in Table 3.1.2.1. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.2.1.(2) | 3.1.2.1. Classification of Buildings | A building intended for use by more than one major occupancy shall be classified according to all major occupancies for which it is used or intended to be used. | obc2019_divb | Div B | 3.1.2.1.(2) | 3.1.2.1. Classification of Buildings | A building intended for use by more than one major occupancy shall be classified according to all major occupancies for which it is used or intended to be used. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.2.2.(1) | 3.1.2.2. Occupancies of the Same Classification | Any building is deemed to be occupied by a single major occupancy, notwithstanding its use for more than one major occupancy, provided that all occupancies are classified as belonging to the same Group classification or, where the Group is divided into Divisions, as belonging to the same Division classification described in Table 3.1.2.1. | obc2019_divb | Div B | 3.1.2.2.(1) | 3.1.2.2. Occupancies of the Same Classification | Any building is deemed to be occupied by a single major occupancy, notwithstanding its use for more than one major occupancy, provided that all occupancies are classified as belonging to the same Group classification or, where the Group is divided into Divisions, as belonging to the same Division classification described in Table 3.1.2.1. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.2.3.(1) | Arena-Type Buildings | An arena-type building intended for occasional use for trade shows and similar exhibition purposes shall be classified as a Group A, Division 3 occupancy. (See Note A-3.1.2.3.(1).) | obc2019_divb | Div B | 3.1.2.3.(1) | 3.1.2.3. Arena Type Buildings | An arena type building intended for occasional use for trade shows and similar exhibition purposes shall be classified as Group A, Division 3 occupancy. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.2.4.(1) | 3.1.2.4 Police Stations | A police station with detention quarters is permitted to be classified as a Group B, Division 2 major occupancy provided the station is not more than 1 storey in building height and 600 m2 in building area. | obc2019_divb | Div B | 3.1.2.4.(1) | 3.1.2.4. Police Stations | A police station with detention quarters is permitted to be classified as a Group B, Division 2 major occupancy provided the station is not more than 1 storey in building height and 600 m2 in building area. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.2.5.(1) | 3.1.2.5. Convalescent and Children's Custodial Homes | Convalescent homes and children’s custodial homes are permitted to be classified as residential occupancies within the application of Part 3, provided that occupants are ambulatory and live as a single housekeeping unit in a suite with sleeping accommodation for not more than 10 persons. | obc2019_divb | Div B | 3.1.2.5.(1) | 3.1.2.5 Group B, Division 3 Occupancies | Group B, Division 3 occupancies are permitted to be classified as Group C major occupancies provided, (a) the occupants live as a single housekeeping unit in a suite with sleeping accommodation for not more than 10 persons, and (b) not more than two occupants require assistance in evacuation in case of an emergency. |  | Common Sentence | Yes | Occupancy Classification
2015 | ON | NBC | Div B | 3.1.2.6.(1) | Storage of Combustible Fibres | Buildings or parts thereof used for the storage of baled combustible fibres shall be classified as medium-hazard industrial occupancies. | obc2019_divb | Div B | 3.1.2.7.(1) | 3.1.2.7. Storage of Combustible Fibres | Buildings or parts of them used for the storage of baled combustible fibres shall be classified as medium hazard industrial occupancies. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.3.1.(1) | Separation of Major Occupancies | Except as permitted by Sentences (2) and (3), major occupancies shall be separated from adjoining major occupancies by fire separations having fire-resistance ratings conforming to Table 3.1.3.1. | obc2019_divb | Div B | 3.1.3.1.(1) | 3.1.3.1. Separation of Major Occupancies | Except as provided by Sentences (2) to (5), major occupancies shall be separated from adjoining major occupancies by fire separations having fire-resistance ratings conforming to Table 3.1.3.1. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.3.1.(1) | Separation of Major Occupancies | Except as permitted by Sentences (2) and (3), major occupancies shall be separated from adjoining major occupancies by fire separations having fire-resistance ratings conforming to Table 3.1.3.1. | obc2019_divb | Div B | 3.1.3.1.(3) | 3.1.3.1. Separation of Major Occupancies | In a building within the scope of Article 3.2.2.43A., a fire separation with a 2 h fire-resistance rating is required between the Group C and Group A, Division 2 major occupancies |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.3.1.(1) | Separation of Major Occupancies | Except as permitted by Sentences (2) and (3), major occupancies shall be separated from adjoining major occupancies by fire separations having fire-resistance ratings conforming to Table 3.1.3.1. | obc2019_divb | Div B | 3.1.3.1.(4) | 3.1.3.1. Separation of Major Occupancies | In a building within the scope of Article 3.2.2.50A., a fire separation with a 2 h fire-resistance rating is required between the Group D and Group A, Division 2 major occupancies. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.3.1.(2) | Separation of Major Occupancies | In a building not more than 3 storeys in building height, if not more than 2 dwelling units are contained together with a Group E major occupancy, the fire-resistance rating of the fire separation between the 2 major occupancies need not be more than 1 h. | obc2019_divb | Div B | 3.1.3.1.(2) | 3.1.3.1. Separation of Major Occupancies | In a building not more than 3 storeys in building height, if not more than two dwelling units are contained together with a Group E major occupancy, the fire-resistance rating of the fire separation between the two major occupancies need not be more than 1 h. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.3.1.(3) | Separation of Major Occupancies | In a building conforming to the requirements of Articles 3.2.8.2. to 3.2.8.8., the requirements of Sentence (1) for fire separations between major occupancies do not apply at the vertical plane around the perimeter of an opening through the horizontal fire separation. | obc2019_divb | Div B | 3.1.3.1.(5) | 3.1.3.1. Separation of Major Occupancies | The fire separations required between major occupancies in Sentence (1) are permitted to be penetrated by floor openings protected in conformance with Subsection 3.2.8., except for fire separations for Group F, Division 1 major occupancies and for mezzanines described in Sentence 3.2.8.2.(1). |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.1.3.2.(2) | Prohibition of Occupancy Combinations | Not more than one suite of residential occupancy shall be contained within a building classifiedasa Group F, Division 2 major occupancy. | obc2019_divb | Div B | 3.1.3.2.(2) | 3.1.3.2. Prohibition of Occupancy Combinations | Except as provided in Sentence (4) and Sentence 3.10.2.4.(9), not more than one suite of residential occupancy shall be contained within a building classified as a Group F, Division 2 major occupancy. |  | Common Sentence | Yes | Live/work Units
2015 | ON | NBC | Div B | 3.1.3.2.(3) | Prohibition of Occupancy Combinations | A building conforming to Article 3.2.2.50. shall not contain (a) except as provided in Sentence (5), a Group A, Division 1 or 3, Group B, or Group F, Division 2 or 3 major occupancy, or (b) a Group A, Division 2 or Group E major occupancy above the second storey. (See Note A-3.1.3.2.(3) to (5).) A building conforming to Article 3.2.2.58. shall not contain (a) a Group A, Division 1 or 3, Group B, or Group F, Division1 major occupancy, or (b) except as provided in Sentence (5), a Group A, Division 2, Group E, or Group F, Division 2 or 3 major occupancy above the second storey. (See Note A-3.1.3.2.(3) to (5).) | obc2019_divb | Div B | 3.1.3.2.(5) | 3.1.3.2. Prohibition of Occupancy Combinations | A building within the scope of Article 3.2.2.43A. or 3.2.2.50A. shall not contain, (a) a Group A, Division 1 or 3, Group B, or Group F, Division 1 or 2 major occupancy, (b) a Group A, Division 2 or a Group E major occupancy above the second storey, (b.1) a retirement home, or (c) except as permitted by Sentence (6), a Group F, Division 3 major occupancy. |  | Common Sentence | Yes | Mid-rise Wood
2015 | ON | NBC | Div B | 3.1.3.2.(3) | Prohibition of Occupancy Combinations Door Release Hardware | Electromagnetic locks that do not incorporate latches, pins or other similar devices to keep the door in the closed position are permitted to be installed on doors in Group B, Division 2 and Division 3 occupancies, provided (a) the building is (i) equipped with a fire alarm system, and (ii) sprinklered, (b) the electromagnetic lock releases upon (i) actuation of the alarm signal from the building’s fire alarm system, (ii) loss of its power supply and of power to its auxiliary controls, (iii) actuation of a manually operated switch that is readily accessible at a constantly attended location within the locked space, and (iv) actuation of the manual station installed within 0.5 m of each door and equipped with an auxiliary contact, which directly releases the electromagnetic lock, (c) upon release, the electromagnetic lock requires manual resetting by actuation of the switch referred to in Subclause 3.4.6.16.(5)(b)(iii), (d) a legible sign with the words “EMERGENCY EXIT UNLOCKED BY FIREALARM”written in letters at least 25 mmhigh with a stroke at least 5 mmwide is permane ntly mounted on the door, (e) the operation of any by-pass switch, where provided for testing of the fire alarm system, sets off an audible signal and a visual signal at the fire alarm annunciator panel and at the monitoring station referred to in Sentence 3.2.4.7.(4), and (f) emergency lighting is provided at the doors. (See Note A- 3.4.6.16.(5).) | obc2019_divb | Div B | 3.4.6.16.(6) | 3.4.6.16. Door Release Hardware | Electromagnetic locks are permitted to be installed on an exterior door leading from an exit stairway in a building containing only a Group B, Division 2 major occupancy, a Group B, Division 3 major occupancy or a retirement home. |  | Common Sentence | Yes | Electromagnetic Locks
2015 | ON | NBC | Div B | 3.1.3.2.(5) | Prohibition of Occupancy Combinations | A building conforming to Article 3.2.2.50.or 3.2.2.58.is permitted to contain a storage garage below the fourth storey. (See Note A-3.1.3.2.(3) to (5).) (See also Sentence 4.4.2.1.(1).) | obc2019_divb | Div B | 3.1.3.2.(6) | 3.1.3.2. Prohibition of Occupancy Combinations | A storage garage below the third storey is permitted in a building within the scope of Article 3.2.2.43A. or 3.2.2.50A. |  | Common Sentence | Yes | Mid-rise Wood
2015 | ON | NBC | Div B | 3.1.4.1.(1) | Combustible Materials Permitted | A building permitted to be of combustible construction is permitted to be constructed of combustible materials, with or without noncombustible components. (See Note A-3.1.4.1.(1).) | obc2019_divb | Div B | 3.1.4.1.(1) | 3.1.4.1. Combustible Materials Permitted | Except as required by this Part, a building permitted to be of combustible construction is permitted to be constructed of combustible materials, with or without noncombustible components. (See Appendix A.) |  | Common Sentence | Yes | Construction Materials
2015 | ON | NBC | Div B | 3.1.4.1.(2) | Combustible Materials Permitted | The flame-spread rating on any exposed surface of foamed plastic insulation, and on any surface that would be exposed by cutting through the insulation in any direction, shall be not more than 500. | obc2019_divb | Div B | 3.1.4.2.(2) | 3.1.4.2. Protection of Foamed Plastics (See Appendix A.) | The flame-spread rating on any exposed surface of combustible insulation, or any surface that would be exposed by cutting through it in any direction, shall be not more than 500. |  | Common Sentence | Yes | Construction Materials
2015 | ON | NBC | Div B | 3.1.4.2.(1) | Protection of Foamed Plastics | Except as permitted in Sentence (2), foamed plastics that form part of a wall or ceiling assembly in combustible construction shall be protected from adjacent spaces in the building, other than adjacent concealed spaces within attic or roof spaces, crawl spaces, and wall and ceiling assemblies, (a) by one of the interior finishes described in Subsections 9.29.4 to 9.29.9, (b) provided the building does not contain a Group A, Group B or Group C major occupancy, by sheet metal (i) mechanically fastened to the supporting assembly independent of the insulation, (ii) not less than 0.38 mm thick, and (iii) with a melting point not below 650Â°C, or (c) by any thermal barrier that meets the requirements of Sentence 3.1.5.15.(2) (see Note A-3.1.4.2.(1)(c)). | obc2019_divb | Div B | 3.1.4.2.(1) | 3.1.4.2. Protection of Foamed Plastics (See Appendix A.) | Except as permitted in Sentence (3), foamed plastics that form part of a wall or ceiling assembly in combustible construction shall be protected from adjacent spaces in the building, other than adjacent concealed spaces within attic or roof spaces, crawl spaces, and wall and ceiling assemblies, by any of the following: (a) one of the interior finishes described in Subsections 9.29.4. to 9.29.9., (b) provided the building does not contain a Group A, Group B or Group C major occupancy, sheet metal that, (i) is mechanically fastened to the supporting assembly independent of the insulation, (ii) is not less than 0.38 mm thick, and (iii) has a melting point not less than 650°C, or (c) any thermal barrier that meets the requirements of Sentence 3.1.5.12A.(2). (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.4.2.(2) | Protection of Foamed Plastics | A walk-in cooler or freezer consisting of factory-assembled wall, floor or ceiling panels containing foamed plastics is permitted in a building required to be of combustible construction, provided the panels (a) are protected on both sides by sheet metal not less than 0.38 mm thick having a melting point not less than 650°C, (b) do not contain an air space, and (c) when a sample panel with an assembled joint typical of field installation is subjected to the applicable test described in Subsection 3.1.12., have a flame-spread rating not more than that permitted for the space in which they are located or the space that they bound, as applicable. | obc2019_divb | Div B | 3.1.4.2.(3) | 3.1.4.2. Protection of Foamed Plastics (See Appendix A.) | A walk-in cooler or freezer consisting of factory-assembled wall, floor or ceiling panels containing foamed plastics is permitted to be used in a building permitted to be of combustible construction, provided the panels, (a) are protected on both sides by sheet metal not less than 0.38 mm thick having a melting point not less than 650°C, (b) do not contain an air space, and (c) when a sample panel with an assembled joint typical of field installation is subjected to the applicable test described in Subsection 3.1.12., have a flame-spread rating not more than that permitted for the space in which they are located, the space that they bound, or the walls of the building to which the cooler or freezer is attached, as applicable. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.4.2.(3) | Protection of Foamed Plastics | The flame-spread rating of doors containing foamed plastics shall comply with Sentences 3.1.13.2.(1) to 3.1.13.2.(3). | obc2019_divb | Div B | 3.1.4.2.(4) | 3.1.4.2. Protection of Foamed Plastics (See Appendix A.) | The flame-spread rating of doors containing foamed plastics shall comply with Sentences 3.1.13.2.(1) to (3). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.4.3.(1) | Wires and Cables | Except as required by Sentence (2), optical fibre cables and electrical wires and cables with combustible insulation, jackets or sheathes that are installed in a building permitted to be of combustible construction shall (a) not convey flame or continue to burn for more than 1 min when tested in conformance with the Vertical Flame Test (FT1 rating) in CSA C22.2 No. 0.3-09 Test Methods for Electrical Wires and Cables or (b) be located in (i) totally enclosed noncombustible raceways (see Note A-3.1.4.3.(1)(b)(i)), (ii) masonry walls, (iii) concrete slabs, or (iv) totally enclosed non-metallic raceways conforming to Clause 3.1.5.23.(1)(b). | obc2019_divb | Div B | 3.1.4.3.(1) | 3.1.4.3. Wires and Cables (See Appendix A.) | Except as permitted by Sentences (2) and (3), optical fibre cables and electrical wires and cables with combustible insulation, jackets or sheathes installed in a building permitted to be of combustible construction shall, (a) not convey flame or continue to burn for more than 1 min when tested in conformance with the Vertical Flame Test in Clause 4.11.1. of CSA C22.2 No. 0.3, "Test Methods for Electrical Wires and Cables (FT1 Rating)", or (b) be located in, (i) totally enclosed noncombustible raceways, (See Appendix A.) (ii) concealed spaces in walls, (iii) concrete slabs, or (iv) totally enclosed nonmetallic raceways conforming to Clause 3.1.5.20(1)(b). |  | Common Sentence | Yes | Construction Materials
2015 | ON | NBC | Div B | 3.1.4.4.(1) | Non-metallic Raceways | Totally enclosed non-metallic raceways used in a plenum in a building permitted to be of combustible construction shall meet the requirements of Clause 3.1.5.23.(1)(a). | obc2019_divb | Div B | 3.1.4.4.(1) | 3.1.4.4. Nonmetallic Raceways | Totally enclosed nonmetallic raceways used in a plenum in a building permitted to be of combustible construction shall meet the requirements of Clause 3.1.5.20.(1)(a). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.4.5.(1) | Fire-Retardant-Treated Wood | If fire-retardant-treated wood is specified in this Part, the wood shall (a) be pressure impregnated with fire-retardant chemicals in conformance with CSA CAN/CSA-O80 Series-08 Wood Preservation and (b) have a flame-spread rating not more than 25. | obc2019_divb | Div B | 3.1.4.5.(1) | 3.1.4.5. Fire-Retardant Treated Wood | If fire-retardant treated wood is specified in this Part, the wood shall, (a) be pressure impregnated with fire-retardant chemicals in conformance with CAN/CSA-O80 Series, "Wood Preservation", and (b) have a flame-spread rating not more than 25. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.4.6.(1) | Heavy Timber Construction Alternative | If combustible construction is permitted and is not required to have a fire-resistance rating more than 45 min, heavy timber construction is permitted to be used. | obc2019_divb | Div B | 3.1.4.6.(1) | Heavy Timber Construction Alternative | If combustible construction is permitted and is not required to have a fire-resistance rating more than 45 min, heavy timber construction is permitted to be used. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.4.6.(2) | Heavy Timber Construction Alternative | If heavy timber construction is permitted, it shall conform to Article 3.1.4.7. | obc2019_divb | Div B | 3.1.4.6.(2) | Heavy Timber Construction Alternative | If heavy timber construction is permitted, it shall conform to Article 3.1.4.7. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.4.7.(1) | Heavy Timber Construction | Wood elements in heavy timber construction shall be arranged in heavy solid masses and with essentially smooth flat surfaces to avoid thin sections and sharp projections. | obc2019_divb | Div B | 3.1.4.7.(1) | 3.1.4.7. Heavy Timber Construction | Wood elements in heavy timber construction shall be arranged in heavy solid masses and with essentially smooth flat surfaces to avoid thin sections and sharp projections. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.4.7.(1) | Slide Escapes | Wood elements in heavy timber construction shall be arranged in heavy solid masses and with essentially smooth flat surfaces to avoid thin sections and sharp projections. | obc2019_divb | Div B | 3.4.1.7.(1) | Slide Escapes | A slide escape shall not be erected on any building as a required exit, but is permitted to be provided as an additional egress facility if unusual hazards are foreseen. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.4.7.(10) | Heavy Timber Construction | Wood girders and beams in heavy timber construction shall be closely fitted to columns, and adjoining ends shall be connected by ties or caps to transfer horizontal loads across the joints. | obc2019_divb | Div B | 3.1.4.7.(10) | 3.1.4.7. Heavy Timber Construction | Wood girders and beams in heavy timber construction shall be closely fitted to columns, and adjoining ends shall be connected by ties or caps to transfer horizontal loads across the joints. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.4.7.(11) | Heavy Timber Construction | In heavy timber construction, intermediate wood beams used to support a floor shall be supported on top of the girders or on metal hangers into which the ends of the beams are closely fitted. | obc2019_divb | Div B | 3.1.4.7.(11) | 3.1.4.7. Heavy Timber Construction | In heavy timber construction, intermediate wood beams used to support a floor shall be supported on top of the girders or on metal hangers into which the ends of the beams are closely fitted. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.4.7.(12) | Heavy Timber Construction | Roof arches supported on the tops of walls or abutments, roof trusses, roof beams and roof girders in heavy timber construction are permitted to be not less than 64 mm wide provided (a) where two or more spaced members are used, the intervening spaces are (i) blocked solidly throughout, or (ii) tightly closed by a continuous wood cover plate not less than 38 mm thick secured to the underside of the members, or (b) the underneath of the roof deck or sheathing is sprinklered. | obc2019_divb | Div B | 3.1.4.7.(12) | 3.1.4.7. Heavy Timber Construction | Roof arches supported on the tops of walls or abutments, roof trusses, roof beams and roof girders in heavy timber construction are permitted to be not less than 64 mm wide provided, (a) where two or more spaced members are used, the intervening spaces are, (i) blocked solidly throughout, or (ii) tightly closed by a continuous wood cover plate not less than 38 mm thick secured to the underside of the members, or (b) the space below the roof deck or sheathing is sprinklered. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.4.7.(2) | Heavy Timber Construction | Except as permitted by Sentences 3.1.4.7.(3) to 3.1.4.7.(6) and 3.1.4.7.(12), the minimum dimensions of wood elements in heavy timber construction shall conform to Table 3.1.4.7. | obc2019_divb | Div B | 3.1.4.7.(2) | 3.1.4.7. Heavy Timber Construction | Except as permitted by Sentences (3) to (6) and (12), the minimum dimensions of wood elements in heavy timber construction shall conform to Table 3.1.4.7. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.4.7.(3) | Heavy Timber Construction | Where splice plates are used at splices of roof arches supported on the tops of walls or abutments, roof trusses, roof beams and roof girders in heavy timber construction, they shall be not less than 64 mm thick. | obc2019_divb | Div B | 3.1.4.7.(3) | 3.1.4.7. Heavy Timber Construction | Where splice plates are used at splices of roof arches supported on the tops of walls or abutments, roof trusses, roof beams and roof girders in heavy timber construction, they shall be not less than 64 mm thick. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.4.7.(4) | Heavy Timber Construction | Floors in heavy timber construction shall be of glued-laminated or solid sawn plank not less than 64 mm thick, splined or tongued and grooved, or 38 mm wide and 89 mm deep set on edge and well spiked together. | obc2019_divb | Div B | 3.1.4.7.(4) | 3.1.4.7. Heavy Timber Construction | Floors in heavy timber construction shall be of glued-laminated or solid sawn plank not less than, 64 mm thick, splined or tongued and grooved, or 38 mm wide and 89 mm deep set on edge and well-spiked together. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.4.7.(5) | Heavy Timber Construction | Floors in heavy timber construction shall be laid, (a) so that no continuous line of end joints will occur except at points of support, and covered with, (i) tongued and grooved flooring not less than 19 mm thick laid cross-wise or diagonally, or (ii) tongued and grooved phenolic-bonded plywood, strandboard or waferboard not less than 12.5 mm thick, and (b) not closer than 15 mm to the walls to provide for expansion, with the gap covered at the top or bottom. | obc2019_divb | Div B | 3.1.4.7.(5) | 3.1.4.7. Heavy Timber Construction | Floors in heavy timber construction shall be laid, (a) so that no continuous line of end joints will occur except at points of support, and covered with, (i) tongued and grooved flooring not less than 19 mm thick laid cross-wise or diagonally, or (ii) tongued and grooved phenolic-bonded plywood, strandboard or waferboard not less than 12.5 mm thick, and (b) not closer than 15 mm to the walls to provide for expansion, with the gap covered at the top or bottom. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.4.7.(6) | Heavy Timber Construction | Roofs in heavy timber construction shall be of tongued and grooved phenolic-bonded plywood, strandboard or waferboard not less than 28 mm thick, or glued-laminated or solid sawn plank that is not less than 38 mm thick, splined or tongued and grooved, or not less than 38 mm wide and 64 mm deep set on edge and laid so that no continuous line of end joints will occur except at the points of support. | obc2019_divb | Div B | 3.1.4.7.(6) | 3.1.4.7. Heavy Timber Construction | Roofs in heavy timber construction shall be of tongued and grooved phenolic-bonded plywood, strandboard or waferboard not less than 28 mm thick, or glued-laminated or solid sawn plank that is, not less than 38 mm thick, splined or tongued and grooved, or not less than 38 mm wide and 64 mm deep set on edge and laid so that no continuous line of end joints will occur except at the points of support. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.4.7.(7) | Heavy Timber Construction | Wood columns in heavy timber construction shall be continuous or superimposed throughout all storeys. | obc2019_divb | Div B | 3.1.4.7.(7) | 3.1.4.7. Heavy Timber Construction | Wood columns in heavy timber construction shall be continuous or superimposed throughout all storeys. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.4.7.(8) | Heavy Timber Construction | Superimposed wood columns in heavy timber construction shall be connected by reinforced concrete or metal caps with brackets, steel or iron caps with pintles and base plates, or timber splice plates fastened to the columns by metal connectors housed within the contact faces. | obc2019_divb | Div B | 3.1.4.7.(8) | 3.1.4.7. Heavy Timber Construction | Superimposed wood columns in heavy timber construction shall be connected by, reinforced concrete or metal caps with brackets, steel or iron caps with pintles and base plates, or timber splice plates fastened to the columns by metal connectors housed within the contact faces. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.4.7.(9) | Heavy Timber Construction | Where beams and girders in heavy timber construction enter masonry, wall plates, boxes of the self-releasing type or hangers shall be used. | obc2019_divb | Div B | 3.1.4.7.(9) | 3.1.4.7. Heavy Timber Construction | Where beams and girders in heavy timber construction enter masonry, wall plates, boxes of the self-releasing type or hangers shall be used. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.4.8.(1) | Exterior Cladding | Not less than 90% of the exterior cladding on each exterior wall of buildings conforming to Article 3.2.2.50. or 3.2.2.58.shall consist of (a) noncombustible cladding, or (b) a wall assembly that satisfies the criteria of Clause 3.1.5.5.(1)(b). (See Note A-3.1.4.8.(1).)(SeealsoNotes A-3.1.5.5.(1)(b)(i)and A-3.1.5.5.(1)(b)(ii).) | obc2019_divb | Div B | 3.1.4.8.(1) | 3.1.4.8. Cladding | Except as permitted by Sentence 3.2.3.7.(6), cladding for a building within the scope of Article 3.2.2.43A. or 3.2.2.50A. that exceeds 4 storeys in building height or cladding for a fire compartment in such a building shall be noncombustible. |  | Common Sentence | Yes | Mid-rise Wood
2015 | ON | NBC | Div B | 3.1.5.1.(1) | Noncombustible Materials | Except as permitted by Sentences 3.1.5.1.(2) to 3.1.5.1.(4) and Articles 3.1.5.2. to 3.1.5.24., Article 3.1.13.4. and Article 3.2.2.16., a building or part of a building required to be of noncombustible construction shall be constructed with noncombustible materials. (See also part 3. for the requirements regarding the flame-spread rating of interior finishes.) | obc2019_divb | Div B | 3.1.5.1.(1) | 3.1.5.1. Noncombustible Materials | Except as permitted by Sentences (2) to (4) and Articles 3.1.5.2. to 3.1.5.25., 3.1.13.4. and 3.2.2.16., a building or part of a building required to be of noncombustible construction, shall be constructed with noncombustible materials. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.1.(2) | Noncombustible Materials | Notwithstanding the definition of noncombustible materials stated in Article 1.4.1.2., a material is permitted to be used in noncombustible construction provided that, when tested in accordance with ULC ULC-S135-04 Test Method for the Determination of Combustibility Parameters of Building Materials Using an Oxygen Consumption Calorimeter (Cone Calorimeter) at a heat flux of 50 kW/m2 , (a) its average total heat release is not more than 3 MJ/m2 , (b) its average total smoke extinction area is not more than 1.0 m2 , and (c) the test duration is extended beyond the time stipulated in the referenced standard until it is clear that there is no further release of heat or smoke. | obc2019_divb | Div B | 3.1.5.1.(2) | 3.1.5.1. Noncombustible Materials | Notwithstanding the definition for noncombustible materials stated in Article 1.4.1.2. of Division A, a material is permitted to be used in noncombustible construction provided that, when tested in accordance with ULC S135, "Test Method for the Determination of Combustibility Parameters of Building Materials Using an Oxygen Consumption Calorimeter (Cone Calorimeter)", at a heat flux of 50 kW/m2, (a) its average total heat release is not more than 3 MJ/m2, (b) its average total smoke extinction area is not more than 1.0 m2, and (c) the test duration is extended beyond the time stipulated in the referenced standard until it is clear that there is no further release of heat or smoke. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.1.(3) | Noncombustible Materials | If a material referred to in Sentence 3.1.5.1.(2) consists of a number of discrete layers and testing reveals that the surface layer or layers protect the underlying layers such that complete combustion of the underlying layers does not occur, the test shall be repeated by removing the outer layers sequentially until all layers have been exposed during testing, or until complete combustion has occurred. | obc2019_divb | Div B | 3.1.5.1.(3) | 3.1.5.1. Noncombustible Materials | If a material referred to in Sentence (2) consists of a number of discrete layers and testing reveals that the surface layer or layers protect the underlying layers such that the complete combustion of the underlying layers does not occur, the test shall be repeated by removing the outer layers sequentially until all layers have been exposed during testing, or until complete combustion has occurred. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.1.(4) | Noncombustible Materials | The acceptance criteria for a material tested in accordance with Sentence 3.1.5.1.(3) shall be based on the cumulative emissions from all layers, which must not exceed the criteria stated in Clauses 3.1.5.1.(2) and 3.1.5.1.(2). | obc2019_divb | Div B | 3.1.5.1.(4) | 3.1.5.1. Noncombustible Materials | The acceptance criteria for a material tested in accordance with Sentence (3) shall be based on the cumulative emissions from all layers, which must not exceed the criteria stated in Clauses (2)(a) and (b). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.10.(1) | Combustible Flooring Elements | Combustiblestage flooring supported on noncombustible structural members is permitted in a building required to be of noncombustible construction. | obc2019_divb | Div B | 3.1.5.8.(1) | 3.1.5.7. Combustible Millwork | Combustible millwork, including interior trim, doors and door frames, show windows together with their frames, aprons and backing, handrails, shelves, cabinets and counters, is permitted in a building required to be of noncombustible construction. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.10.(2) | Combustible Flooring Elements | Wood members more than 50 mm but not more than 300 mm high applied directly to or set into a noncombustible floor slab are permitted for the construction of a raised platform in a building required to be of noncombustible construction provided the concealed spaces created are divided into compartments by fire blocks in conformance with Sentence 3.1.11.3.(2). | obc2019_divb | Div B | 3.1.5.8.(2) | 3.1.5.8. Combustible Flooring Elements | Wood members more than 50 mm but not more than 375 mm high applied directly to or set into a noncombustible floor slab are permitted for the construction of a raised platform in a building required to be of noncombustible construction provided the concealed spaces created are divided into compartments by fire blocks in conformance with Sentence 3.1.11.3.(2). |  | Common Sentence | Yes | Construction Materials
2015 | ON | NBC | Div B | 3.1.5.10.(3) | Combustible Flooring Elements | The floor system for the raised platform referred to in Sentence 3.1.5.10.(2) is permitted to include a combustible subfloor and combustible finished flooring. | obc2019_divb | Div B | 3.1.5.8.(3) | 3.1.5.8. Combustible Flooring Elements | The floor system for the raised platform referred to in Sentence (2) is permitted to include combustible subfloor and combustible finished flooring. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.11.(1) | Combustible Stairs in Dwelling Units | Combustible stairs are permitted in a dwelling unit in a building required to be of noncombustible construction. | obc2019_divb | Div B | 3.1.5.9.(1) | 3.1.5.8. Combustible Flooring Elements | Combustible stage flooring supported on noncombustible structural members is permitted in a building required to be of noncombustible construction. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.12.(1) | Combustible Interior Finishes | Except as permitted in Sentences 3.1.5.12.(2) and 3.1.5.12.(3), combustible interior wall and ceiling finishes referred to in Clause 3.1.13.1.(2)(b) that are not more than 1 mm thick are permitted in a building required to be of noncombustible construction. | obc2019_divb | Div B | 3.1.5.10.(1) | 3.1.5.10. Combustible Interior Finish | Except as provided in Sentences (2) and (3), combustible interior wall and ceiling finishes described in Clause 3.1.13.1.(1)(b) that are not more than 1 mm thick are permitted in a building required to be of noncombustible construction. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.12.(3) | Combustible Interior Finishes | Except as provided in Sentence 3.1.5.12.(4), combustible interior ceiling finishes, other than foamed plastics, that are not more than 25 mm thick are permitted in a building required to be of noncombustible construction, provided they have a flame-spread rating not more than 25 on any exposed surface or on any surface that would be exposed by cutting through the material in any direction, except that not more than 10% of the ceiling area within each fire compartment is permitted to have a flame-spread rating not more than 150. | obc2019_divb | Div B | 3.1.5.10.(3) | 3.1.5.10. Combustible Interior Finish | Except as provided in Sentence (4), combustible interior ceiling finishes, other than foamed plastics, that are not more than 25 mm thick are permitted in a building required to be of noncombustible construction, provided that, (a) they have a flame-spread rating not more than 25 on any exposed surface or on any surface that would be exposed by cutting through the material in any direction, and (b) not more than 10% of the ceiling area within each fire compartment where such finishes are installed has a flame-spread rating not more than 150. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.13.(1) | Gypsum Board | Gypsum board with a tightly adhering paper covering not more than 1 mm thick is permitted in a building required to be of noncombustible construction provided the flame-spread rating on the surface is not more than 25. | obc2019_divb | Div B | 3.1.5.11.(1) | 3.1.5.11. Gypsum Board | Gypsum board with a tightly adhering paper covering not more than 1 mm thick is permitted in a building required to be of noncombustible construction provided the flame-spread rating of the surface is not more than 25. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.14.(1) | Combustible Insulation | Foamed plastic insulation shall conform to Article 3.1.5.15. | obc2019_divb | Div B | 3.1.5.12.(1) | 3.1.5.12. Combustible Insulation | Foamed plastic insulation shall conform to Article 3.1.5.12A. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.14.(4) | Combustible Insulation | Except as provided in Sentences 3.1.5.14.(5) and 3.1.5.14.(6), combustible insulation with a flame-spread rating more than 25 but not more than 500 on any exposed surface, or any surface that would be exposed by cutting through the material in any direction, is permitted in a building required to be of noncombustible construction, provided the insulation is protected from adjacent space in the building, other than adjacent concealed spaces within wall assemblies, by a thermal barrier consisting of (a) not less than 12.7 mm thick gypsum board mechanically fastened to a supporting assembly independent of the insulation, (b) lath and plaster, mechanically fastened to a supporting assembly independent of the insulation, (c) masonry, or (d) concrete. | obc2019_divb | Div B | 3.1.5.12.(4) | 3.1.5.12. Combustible Insulation | Except as provided in Sentences (5) and (6), combustible insulation with a flame-spread rating more than 25 but not more than 500 on any exposed surface, or any surface that would be exposed by cutting through the material in any direction, is permitted in a building required to be of noncombustible construction, provided the insulation is protected from adjacent space in the building, other than adjacent concealed spaces within wall assemblies, by a thermal barrier consisting of, (a) not less than 12.7 mm thick gypsum board mechanically fastened to a supporting assembly independent of the insulation, (b) lath and plaster, mechanically fastened to a supporting assembly independent of the insulation, (c) masonry, or (d) concrete. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.14.(5) | Combustible Insulation | Combustible insulation with a flame-spread rating more than 25 but not more than 500 on any exposed surface, or any surface that would be exposed by cutting through the material in any direction, is permitted in the exterior walls of a building required to be of noncombustible construction that is not sprinklered and is more than 18 m high, measured from grade to the underside of the roof, provided the insulation is protected from adjacent space in the building, other than adjacent concealed spaces within wall assemblies, by a thermal barrier consisting of (a) gypsum board not less than 12.7 mm thick, mechanically fastened to a supporting assembly independent of the insulation and with all joints either backed or taped and filled, (b) lath and plaster, mechanically fastened to a supporting assembly independent of the insulation, (c) masonry or concrete not less than 25 mm thick, or (d) any thermal barrier that, when tested in conformance with ULC CAN/ULC-S101-14 Fire Endurance Tests of Building Construction and Materials will not develop an average temperature rise more than 140Â°C or a maximum temperature rise more than 180Â°C at any point on its unexposed face within 10 min (see Note A-3.1.5.14.(5)(d)) (see also Article 3.2.3.7.). | obc2019_divb | Div B | 3.1.5.12.(5) | 3.1.5.12. Combustible Insulation | Combustible insulation with a flame-spread rating more than 25 but not more than 500 on any exposed surface, or any surface that would be exposed by cutting through the material in any direction, is permitted in the exterior walls of a building required to be of noncombustible construction, that is not sprinklered and is more than 18 m high, measured from grade to the underside of the roof, provided the insulation is protected from adjacent space in the building, other than adjacent concealed spaces within wall assemblies, by a thermal barrier that, (a) consists of gypsum board not less than 12.7 mm thick, mechanically fastened to a supporting assembly independent of the insulation and with all joints either backed or taped and filled, (b) consists of lath and plaster, mechanically fastened to a supporting assembly independent of the insulation, (c) consists of masonry or concrete not less than 25 mm thick, or (d) when tested in conformance with CAN/ULC-S101, "Fire Endurance Tests of Building Construction and Materials", does not develop an average temperature rise more than 140Ã‚Â°C or a maximum temperature rise more than 180Ã‚Â°C at any point on its unexposed face within 10 min. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.14.(6) | Combustible Insulation | Combustible insulation with a flame-spread rating more than 25 but not more than 500 on any exposed surface, or any surface that would be exposed by cutting through the material in any direction, is permitted in the interior walls, within ceilings and within roof assemblies of a building required to be of noncombustible construction that is not sprinklered and is more than 18 m high, measured from grade to the underside of the roof, provided the insulation is protected from adjacent space in the building, other than adjacent concealed spaces within wall assemblies, by a thermal barrier consisting of (a) Type X gypsum board not less than 15.9 mm thick, mechanically fastened to a supporting assembly independent of the insulation and with all joints either backed or taped and filled, conforming to (i) ASTM C 1177/C 1177M-13 Glass Mat Gypsum Substrate for Use as Sheathing (ii) ASTM C 1178/C 1178M-13 Coated Glass Mat Water-Resistant Gypsum Backing Panel (iii) ASTM C 1396/C 1396M-14 Gypsum Board (iv) ASTM C 1658/C 1658M-13 Glass Mat Gypsum Panels or (v) CAN/CSA-A82.27-M91 Gypsum Board (b) non-loadbearing masonry or concrete not less than 50 mm thick, (c) loadbearing masonry or concrete not less than 75 mm thick, or (d) any thermal barrier that, when tested in conformance with ULC CAN/ULC-S101-14 Fire Endurance Tests of Building Construction and Materials (i) does not develop an average temperature rise more than 140Â°C or a maximum temperature rise more than 180Â°C at any point on its unexposed face within 20 min, and (ii) remains in place for not less than 40 min. | obc2019_divb | Div B | 3.1.5.12.(6) | 3.1.5.12. Combustible Insulation | Combustible insulation with a flame-spread rating more than 25 but not more than 500 on any exposed surface, or any surface that would be exposed by cutting through the material in any direction, is permitted in the interior walls, within ceilings and within roof assemblies of a building required to be of noncombustible construction, that is not sprinklered and is more than 18 m high, measured from grade to the underside of the roof, provided the insulation is protected from adjacent space in the building, other than adjacent concealed spaces within wall assemblies, by a thermal barrier that, (a) consists of Type X gypsum board not less than 15.9 mm thick, mechanically fastened to a supporting assembly independent of the insulation and with all joints either backed or taped and filled, conforming to,(i) ASTM C1177 / C1177M, "Glass Mat Gypsum Substrate for Use as Sheathing", (ii) ASTM C1178 / C1178M, "Coated Glass Mat Water-Resistant Gypsum Backing Panel", (iii) ASTM C1396 / C1396M, "Gypsum Board", (iv) ASTM C1658 / C1658M, "Glass Mat Gypsum Panels", or (v) CAN/CSA-A82.27-M, "Gypsum Board", (b) consists of non-loadbearing masonry or concrete not less than 50 mm thick, (c) consists of loadbearing masonry or concrete not less than 75 mm thick, or (d) when tested in conformance with CAN/ULC-S101, "Fire Endurance Tests of Building Construction and Materials", (i) does not develop an average temperature rise more than 140°C or a maximum temperature rise more than 180°C at any point on its unexposed face within 20 min, and (ii) remains in place for not less than 40 min. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.15.(1) | Foamed Plastic Insulation | Foamed plastic insulation is permitted to be installed above roof decks, outside of foundation walls below ground level, and beneath concrete slabs-on-ground of a building required to be of noncombustible construction. | obc2019_divb | Div B | 3.1.5.12.(1) | 3.1.5.11. Gypsum Board | Gypsum board with a tightly adhering paper covering not more than 1 mm thick is permitted in a building required to be of noncombustible construction provided the flame-spread rating of the surface is not more than 25. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.15.(2) | Foamed Plastic Insulation | Except as provided in Sentences 3.1.5.15.(3) and 3.1.5.15.(4), foamed plastic insulation with a flame-spread rating not more than 500 on any exposed surface, or any surface that would be exposed by cutting through the material in any direction, is permitted in a building required to be of noncombustible construction, provided the insulation is protected from adjacent space in the building, other than adjacent concealed spaces within wall assemblies, by a thermal barrier consisting of (a) not less than 12.7 mm thick gypsum board mechanically fastened to a supporting assembly independent of the insulation, (b) lath and plaster, mechanically fastened to a supporting assembly independent of the insulation, (c) masonry, (d) concrete, or (e) any thermal barrier that meets the requirements of classification B when tested in conformance with ULC CAN/ULC-S124-06 Test for the Evaluation of Protective Coverings for Foamed Plastic | obc2019_divb | Div B | 3.1.5.12.(2) | 3.1.5.12A. Foamed Plastic Insulation | Except as provided in Sentences (3) and (4), foamed plastic insulation with a flame-spread rating not more than 500 on any exposed surface, or any surface that would be exposed by cutting through the material in any direction, is permitted in a building required to be of noncombustible construction, provided the insulation is protected from adjacent space in the building, other than adjacent concealed spaces within wall assemblies, by a thermal barrier that, (a) consists of not less than 12.7 mm thick gypsum board mechanically fastened to a supporting assembly independent of the insulation, (b) consists of lath and plaster, mechanically fastened to a supporting assembly independent of the insulation, (c) consists of masonry, (d) consists of concrete, or (e) meets the requirements of classification B when tested in conformance with CAN/ULC-S124, "Test for the Evaluation of Protective Coverings for Foamed Plastic". (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.15.(3) | Foamed Plastic Insulation | Foamed plastic insulation with a flame-spread rating more than 25 but not more than 500 on any exposed surface, or any surface that would be exposed by cutting through the material in any direction, is permitted in the exterior walls of a building required to be of noncombustible construction that is not sprinklered and is more than 18 m high, measured from grade to the underside of the roof, provided the insulation is protected from adjacent space in the building, other than adjacent concealed spaces within wall assemblies, by a thermal barrier consisting of (a) gypsum board not less than 12.7 mm thick, mechanically fastened to a supporting assembly independent of the insulation and with all joints either backed or taped and filled, (b) lath and plaster, mechanically fastened to a supporting assembly independent of the insulation, (c) masonry or concrete not less than 25 mm thick, or (d) any thermal barrier that, when tested in conformance with ULC CAN/ULC-S101-14 Fire Endurance Tests of Building Construction and Materials does not develop an average temperature rise more than 140Â°C or a maximum temperature rise more than 180Â°C at any point on its unexposed face within 10 min (see Note A-3.1.5.14.(5)(d)) (see also Article 3.2.3.7.). | obc2019_divb | Div B | 3.1.5.12.(3) | 3.1.5.12A. Foamed Plastic Insulation | Foamed plastic insulation with a flame-spread rating more than 25 but not more than 500 on any exposed surface, or any surface that would be exposed by cutting through the material in any direction, is permitted in the exterior walls of a building required to be of noncombustible construction, that is not sprinklered and is more than 18 m high, measured from grade to the underside of the roof, provided the insulation is protected from adjacent space in the building, other than adjacent concealed spaces within wall assemblies, by a thermal barrier that, (a) consists of gypsum board not less than 12.7 mm thick, mechanically fastened to a supporting assembly independent of the insulation and with all joints either backed or taped and filled, (b) consists of lath and plaster, mechanically fastened to a supporting assembly independent of the insulation, (c) consists of masonry or concrete not less than 25 mm thick, or (d) when tested in conformance with CAN/ULC-S101, "Fire Endurance Tests of Building Construction and Materials", does not develop an average temperature rise more than 140Ã‚Â°C or a maximum temperature rise more than 180Ã‚Â°C at any point on its unexposed face within 10 min. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.15.(4) | Foamed Plastic Insulation | Foamed plastic insulation with a flame-spread rating more than 25 but not more than 500 on any exposed surface, or any surface that would be exposed by cutting through the material in any direction, is permitted in the interior walls, within ceilings and within roof assemblies of a building required to be of noncombustible construction that is not sprinklered and is more than 18 m high, measured from grade to the underside of the roof, provided the insulation is protected from adjacent space in the building, other than adjacent concealed spaces within wall assemblies, by a thermal barrier consisting of (a) Type X gypsum board not less than 15.9 mm thick, mechanically fastened to a supporting assembly independent of the insulation and with all joints either backed or taped and filled, conforming to (i) ASTM C 1177/C 1177M-13 Glass Mat Gypsum Substrate for Use as Sheathing (ii) ASTM C 1178/C 1178M-13 Coated Glass Mat Water-Resistant Gypsum Backing Panel (iii) ASTM C 1396/C 1396M-14 Gypsum Board or (iv) CAN/CSA-A82.27-M91 Gypsum Board (b) non-loadbearing masonry or concrete not less than 50 mm thick, (c) loadbearing masonry or concrete not less than 75 mm thick, or (d) any thermal barrier that, when tested in conformance with ULC CAN/ULC-S101-14 Fire Endurance Tests of Building Construction and Materials (i) does not develop an average temperature rise more than 140Â°C or a maximum temperature rise more than 180Â°C at any point on its unexposed face within 20 min, and (ii) remains in place for not less than 40 min. | obc2019_divb | Div B | 3.1.5.12.(4) | 3.1.5.12A. Foamed Plastic Insulation | Foamed plastic insulation with a flame-spread rating more than 25 but not more than 500 on any exposed surface, or any surface that would be exposed by cutting through the material in any direction, is permitted in the interior walls, within ceilings and within roof assemblies of a building required to be of noncombustible construction, that is not sprinklered and is more than 18 m high, measured from grade to the underside of the roof, provided the insulation is protected from adjacent space in the building, other than adjacent concealed spaces within wall assemblies, by a thermal barrier that, (a) consists of Type X gypsum board not less than 15.9 mm thick, mechanically fastened to a supporting assembly independent of the insulation and with all joints either backed or taped and filled, conforming to, (i) ASTM C1177 / C1177M, "Glass Mat Gypsum Substrate for Use as Sheathing", (ii) ASTM C1178 / C1178M, "Coated Glass Mat Water-Resistant Gypsum Backing Panel", (iii) ASTM C1396 / C1396M, "Gypsum Board", or (iv) CAN/CSA-A82.27-M, "Gypsum Board", (b) consists of non-loadbearing masonry or concrete not less than 50 mm thick, (c) consists of loadbearing masonry or concrete not less than 75 mm thick, or (d) when tested in conformance with CAN/ULC-S101, "Fire Endurance Tests of Building Construction and Materials", (i) does not develop an average temperature rise more than 140°C or a maximum temperature rise more than 180°C at any point on its unexposed face within 20 min, and (ii) remains in place for not less than 40 min. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.16.(1) | Combustible Elements in Partitions | Except as permitted by Sentence 3.1.5.16.(2), solid lumber partitions not less than 38 mm thick and wood framing in partitions located in a fire compartment not more than 600 m2 in area are permitted to be used in a building required to be of noncombustible construction in a floor area that is not sprinklered throughout provided the partitions (a) are not required fire separations, and (b) are not located in a care, treatment or detention occupancy. | obc2019_divb | Div B | 3.1.5.13.(1) | 3.1.5.13. Combustible Elements in Partitions | Except as permitted by Sentence (2), solid lumber partitions not less than 38 mm thick and wood framing in partitions located in a fire compartment not more than 600 m2 in area are permitted to be used in a building required to be of noncombustible construction in a floor area that is not sprinklered provided the partitions, (a) are not required fire separations, and (b) are not located in a care, care and treatment or detention occupancy or in a retirement home. |  | Common Sentence | Yes | Retirement Homes
2015 | ON | NBC | Div B | 3.1.5.16.(2) | Combustible Elements in Partitions | Partitions installed in a building of noncombustible construction are permitted to contain wood framing provided (a) the building is not more than 3 storeys in building height, (b) the partitions are not located in a care, treatment or detention occupancy, and (c) the partitions are not installed as enclosures for exits or vertical service spaces. | obc2019_divb | Div B | 3.1.5.13.(2) | 3.1.5.13. Combustible Elements in Partitions | Partitions installed in a building required to be of noncombustible construction are permitted to contain wood framing provided, (a) the building is not more than 3 storeys in building height, (b) the partitions are not located in a care, care and treatment or detention occupancy or in a retirement home, and (c) the partitions are not installed as enclosures for exits or vertical service spaces. |  | Common Sentence | Yes | Retirement Homes
2015 | ON | NBC | Div B | 3.1.5.16.(3) | Combustible Elements in Partitions | Solid lumber partitions not less than 38 mm thick and partitions that contain wood framing are permitted to be used in a building required to be of noncombustible construction provided (a) the building is sprinklered throughout, and (b) the partitions are not (i) located in a care, treatment or detention occupancy, (ii) installed as enclosures for exits or vertical service spaces, or (iii) used to satisfy the requirements of Clause 3.2.8.1.(1). | obc2019_divb | Div B | 3.1.5.13.(3) | 3.1.5.13. Combustible Elements in Partitions | Solid lumber partitions not less than 38 mm thick and partitions that contain wood framing are permitted to be used in a building required to be of noncombustible construction provided, (a) the floor area containing the partitions is sprinklered, and (b) the partitions are not, (i) located in a care, care and treatment or detention occupancy or in a retirement home, (ii) installed as enclosures for exits or vertical service spaces, or (iii) used to satisfy the requirements of Clause 3.2.8.1.(1)(a). |  | Common Sentence | Yes | Retirement Homes
2015 | ON | NBC | Div B | 3.1.5.17.(1) | Storage Lockers in Residential Buildings | Storage lockers in storage rooms are permitted to be constructed of wood in a building of residential occupancy required to be of noncombustible construction. | obc2019_divb | Div B | 3.1.5.14.(1) | 3.1.5.14. Storage Lockers in Residential Buildings | Except in a retirement home, storage lockers in storage rooms are permitted to be constructed of wood in a building of residential occupancy required to be of noncombustible construction. |  | Common Sentence | Yes | Retirement Homes
2015 | ON | NBC | Div B | 3.1.5.18.(1) | Combustible Ducts | Except as required by Sentence 3.6.4.3.(1), combustible ducts, including plenums and duct connectors, are permitted to be used in a building required to be of noncombustible construction provided these ducts and duct connectors are used only in horizontal runs. | obc2019_divb | Div B | 3.1.5.15.(1) | 3.1.5.13. Combustible Elements in Partitions | Except as permitted by Sentence (2), solid lumber partitions not less than 38 mm thick and wood framing in partitions located in a fire compartment not more than 600 m2 in area are permitted to be used in a building required to be of noncombustible construction in a floor area that is not sprinklered provided the partitions, are not required fire separations, and are not located in a care, care and treatment or detention occupancy or in a retirement home. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.18.(2) | Combustible Ducts | Combustible duct linings, duct coverings, duct insulation, vibration isolation connectors, duct tape, pipe insulation and pipe coverings are permitted to be used in a building required to be of noncombustible construction provided they conform to the appropriate requirements of Subsection 3.6.5. | obc2019_divb | Div B | 3.1.5.15.(2) | 3.1.5.15. Combustible Ducts | Combustible duct linings, duct coverings, duct insulation, vibration isolation connectors, duct tape, pipe insulation and pipe coverings are permitted to be used in a building required to be of noncombustible construction provided they conform to the appropriate requirements of Part 6. |  | Common Sentence | Yes | Construction Materials
2015 | ON | NBC | Div B | 3.1.5.18.(3) | Combustible Ducts | In a building required to be of noncombustible construction, combustible ducts need not comply with the requirements of Sentences 3.6.5.1.(1) and (2) provided the ducts are (a) part of a duct system conveying only ventilation air, and (b) contained entirely within a dwelling unit. | obc2019_divb | Div B | 3.1.5.15.(3) | 3.1.5.15. Combustible Ducts | In a building required to be of noncombustible construction, combustible ducts need not comply with the requirements of Part 6 provided the ducts are, (a) part of a duct system conveying only ventilation air, and (b) contained entirely within a dwelling unit. |  | Common Sentence | Yes | Construction Materials
2015 | ON | NBC | Div B | 3.1.5.19.(1) | Combustible Piping Materials | Except as permitted by Sentence 3.1.5.2.(1) and Sentences 3.1.5.19.(2) and 3.1.5.19.(3), combustible piping and tubing and associated adhesives are permitted to be used in a building required to be of noncombustible construction provided that, except when concealed in a wall or concrete floor slab, they (a) have a flame-spread rating not more than 25, and (b) if used in a building described in Subsection 3.2.6., have a smoke developed classification not more than 50. | obc2019_divb | Div B | 3.1.5.16.(1) | 3.1.5.16. Combustible Piping Materials | Except as permitted by Sentences (2) and (3) and by Clause 3.1.5.2.(1)(d) and Article 3.1.5.22., combustible piping and tubing and associated adhesives are permitted to be used in a building required to be of noncombustible construction provided that, except when concealed in a wall or concrete floor slab, they, (a) have a flame-spread rating not more than 25, and (b) if used in a building described in Subsection 3.2.6., have a smoke developed classification not more than 50. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.19.(2) | Combustible Piping Materials | Combustible sprinkler piping is permitted to be used within a sprinklered floor area in a building required to be of noncombustible construction. (See also Article 3.2.5.13.) | obc2019_divb | Div B | 3.1.5.16.(2) | 3.1.5.16. Combustible Piping Materials | Combustible sprinkler piping is permitted to be used within a sprinklered floor area in a building required to be of noncombustible construction. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.19.(3) | Combustible Piping Materials | Polypropylene pipes and fittings are permitted to be used for drain, waste and vent piping for the conveyance of highly corrosive materials and for piping used to distribute distilled or dialyzed water in laboratory and hospital facilities in a building required to be of noncombustible construction, provided (a) the building is sprinklered throughout, (b) the piping is not located in a vertical shaft, and (c) piping that penetrates a fire separation is sealed at the penetration by a fire stop that has an FT rating not less than the fire-resistance rating of the fire separation when subjected to the fire test method in ULC CAN/ULC-S115-11 Fire Tests of Firestop Systems with a pressure differential of 50 Pa between the exposed and unexposed sides, with the higher pressure on the exposed side. | obc2019_divb | Div B | 3.1.5.16.(3) | 3.1.5.16. Combustible Piping Materials | Polypropylene pipes and fittings are permitted to be used for drain, waste and vent piping for the conveyance of highly corrosive materials and for piping used to distribute distilled or dialyzed water in laboratory and hospital facilities in a building required to be of noncombustible construction, provided, (a) the building is sprinklered, (b) the piping is not located in a vertical shaft, and (c) piping that penetrates a fire separation is sealed at the penetration by a fire stop that has an FT rating not less than the fire-resistance rating of the fire separation when subjected to the fire test method in CAN/ULC-S115, "Fire Tests of Firestop Systems", with a pressure differential of 50 Pa between the exposed and unexposed sides, with the higher pressure on the exposed side. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.2.(1) | Minor Combustible Components | The following minor combustible components are permitted in a building required to be of noncombustible construction: (a) paint (see also Sentence 3.1.13.1.(2)), (b) self-adhesive tapes, mastics and caulking materials, including foamed plastic air sealants, applied to provide a seal between the major components of exterior wall construction, (see also Article 3.6.4.3. for limits on the use of combustible materials in plenum spaces), fire stops and fire blocks conforming to Sentence 3.1.9.1.(1) and Article 3.1.11.7., tubing for pneumatic controls provided it has an outside diameter of not more than 10 mm, adhesives, vapour barriers and sheathing papers, electrical outlet and junction boxes, wood blocking within wall assemblies intended for the attachment of handrails, fixtures, and similar items mounted on the surface of the wall, and similar minor components. | obc2019_divb | Div B | 3.1.5.2.(1) | 3.1.5.2. Minor Combustible Components | The following minor combustible components are permitted in a building required to be of noncombustible construction: (a) paint, (b) self-adhesive tapes, mastics and caulking materials applied to provide flexible seals between the major components of exterior wall construction,(c) fire stops conforming to Sentence 3.1.9.1.(1) and fire blocks conforming to Article 3.1.11.7., (d) tubing for pneumatic controls provided it has an outside diameter not more than 10 mm, (e) adhesives, vapour barriers and sheathing papers, (f) electrical outlet and junction boxes, (g) wood blocking within wall assemblies intended for the attachment of handrails, fixtures, and similar items mounted on the surface of the wall, and (h) similar minor components. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.20.(1) | Combustible Plumbing Fixtures | Combustible plumbing fixtures, including wall and ceiling enclosures that form part of the plumbing fixture, are permitted in a building required to be of noncombustible construction provided they are constructed of material having a flame-spread rating and smoke developed classification not more than that permitted for the wall surface of the room or space in which they are installed. | obc2019_divb | Div B | 3.1.5.17.(1) | 3.1.5.17. Combustible Plumbing Fixtures | Combustible plumbing fixtures are permitted in a building required to be of noncombustible construction if they are constructed of material having a flame-spread rating and smoke developed classification permitted in Subsection 3.1.13. |  | Common Sentence | Yes | Construction Materials
2015 | ON | NBC | Div B | 3.1.5.21.(1) | Wires and Cables | Except as required by Sentence 3.1.5.21.(2) and Article 3.1.5.22., optical fibre cables and electrical wires and cables with combustible insulation, jackets or sheathes are permitted in a building required to be of noncombustible construction, provided (a) the wires and cables exhibit a vertical char of not more than 1.5 m when tested in conformance with the Vertical Flame Test â€“ Cables in Cable Trays (FT4 rating) in CSA C22.2 No. 0.3-09 Test Methods for Electrical Wires and Cables (b) the wires and cables are located in (i) totally enclosed noncombustible raceways (see Note A-3.1.4.3.(1)(b)(i)), (ii) masonry walls, (iii) concrete slabs, (iv) a service room separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h, or (v) totally enclosed non-metallic raceways conforming to Clause 3.1.5.23.(1)(b), or (c) the wires and cables are communication cables used at the service entry to a building and are not more than 3 m long. | obc2019_divb | Div B | 3.1.5.18.(1) | 3.1.5.18. Wires and Cables | Except as permitted by Sentence (2) and Articles 3.1.5.19. and 3.1.5.21., optical fibre cables and electrical wires and cables with combustible insulation, jackets or sheathes are permitted in a building required to be of noncombustible construction, provided, (a) the wires and cables exhibit a vertical char of not more than 1.5 m when tested in conformance with the Vertical Flame Test ‚¬" Cables in Cable trough in Clause 4.11.4. of CSA C22.2 No. 0.3, "Test Methods for Electrical Wires and Cables", (FT4 Rating), (b) the wires and cables are located in, (i) totally enclosed noncombustible raceways, (ii) concealed spaces in walls, (iii) concrete slabs, (iv) a service room separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h, or (v) totally enclosed nonmetallic raceways conforming to Clause 3.1.5.20.(1)(b), or the wires and cables are communication cables used at the service entry to a building and are not more than 3 m long. |  | Common Sentence | Yes | Construction Materials
2015 | ON | NBC | Div B | 3.1.5.22.(1) | Combustible Travelling Cables for Elevators | Combustible travelling cables are permitted on elevating devices in a building required to be of noncombustible construction. | obc2019_divb | Div B | 3.1.5.19.(1) | 3.1.5.17. Combustible Plumbing Fixtures | Combustible plumbing fixtures are permitted in a building required to be of noncombustible construction if they are constructed of material having a flame-spread rating and smoke developed classification permitted in Subsection 3.1.13. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.23.(1) | Non-metallic Raceways | Except as required in Sentence 3.1.5.23.(2), subject to the limits on the size of elements that penetrate fire separations as stated in Sentence 3.1.9.3.(2), within a fire compartment of a building required to be of noncombustible construction, totally enclosed non-metallic raceways not more than 175 mm in outside diameter, or of an equivalent rectangular area, are permitted to be used to enclose optical fibre cables and electrical wires and cables, provided (a) where the wires and cables in the raceways meet or exceed the requirements of Sentence 3.1.5.21.(1), the non-metallic raceways meet the requirements for at least an FT4 rating in (i) CAN/CSA-C22.2 No. 262-04 Optical Fiber Cable and Communication Cable Raceway Systems or (ii) CAN/ULC-S143-14 Fire Tests for Non-Metallic Electrical and Optical Fibre Cable Raceway Systems and (b) where the wires and cables in the raceways do not meet or exceed the requirements of Sentence 3.1.5.21.(1), the non-metallic raceways exhibit a vertical char of not more than 1.5 m when tested in conformance with the Vertical Flame Test (FT4) â€“ Conduit or Tubing on Cable Tray in Clause 6.16 of CSA C22.2 No. 211.0-03 General Requirements and Methods of Testing for Nonmetallic Conduit | obc2019_divb | Div B | 3.1.5.20.(1) | 3.1.5.20. Nonmetallic Raceways | Except as provided by Subclause 3.6.4.3.(1)(a)(iv) and subject to limits on size for penetrations of fire separations as required by Sentence 3.1.9.3.(2), within a fire compartment of a building required to be of noncombustible construction, totally enclosed nonmetallic raceways not more than 175 mm in outside diameter, or an equivalent rectangular area, are permitted to be used to enclose optical fibre cables and electrical wires and cables, provided, where, (a) the wires and cables in the raceways meet or exceed the requirements of Clause 3.1.5.18.(1)(a), the nonmetallic raceways meet the requirements for at least an FT4 rating in, (i) CAN/CSA-C22.2 No. 262, "Optical Fiber Cable and Communication Cable Raceway Systems", or (ii) CAN/ULC-S143, "Fire Tests for Non-Metallic Electrical and Optical Fibre Cable Raceway Systems", and (b) the wires and cables in the raceways do not meet or exceed the requirements of Clause 3.1.5.18.(1)(a), the nonmetallic raceways exhibit a vertical char not more than 1.5 m when tested in conformance with the Vertical Flame Test (FT4) Ã¢â‚¬" Conduit or Tubing on Cable Tray in Clause 6.16 of CSA C22.2 No. 211.0, "General Requirements and Methods of Testing for Nonmetallic Conduit". |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.24.(1) | Decorative Wood Cladding | On buildings required to be of noncombustible construction, decorative wood cladding is permitted to be used on the exterior fascias and soffits of marquees or canopies on the building face of a storey having direct access to a street or access route, provided the wood cladding is fire-retardant-treated wood that has been conditioned in conformance with ASTM D 2898-10 Accelerated Weathering of Fire-Retardant-Treated Wood for Fire Testing before being tested in accordance with ULC CAN/ULC-S102-10 Test for Surface Burning Characteristics of Building Materials and Assemblies | obc2019_divb | Div B | 3.1.5.25.(1) | 3.1.5.25. Wood Decorative Cladding | Wood decorative cladding is permitted to be used on exterior marquee fascias, of a storey having direct access to a street or access route, of a building required to be of noncombustible construction, provided the cladding is fire-retardant treated wood that, before testing to CAN/ULC-S102, "Test for Surface Burning Characteristics of Building Materials and Assemblies", has been conditioned in conformance with ASTM D2898, "Accelerated Weathering of Fire-Retardant-Treated Wood for Fire Testing". |  | Common Sentence | Yes | Construction Materials
2015 | ON | NBC | Div B | 3.1.5.3.(1) | Combustible Roofing Materials | Combustible roof covering that has an A, B, or C classification determined in conformance with part 3. is permitted on a building required to be of noncombustible construction. | obc2019_divb | Div B | 3.1.5.3.(1) | 3.1.5.3. Combustible Roofing Materials | Combustible roof covering that has an A, B or C classification determined in conformance with Subsection 3.1.15. is permitted on a building required to be of noncombustible construction. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.3.(2) | Combustible Roofing Materials | Combustible roof sheathing and roof sheathing supports installed above a concrete deck are permitted on a building required to be of noncombustible construction provided the concrete deck is not less than 50 mm thick, the height of the roof space above the deck is not more than 1 m, the roof space is divided into compartments by fire blocks in conformance with Article 3.1.11.5., openings through the concrete deck other than for noncombustible roof drains and plumbing piping are protected by masonry or concrete shafts constructed as fire separations having a fire-resistance rating not less than 1 h, and extending from the concrete deck to not less than 150 mm above the adjacent roof sheathing, the perimeter of the roof is protected by a noncombustible parapet extending from the concrete deck to not less than 150 mm above the adjacent sheathing, and except as permitted by Sentence 3.1.5.3.(2), the roof space does not contain any building services. | obc2019_divb | Div B | 3.1.5.3.(2) | 3.1.5.3. Combustible Roofing Materials | Combustible roof sheathing and roof sheathing supports installed above a concrete deck are permitted on a building required to be of noncombustible construction provided, (a) the concrete deck is not less than 50 mm thick, (b) the height of the roof space above the deck is not more than 1 000 mm, (c) the roof space is divided into compartments by fire blocks in conformance with Article 3.1.11.5., (d) openings through the concrete deck, other than for noncombustible roof drains and plumbing piping, are protected by masonry or concrete shafts, (i) constructed as fire separations having a fire-resistance rating not less than 1 h, and (ii) extending from the concrete deck to not less than 150 mm above the adjacent roof sheathing, (e) the perimeter of the roof is protected by a noncombustible parapet extending from the concrete deck to not less than 150 mm above the adjacent sheathing, and (f) except as permitted by Clause (d), the roof space does not contain any building services. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.3.(3) | Combustible Roofing Materials | Combustible cant strips, roof curbs, nailing strips and similar components used in the installation of roofing are permitted on a building required to be of noncombustible construction. | obc2019_divb | Div B | 3.1.5.3.(3) | 3.1.5.3. Combustible Roofing Materials | Combustible cant strips, roof curbs, nailing strips and similar components used in the installation of roofing are permitted on a building required to be of noncombustible construction. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.3.(4) | Combustible Roofing Materials | Wood nailer facings to parapets, not more than 600 mm high, are permitted on a building required to be of noncombustible construction, if the facings and any roof membranes covering the facings are protected by sheet metal. | obc2019_divb | Div B | 3.1.5.3.(4) | 3.1.5.3. Combustible Roofing Materials | Wood nailer facings to parapets, not more than 600 mm high, are permitted on a building required to be of noncombustible construction, if the facings and any roof membranes covering the facings are protected by sheet metal. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.4.(1) | Combustible Glazing and Skylights | Combustible skylight assemblies are permitted in a building required to be of noncombustible construction if the assemblies have a flame-spread rating not more than 150 provided the assemblies have an individual area not more than 9 m2 , have an aggregate horizontal projected area of the openings through the ceiling not more than 25% of the area of the ceiling of the room or space in which they are located, and are spaced not less than 2.5 m from adjacent assemblies and from required fire separations, or 75 provided the assemblies have an individual area not more than 27 m2 , have an aggregate horizontal projected area of the openings through the ceiling not more than 33% of the area of the ceiling of the room or space in which they are located, and are spaced not less than 1.2 m from adjacent assemblies and from required fire separations. | obc2019_divb | Div B | 3.1.5.4.(1) | 3.1.5.4. Combustible Glazing and Skylights | Combustible skylight assemblies are permitted in a building required to be of noncombustible construction if the assemblies have a flame-spread rating not more than, (a) 150, provided the assemblies, (i) have an individual area not more than 9 m2, (ii) have an aggregate horizontal projected area of the openings through the ceiling not more than 25% of the area of the ceiling of the room or space in which they are located, and (iii) are spaced not less than 2 500 mm from adjacent assemblies and 1 200 mm from required fire separations, or (b) 75, provided the assemblies, (i) have an individual area not more than 27 m2, (ii) have an aggregate horizontal projected area of the openings through the ceiling not more than 33% of the area of the ceiling of the room or space in which they are located, and (iii) are spaced not less than 1 200 mm from adjacent assemblies and from required fire separations. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.4.(2) | Combustible Glazing and Skylights | Combustible vertical glazing installed no higher than the second storey is permitted in a building required to be of noncombustible construction. | obc2019_divb | Div B | 3.1.5.4.(2) | 3.1.5.4. Combustible Glazing and Skylights | Combustible vertical glazing installed no higher than the second storey is permitted in a building required to be of noncombustible construction. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.4.(3) | Combustible Glazing and Skylights | Except as permitted by Sentence 3.1.5.4.(4), the combustible vertical glazing permitted by Sentence 3.1.5.4.(2) shall have a flame-spread rating not more than 75. | obc2019_divb | Div B | 3.1.5.4.(3) | 3.1.5.4. Combustible Glazing and Skylights | Except as permitted by Sentence (4), the combustible vertical glazing permitted by Sentence (2) shall have a flame-spread rating not more than 75. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.4.(4) | Combustible Glazing and Skylights | The flame-spread rating of combustible glazing is permitted to be not more than 150 if the aggregate area of glazing is not more than 25% of the wall area of the storey in which it is located, and (a) the glazing is installed in a building not more than 1 storey in building height, (b) the glazing in the first storey is separated from the glazing in the second storey in accordance with the requirements of Article 3.2.3.17. for opening protection, or (c) the building is sprinklered throughout. | obc2019_divb | Div B | 3.1.5.4.(4) | 3.1.5.4. Combustible Glazing and Skylights | The flame-spread rating of combustible glazing in Sentence (2) is permitted to be not more than 150 if the aggregate area of glazing is not more than 25% of the wall area of the storey in which it is located, and, (a) the glazing is installed in a building not more than 1 storey in building height, (b) the glazing in the first storey is separated from the glazing in the second storey in accordance with the requirements of Article 3.2.3.17. for opening protection, or (c) sprinklers are installed in, (i) any storey with combustible glazing, and (ii) the storey immediately above the storey with combustible glazing. |  | Common Sentence | Yes | Construction Materials
2015 | ON | NBC | Div B | 3.1.5.4.(5) | Combustible Glazing and Skylights | Combustible window sashes and frames are permitted in a building required to be of noncombustible construction provided (a) each window in an exterior wall face is an individual unit separated by noncombustible wall construction from every other opening in the wall, (b) windows in exterior walls in contiguous storeys are separated by not less than 1 m of noncombustible construction, and (c) the aggregate area of openings in an exterior wall face of a fire compartment is not more than 40% of the area of the wall face. | obc2019_divb | Div B | 3.1.5.4.(5) | 3.1.5.4. Combustible Glazing and Skylights | Combustible window sashes and frames are permitted in a building required to be of noncombustible construction provided,(a) each window in an exterior wall face is an individual unit separated by a wall of noncombustible construction from every other opening in the exterior wall, (b) windows in exterior walls in contiguous storeys are separated by not less than 1 000 mm of noncombustible construction, and (c) the aggregate area of openings in an exterior wall face of a fire compartment is not more than 40% of the area of the wall face. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.5.(1) | Combustible Cladding on Exterior Walls Combustible Components for Exterior Walls | Except as provided in Sentences (2) and (3), combustible cladding is permitted to be used on an exterior wall assembly in a building required to be of noncombustible construction, provided (a) the building is (i) not more than 3 storeys in building height, or (ii) sprinklered throughout, and (b) when tested in accordance with CAN/ULC S134, “Fire Test of Exterior Wall Assemblies,” the wall assembly satisfies the following criteria for testing and conditions of acceptance (see Note A-3.1.5.5.(1)(b)): (i) flaming on or in the wall assembly does not spread more than 5m above the opening (see Note A-3.1.5.5.(1)(b)(i)), and (ii) the heat flux during the flame exposure on the wall assembly is not more than 35kW/m 2 measured at 3.5m above the opening (see Note A-3.1.5.5.(1)(b)(ii)). Combustible components, other than those permitted by Article 3.1.5.5., are permitted to be used in an exterior wall assembly of a building required to be of noncombustible construction, provided (a) the building is (i) not more than 3 storeys in building height, or (ii) sprinklered throughout, and (b) the wall assembly (i) meets the requirements of Clause 3.1.5.5.(1)(b), or (ii) is protected by masonry or concrete cladding not less than 25 mm thick (see Note A-3.1.5.5.(1)(b)). | obc2019_divb | Div B | 3.1.5.5.(1) | 3.1.5.5. Combustible Components for Exterior Walls | Except as provided in Sentences (2) and (4), combustible components are permitted to be used for an exterior non-loadbearing wall assembly in a building required to be of noncombustible construction, provided that, (a) the building is, (i) not more than 3 storeys in building height, or (ii) not more than 6 storeys in building height if sprinklered, (b) when tested in accordance with CAN/ULC-S134, "Fire Test of Exterior Wall Assemblies", the wall assembly satisfies the following criteria for testing and conditions of acceptance: (i) flaming on or in the wall assembly does not spread more than 5 m above the opening, and (ii) the heat flux during the flame exposure on the wall assembly is not more than 35 kW/m2 measured at 3.5 m above the opening, and (c) the interior surfaces of the wall assembly are protected by a thermal barrier conforming to Sentence 3.1.5.12.(5). |  | Common Sentence | Yes | Construction Materials
2015 | ON | NBC | Div B | 3.1.5.5.(2) | Combustible Cladding on Exterior Walls | Except as permitted by Articles 3.2.3.10.and 3.2.3.11., where the limiting distance in Tables 3.2.3.1.-Bto 3.2.3.1.-E permits an area of unprotected openings of not more than 10% of the exposing building face, the construction requirements of Table 3.2.3.7. shall be met. | obc2019_divb | Div B | 3.1.5.5.(2) | 3.1.5.5. Combustible Components for Exterior Walls | Except as permitted by Articles 3.2.3.10. and 3.2.3.11., where the limiting distance in Tables 3.2.3.1.B. to 3.2.3.1.E. permits an area of unprotected openings of not more than 10% of the exposing building face, the construction requirements of Table 3.2.3.7. shall be met. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.5.(3) | Combustible Cladding on Exterior Walls | A wall assembly permitted by Sentence 3.1.5.5.(1) that includes combustible cladding of fire-retardant-treated wood shall be tested for fire exposure after the cladding has been subjected to an accelerated weathering test as specified in ASTM D 2898-10 Accelerated Weathering of Fire-Retardant-Treated Wood for Fire Testing | obc2019_divb | Div B | 3.1.5.5.(3) | 3.1.5.5. Combustible Components for Exterior Walls | A wall assembly permitted by Sentence (1) that includes combustible cladding of fire-retardant treated wood shall be tested for fire exposure after the cladding has been subjected to an accelerated weathering test as specified in ASTM D2898, "Accelerated Weathering of Fire-Retardant-Treated Wood for Fire Testing". |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.7.(1) | Factory-Assembled Panels | Except as provided in Sentence 3.1.5.7.(2), factory-assembled wall and ceiling panels containing foamed plastic insulation with a flame-spread rating not more than 500 are permitted to be used in a building required to be of noncombustible construction, (a) provided the building (i) is sprinklered, (ii) is not more than 18 m high, measured from grade to the underside of the roof, and (iii) does not contain a Group A, Group B, or Group C major occupancy, and Ib) the panels (i) do not contain an air space, (ii) when tested in accordance with ULC CAN/ULC-S138-06 Test for Fire Growth of Insulated Building Panels in a Full-Scale Room Configuration meet the criteria defined therein, and (ii) when a sample panel with an assembled joint typical of field installation is subjected to the applicable test described in part 3., have a flame-spread rating not more than that permitted for the room or space that they bound. | obc2019_divb | Div B | 3.1.5.5.(1) | 3.1.5.5A. Factory-Assembled Panels | Except as permitted in Sentence (2), factory-assembled wall and ceiling panels containing foamed plastic insulation with a flame-spread rating not more than 500 are permitted to be used in a building required to be of noncombustible construction, provided that, (a) the building, (i) is sprinklered, (ii) is not more than 18 m high, measured from grade to the underside of the roof, and (iii) does not contain a Group A, Group B or Group C major occupancy, and (b) the panels, (i) do not contain an air space, (ii) when tested in accordance with CAN/ULC-S138, "Test for Fire Growth of Insulated Building Panels in a Full-Scale Room Configuration", meet the criteria set out in that document, and (iii) when a sample panel with an assembled joint typical of field installation is subjected to the applicable test described in Subsection 3.1.12., have a flame-spread rating not more than that permitted for the room or space that they bound. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.7.(2) | Factory-Assembled Panels | Factory-assembled exterior wall panels containing thermosetting foamed plastic insulation are permitted to be used in a building required to be of noncombustible construction, provided (a) the building (i) is not more than 18 m high, measured from grade to the underside of the roof, and (ii) does not contain a Group B or Group C major occupancy, and (b) the wall panels (i) do not contain an air space, (ii) are protected on both sides by sheet steel not less than 0.38 mm thick, (iii) remain in place for not less than 10 min when tested in conformance with ULC CAN/ULC-S101-14 Fire Endurance Tests of Building Construction and Materials where the exposed surface includes typical vertical and horizontal joints, and (iv) when a sample panel with an assembled joint typical of field installation is subjected to the applicable test described in part 3., have a flame-spread rating not more than that permitted for the room or space that they bound. | obc2019_divb | Div B | 3.1.5.5.(2) | 3.1.5.5A. Factory-Assembled Panels | Factory-assembled exterior wall panels containing thermosetting foamed plastic insulation are permitted to be used in a building required to be of noncombustible construction, provided that, (a) the building, (i) is not more than 18 m high, measured from grade to the underside of the roof, and (ii) does not contain a Group B or Group C major occupancy, and (b) the wall panels, (i) do not contain an air space, (ii) are protected on both sides by sheet steel not less than 0.38 mm thick, (iii) remain in place for not less than 10 min when tested in accordance with CAN/ULC-S101, "Fire Endurance Tests of Building Construction and Materials", where the exposed surface includes typical vertical and horizontal joints, and (iv) when a sample panel with an assembled joint typical of field installation is subjected to the applicable test described in Subsection 3.1.12., have a flame-spread rating not more than that permitted for the room or space that they bound. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.7.(3) | Factory-Assembled Panels | A walk-in cooler or freezer consisting of factory-assembled wall, floor or ceiling panels containing foamed plastic insulation with a flame-spread rating not more than 500 is permitted to be used in a building required to be of noncombustible construction, provided (a) the building is sprinklered, and (b) the panels (i) are protected on both sides by sheet metal not less than 0.38 mm thick with a melting point not less than 650Â°C, (ii) do not contain an air space, (iii) when tested in accordance with ULC CAN/ULC-S138-06 Test for Fire Growth of Insulated Building Panels in a Full-Scale Room Configuration meet the criteria defined therein, and (iv) when a sample panel with an assembled joint typical of field installation is subjected to the applicable test described in Sebsection 3.1.12., have a flame-spread rating not more than that permitted for the space in which they are located or the space that they bound, as applicable. | obc2019_divb | Div B | 3.1.5.5.(3) | 3.1.5.5A. Factory-Assembled Panels | A walk-in cooler or freezer consisting of factory-assembled wall, floor or ceiling panels containing foamed plastic insulation with a flame-spread rating not more than 500 is permitted to be used in a building required to be of noncombustible construction, provided that, (a) the building is sprinklered, (b) the panels, (i) are protected on both sides by sheet metal not less than 0.38 mm thick with a melting point not less than 650°C, (ii) do not contain an air space, (iii) when tested in accordance with CAN/ULC-S138, "Test for Fire Growth of Insulated Building Panels in a Full-Scale Room Configuration", meet the criteria set out in that document, and (iv) when a sample panel with an assembled joint typical of field installation is subjected to the applicable test described in Subsection 3.1.12., have a flame-spread rating not more than that permitted for the space in which they are located, the space that they bound, or the walls of the building to which the cooler or freezer is attached, as applicable. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.8.(1) | Nailing Elements | Wood nailing elements attached directly to or set into a continuous noncombustible backing for the attachment of interior finishes are permitted in a building required to be of noncombustible construction provided the concealed space created by the wood elements is not more than 50 mm thick. | obc2019_divb | Div B | 3.1.5.6.(1) | 3.1.5.5A. Factory-Assembled Panels | Except as permitted in Sentence (2), factory-assembled wall and ceiling panels containing foamed plastic insulation with a flame-spread rating not more than 500 are permitted to be used in a building required to be of noncombustible construction, provided that, the building, is sprinklered, is not more than 18 m high, measured from grade to the underside of the roof, and does not contain a Group A, Group B or Group C major occupancy, and the panels, do not contain an air space, when tested in accordance with CAN/ULC-S138, "Test for Fire Growth of Insulated Building Panels in a Full-Scale Room Configuration", meet the criteria set out in that document, and when a sample panel with an assembled joint typical of field installation is subjected to the applicable test described in Subsection 3.1.12., have a flame-spread rating not more than that permitted for the room or space that they bound. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.5.9.(1) | Combustible Millwork | Combustible millwork, including interior trim, doors and door frames, show windows together with their frames, aprons and backing, handrails, shelves, cabinets and counters, is permitted in a building required to be of noncombustible construction. | obc2019_divb | Div B | 3.1.5.7.(1) | 3.1.5.6. Nailing Elements | Wood nailing elements attached directly to or set into a continuous noncombustible backing for the attachment of interior finishes, are permitted in a building required to be of noncombustible construction provided the concealed space created by the wood elements is not more than 50 mm thick. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.6.1.(1) | Means of Egress | Tents and air-supported structures shall conform to Sections 3.3 and 3.4 | obc2019_divb | Div B | 3.14.1.3.(1) | 3.14.1.3. Means of Egress | Except as provided in Sentences (2) and (3), tents shall conform to Sections 3.3. and 3.4. |  | Common Sentence | Yes | Tents and Air-Supported Structures
2015 | ON | NBC | Div B | 3.1.6.2.(2) | Restrictions | An air-supported structure shall not be used for Groups B, C, or Group F, Division 1 major occupancies or for classrooms. | obc2019_divb | Div B | 3.14.2.2.(1) | 3.14.2.2. General | Air-supported structures shall not be used for Groups B, C or Group F, Division 1 major occupancies or for classrooms. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.6.2.(3) | Restrictions | An air-supported structure shall be designed as open floor space without interior walls, mezzanines, intermediate floors or similar construction. | obc2019_divb | Div B | 3.14.2.2.(4) | 3.14.2.2. General | Air-supported structures may be designed with interior walls, mezzanines, or similar construction. |  | Common Sentence | Yes | Tents and Air-Supported Structures
2015 | ON | NBC | Div B | 3.1.6.3.(2) | Clearance to Other Structures | Tents and air-supported structures (a) shall not be erected closer than 3 m to other structures on the same property except as permitted by Sentences (3) and (4), and (b) shall be sufficiently distant from one another to provide an area to be used as a means of emergency egress. | obc2019_divb | Div B | 3.14.1.4.(2) | 3.14.1.4. Clearance to Other Structures | Except as provided in Sentences (3), (4) and (5), tents shall not be erected closer than 3 m to other tents or structures on the same property. |  | Common Sentence | Yes | Tents and Air-Supported Structures
2015 | ON | NBC | Div B | 3.1.6.3.(2) | Clearance to Other Structures | Tents and air-supported structures (a) shall not be erected closer than 3 m to other structures on the same property except as permitted by Sentences (3) and (4), and (b) shall be sufficiently distant from one another to provide an area to be used as a means of emergency egress. | obc2019_divb | Div B | 3.14.2.3.(1) | 3.14.2.3. Spatial Separation | Except as provided in Sentences (2), (3) and (4), air-supported structures shall not be erected closer than 3 m to other structures on the same property or to the property line. |  | Common Sentence | Yes | Tents and Air-Supported Structures
2015 | ON | NBC | Div B | 3.1.6.3.(3) | Clearance to Other Structures | Tents and air-supported structures not occupied by the public (a) need not be separated from one another, and (b) are permitted to be erected less than 3 m from other structures on the same property provided this spacing does not create a hazard to the public. | obc2019_divb | Div B | 3.14.1.4.(4) | 3.14.1.4. Clearance to Other Structures | Tents not occupied by the public need not be separated from one another, and are permitted to be erected less than 3 m from other structures on the same property, where such closer spacing does not create a hazard to the public. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.6.3.(3) | Clearance to Other Structures | Tents and air-supported structures not occupied by the public (a) need not be separated from one another, and (b) are permitted to be erected less than 3 m from other structures on the same property provided this spacing does not create a hazard to the public. | obc2019_divb | Div B | 3.14.2.3.(2) | 3.14.2.3. Spatial Separation | Air-supported structures not occupied by the public need not be separated from one another, and are permitted to be erected closer than 3 m from other structures on the same property where such closer spacing does not create a hazard to the building occupants or the public. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.6.3.(4) | Clearance to Other Structures | Tents not more than 120 m2 in ground area, located on fair grounds or similar open spaces, need not be separated from one another provided this does not create a hazard to the public. | obc2019_divb | Div B | 3.14.1.4.(5) | 3.14.1.4. Clearance to Other Structures | Tents located on fair grounds or similar open spaces, need not be separated from one another provided such closer spacing does not create a hazard to the public. |  | Common Sentence | Yes | Tents and Air-Supported Structures
2015 | ON | NBC | Div B | 3.1.6.4.(1) | Clearance to Flammable Material | The ground enclosed by a tent or air-supported structure and not less than 3 m of ground outside the structure shall be cleared of all flammable material or vegetation that will spread fire. | obc2019_divb | Div B | 3.14.1.5.(1) | 3.14.1.5. Clearances to Flammable Material | The ground enclosed by a tent and for not less than 3 m outside of such structure shall be cleared of all flammable or combustible material or vegetation that will carry fire. |  | Common Sentence | Yes | Tents and Air-Supported Structures
2015 | ON | NBC | Div B | 3.1.6.4.(1) | Clearance to Flammable Material | The ground enclosed by a tent or air-supported structure and not less than 3 m of ground outside the structure shall be cleared of all flammable material or vegetation that will spread fire. | obc2019_divb | Div B | 3.14.2.4.(1) | 3.14.2.4. Clearances to Flammable Material | The ground enclosed by an air-supported structure and for not less than 3 m outside of such structure shall be clear of all flammable or combustible material or vegetation that will carry fire. |  | Common Sentence | Yes | Tents and Air-Supported Structures
2015 | ON | NBC | Div B | 3.1.6.5.(1) | Flame Resistance | Every tent and air-supported structure and all tarpaulins and decorative materials used in connection with these structures shall conform to CAN/ULC-S109, “Flame Tests of Flame-Resistant Fabrics and Films.” | obc2019_divb | Div B | 3.14.1.6.(1) | 3.14.1.6. Flame Resistance | Every tent, and tarpaulins, decorative materials, fabrics and films used in connection with tents, shall be certified to CAN/ULC-S109, “Flame Tests of Flame-Resistant Fabrics and Films”, or NFPA 701, “Fire Tests for Flame Propagation of Textiles and Films”. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.6.5.(1) | Flame Resistance | Every tent and air-supported structure and all tarpaulins and decorative materials used in connection with these structures shall conform to CAN/ULC-S109, “Flame Tests of Flame-Resistant Fabrics and Films.” | obc2019_divb | Div B | 3.14.2.5.(1) | 3.14.2.5. Flame Resistance | Air-supported structures shall be constructed of material conforming to CAN/ULC-S109, "Flame Tests of Flame-Resistant Fabrics and Films", or NFPA 701, "Fire Tests for Flame Propagation of Textiles and Films". |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.6.6.(1) | Emergency Air Supply | An air-supported structure used as a place of assembly for more than 200 persons shall have either an automatic emergency engine-generator set capable of powering one blower continuously for 4 h, or a supplementary blower powered by an automatic internal combustion engine. | obc2019_divb | Div B | 3.14.2.6.(1) | 3.14.2.6. Emergency Air Supply | An air-supported structure designed for an assembly occupancy with an occupant load of more than 200 persons shall have either an automatic emergency engine-generator set capable of powering one blower continuously for 4 h, or a supplementary blower powered by an automatic internal combustion engine. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.6.7.(1) | Electrical Systems | The electrical system and equipment in a tent or air-supported structure, including electrical fuses and switches, shall be inaccessible to the public. | obc2019_divb | Div B | 3.14.1.10.(1) | 3.14.1.10. Electrical Systems | The electrical system and equipment in a tent, including electrical fuses and switches, shall be inaccessible to the public. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.6.7.(1) | Electrical Systems | The electrical system and equipment in a tent or air-supported structure, including electrical fuses and switches, shall be inaccessible to the public. | obc2019_divb | Div B | 3.14.2.7.(1) | 3.14.2.7. Electrical Systems | The electrical system and equipment in an air-supported structure, including electrical fuses and switches, shall be inaccessible to the public. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.6.7.(2) | Electrical Systems | Cables on the ground in areas used by the public in a tent or air-supported structure shall be placed in trenches or protected by covers to prevent damage from traffic. | obc2019_divb | Div B | 3.14.1.10.(2) | 3.14.1.10. Electrical Systems | Cables on the ground in areas used by the public in a tent shall be placed in trenches or protected by covers to prevent damage from traffic. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.6.7.(2) | Electrical Systems | Cables on the ground in areas used by the public in a tent or air-supported structure shall be placed in trenches or protected by covers to prevent damage from traffic. | obc2019_divb | Div B | 3.14.2.7.(2) | 3.14.2.7. Electrical Systems | Cables on the ground in areas used by the public in an air-supported structure shall be placed in trenches or protected by covers to prevent damage from traffic. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.7.1.(1) | Determination of Ratings | Except as permitted by Sentence 3.1.7.1.(2) and Articles 3.1.7.2. and 3.6.3.5. , the rating of a material, assembly of materials or a structural member that is required to have a fire-resistance rating, shall be determined on the basis of the results of tests conducted in conformance with ULC CAN/ULC-S101-14 Fire Endurance Tests of Building Construction and Materials | obc2019_divb | Div B | 3.1.7.1.(1) | 3.1.7.1. Determination of Ratings | Except as permitted by Sentence (2) and Articles 3.1.7.2. and 3.6.3.5., the rating of a material, assembly of materials or a structural member that is required to have a fire-resistance rating, shall be determined on the basis of the results of tests conducted in conformance with CAN/ULC-S101, "Fire Endurance Tests of Building Construction and Materials". |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.7.1.(2) | Determination of Ratings | A material, assembly of materials or a structural member is permitted to be assigned a fire-resistance rating on the basis of Appendix. | obc2019_divb | Div B | 3.1.7.1.(2) | 3.1.7.1. Determination of Ratings | A material, assembly of materials or a structural member is permitted to be assigned a fire-resistance rating on the basis of MMAH Supplementary Standard SB-2, "Fire Performance Ratings". |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.1.7.2.(1) | Exception for Exterior Walls | The limit on the rise of temperature on the unexposed surface of an assembly as required by the tests referred to in Sentence 3.1.7.1.(1) shall not apply to an exterior wall that has a limiting distance of 1.2 m or more, provided correction is made for radiation from the unexposed surface in accordance with Sentence 3.2.3.1.(9). | obc2019_divb | Div B | 3.1.7.2.(1) | 3.1.7.2. Exception for Exterior Walls | The limit on the rise of temperature on the unexposed surface of an assembly as required by the tests referred to in Sentence 3.1.7.1.(1) shall not apply to an exterior wall that has a limiting distance of 1.2 m or more, provided correction is made for radiation from the unexposed surface in accordance with Sentence 3.2.3.1.(9). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.7.3.(1) | Exposure Conditions for Rating | Floor, roof and ceiling assemblies shall be rated for exposure to fire on the underside. | obc2019_divb | Div B | 3.1.7.3.(1) | 3.1.7.3. Exposure Conditions for Rating | Floor, roof and ceiling assemblies shall be rated for exposure to fire on the underside. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.7.3.(2) | Exposure Conditions for Rating | Firewalls and interior vertical fire separations shall be rated for exposure to fire on each side. | obc2019_divb | Div B | 3.1.7.3.(2) | 3.1.7.3. Exposure Conditions for Rating | Firewalls and interior vertical fire separations shall be rated for exposure to fire on each side. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.7.3.(3) | Exposure Conditions for Rating | Exterior walls shall be rated for exposure to fire from inside the building. | obc2019_divb | Div B | 3.1.7.3.(3) | 3.1.7.3. Exposure Conditions for Rating | Exterior walls shall be rated for exposure to fire from inside the building. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.7.4.(1) | Minimum Fire-Resistance Rating | The use of materials or assemblies having a greater fire-resistance rating than required shall impose no obligation to exceed in whole or in part the minimum fire-resistance ratings required by this Part. | obc2019_divb | Div B | 3.1.7.4.(1) | 3.1.7.4. Minimum Fire-Resistance Rating | The use of materials or assemblies having a greater fire-resistance rating than required shall impose no obligation to exceed in whole or in part the minimum fire-resistance ratings required by this Part. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.7.5.(1) | Rating of Supporting Construction | Except as permitted by Sentence 3.1.7.5.(2) and by Articles 3.2.2.20. to 3.2.2.90. for mixed types of construction, all loadbearing walls, columns and arches in the storey immediately below a floor or roof assembly required to have a fire-resistance rating shall have a fire-resistance rating not less than that required for the supported floor or roof assembly. | obc2019_divb | Div B | 3.1.7.5.(1) | 3.1.7.5. Rating of Supporting Construction | Except as permitted by Sentence (2) and by Articles 3.2.2.20. to 3.2.2.83. for mixed types of construction, all loadbearing walls, columns and arches in the storey immediately below a floor or roof assembly required to have a fire-resistance rating shall have a fire-resistance rating not less than that required for the supported floor or roof assembly. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.1.7.5.(2) | Rating of Supporting Construction | Loadbearing walls, columns and arches supporting a service room or service space need not conform to Sentence 3.1.7.5.(1). | obc2019_divb | Div B | 3.1.7.5.(2) | 3.1.7.5. Rating of Supporting Construction | Loadbearing walls, columns and arches supporting a service room or service space need not conform to Sentence (1). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.7.5.(3) | Rating of Supporting Construction | Except for noncombustible roof assemblies required by Clauses 3.2.2.50.(2) and 3.2.2.58.(2), if an assembly is required to be of noncombustible construction and have a fire-resistance rating, it shall be supported by noncombustible construction. | obc2019_divb | Div B | 3.1.7.5.(3) | 3.1.7.5. Rating of Supporting Construction | Except for noncombustible construction required by Subclauses 3.2.2.43A.(2)(c)(i) and 3.2.2.50A.(2)(c)(i), if an assembly is required to be of noncombustible construction and have a fire resistance rating, it shall be supported by noncombustible construction. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.1.(1) | General Requirements | Any wall, partition or floor assembly required to be a fire separation shall except as permitted by Sentence 3.1.8.1.(2), be constructed as a continuous element, and as required in this Part, have a fire-resistance rating as specified (see Note A-3.1.8.1.(1)(b)). | obc2019_divb | Div B | 3.1.8.1.(1) | 3.1.8.1. General Requirements | Any wall, partition or floor assembly required to be a fire separation shall, (a) except as permitted by Sentence (2), be constructed as a continuous element, and (b) as required in this Part, have a fire-resistance rating as specified. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.1.(2) | General Requirements | Openings in a fire separation shall be protected with closures, shafts or other means in conformance with Articles 3.1.8.4. to 3.1.8.19. and Subsections 3. and 3. (See Note A-3.1.8.1.(2).) | obc2019_divb | Div B | 3.1.8.1.(2) | 3.1.8.1. General Requirements | Openings in a fire separation shall be protected with closures, shafts or other means in conformance with Articles 3.1.8.4. to 3.1.8.18. and Subsections 3.1.9. and 3.2.8. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.10.(1) | Installation of Fire Dampers | A fire damper shall be installed in the plane of the fire separation so as to stay in place should the duct become dislodged during a fire. (See Note A-3.1.8.10.(1).) | obc2019_divb | Div B | 3.1.8.9.(3) | 3.1.8.9. Installation of Fire Dampers | A fire damper shall be installed in the plane of the fire separation so as to stay in place should the duct be dislodged during a fire. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.10.(2) | Installation of Fire Dampers | A fire damper shall be arranged so as to close automatically upon the operation of a fusible link conforming to ULC ULC-S505-1974 Fusible Links for Fire Protection Service or other heat-actuated or smoke-actuated device. | obc2019_divb | Div B | 3.1.8.9.(1) | 3.1.8.9. Installation of Fire Dampers | A fire damper shall be arranged to close automatically upon the operation of a fusible link conforming to ULC S505, "Fusible Links for Fire Protection Service", or other heat-actuated or smoke-actuated device. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.10.(3) | Installation of Fire Dampers | A heat-actuated device referred to in Sentence 3.1.8.10.(2) shall (a) be located where it is readily affected by an abnormal rise in temperature in the duct, and (b) have a temperature rating approximately 30Â°C above the maximum temperature that would exist in the system, whether it is in operation or shut down. | obc2019_divb | Div B | 3.1.8.9.(2) | 3.1.8.9. Installation of Fire Dampers | A heat-actuated device referred to in Sentence (1) shall, (a) be located where it is readily affected by an abnormal rise of temperature in the duct, and (b) have a temperature rating approximately 30Ã‚Â°C above the maximum temperature that would exist in the system either with the system in operation or shut down. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.10.(5) | Installation of Fire Dampers | A tightly fitted access door shall be installed for each fire damper to provide access for the inspection of the damper and the resetting of the release device. (See Note A-3.1.8.10.(5).) | obc2019_divb | Div B | 3.1.8.9.(5) | 3.1.8.9. Installation of Fire Dampers | A tightly fitted access door shall be installed for each fire damper to provide access for the inspection of the damper and the resetting of the release device. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.11.(1) | Installation of Smoke Dampers | Where smoke dampers are used as a closure in an air-transfer opening, they shall be installed in the plane of the fire separation. | obc2019_divb | Div B | 3.1.8.9.(1) | 3.1.8.8A. Smoke Dampers Waived | Except as permitted in Sentence (2), the requirement for smoke dampers or combination smoke and fire dampers described in Sentence 3.1.8.7.(2) is permitted to be waived for ducts, that serve commercial cooking equipment, in which all inlet and outlet openings serve not more than one fire compartment, or that penetrate a vertical fire separation referred to in Clause 3.3.1.7.(1)(b) or in Sentence 3.3.3.5.(4), provided, the movement of air is continuous, and the configuration of the air-handling system prevents the recirculation of exhaust or return air under fire emergency conditions. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.11.(2) | Installation of Smoke Dampers | Where combination smoke/fire dampers are used as a closure in a duct, they shall be installed within 610 mm of the plane of the fire separation, provided there is no inlet or outlet opening between the fire separation and the damper. | obc2019_divb | Div B | 3.1.8.9.(2) | 3.1.8.9A. Installation of Smoke Dampers | Where combination smoke and fire dampers are used as a closure in a duct, they shall be installed within 610 mm of the plane of the fire separation, provided there is no inlet or outlet opening between the fire separation and the damper. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.11.(3) | Installation of Smoke Dampers | Except as required by a smoke control system, smoke dampers and combination smoke/fire dampers shall be configured so as to close automatically upon a signal from an adjacent smoke detector located as described in ULC CAN/ULC-S524-14 Installation of Fire Alarm Systems within 1.5 m horizontally of the duct or air-transfer opening in the fire separation (a) on both sides of the air-transfer opening, or (b) in the duct downstream of the smoke damper or combination smoke/fire damper. | obc2019_divb | Div B | 3.1.8.9.(3) | 3.1.8.9A. Installation of Smoke Dampers | Except as required by a smoke control system, smoke dampers and combination smoke and fire dampers shall be configured so as to close automatically upon a signal from an adjacent smoke detector located as described in CAN/ULC-S524, "Installation of Fire Alarm Systems", within 1.5 m horizontally of the duct or air-transfer opening in the fire separation, (a) on both sides of the air-transfer opening, or (b) in the duct downstream of the smoke damper or combination smoke and fire damper. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.11.(4) | Installation of Smoke Dampers | Smoke dampers or combination smoke/fire dampers shall be installed in the vertical or horizontal position in which they were tested. | obc2019_divb | Div B | 3.1.8.9.(4) | 3.1.8.9A. Installation of Smoke Dampers | Smoke dampers or combination smoke and fire dampers shall be installed in the vertical or horizontal position in which they were tested. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.11.(5) | Installation of Smoke Dampers | A tightly fitted access door shall be installed for each smoke damper and combination smoke/fire damper to provide access for their inspection and the resetting of the release device. (See Note A-3.1.8.10.(5).) | obc2019_divb | Div B | 3.1.8.9.(5) | 3.1.8.9A. Installation of Smoke Dampers | A tightly fitted access door shall be installed for each smoke damper and combination smoke and fire damper to provide access for their inspection and the resetting of the release device. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.12.(1) | Twenty-Minute Closures | A door assembly having a fire-protection rating not less than 20 min is permitted to be used as a closure in a fire separation not required to have a fire-resistance rating more than 1 h, located between a public corridor and a suite, a corridor and adjacent sleeping rooms, or a corridor and adjacent classrooms, offices and libraries in Group A, Division 2 major occupancies, or a fire separation not required to have a fire-resistance rating more than 45 min, located in a building not more than 3 storeys in building height. | obc2019_divb | Div B | 3.1.8.10.(1) | 3.1.8.9. Installation of Fire Dampers | A fire damper shall be arranged to close automatically upon the operation of a fusible link conforming to ULC S505, "Fusible Links for Fire Protection Service", or other heat-actuated or smoke-actuated device. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.12.(2) | Twenty-Minute Closures | The requirements for noncombustible sills and combustible floor coverings in NFPA 80-2013 Fire Doors and Other Opening Protectives do not apply to a door described in Sentence 3.1.8.12.(1). | obc2019_divb | Div B | 3.1.8.10.(2) | 3.1.8.10. Twenty-Minute Closures | The requirements for noncombustible sills and combustible floor coverings in NFPA 80, "Fire Doors and Other Opening Protectives", do not apply to a door described in Sentence (1). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.12.(3) | Twenty-Minute Closures | A door described in Sentence 3.1.8.12.(1) shall have clearances of not more than 6 mm at the bottom and not more than 3 mm at the sides and top. | obc2019_divb | Div B | 3.1.8.10.(3) | 3.1.8.10. Twenty-Minute Closures | A door described in Sentence (1) shall have a clearance not more than 6 mm at the bottom and not more than 3 mm at the sides and top. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.13.(1) | Self-closing Devices | Except as permitted by Sentence (2), every door in a fire separation, other than doors to freight elevators and dumbwaiters, shall be equipped with a self-closing device designed to return the door to the closed position after each use. | obc2019_divb | Div B | 3.1.8.11.(1) | 3.1.8.11. Self-Closing Devices | Except as provided in Sentences (2) to (5) and 3.3.3.2.(5), every door in a fire separation shall be equipped with a self-closing device designed to return the door to the closed position after each use. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.13.(1) | Self-closing Devices | Except as permitted by Sentence (2), every door in a fire separation, other than doors to freight elevators and dumbwaiters, shall be equipped with a self-closing device designed to return the door to the closed position after each use. | obc2019_divb | Div B | 3.1.8.11.(2) | 3.1.8.11. Self-Closing Devices | Self-closing devices need not be provided on doors to freight elevators and dumbwaiters. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.13.(2) | Self-closing Devices | A self-closing device need not be provided on a door that is located between (a) a classroom and a corridor providing access to exit from the classroom in a building that is not more than 3 storeys in building height, (b) a public corridor and an adjacent room of business and personal services occupancy in a building that is not more than 3 storeys in building height provided the door is not located in a dead-end portion of the corridor, (c) a patients’ sleeping room and a corridor serving the patients’ sleeping room, provided the room and corridor are within a fire compartment in a hospital or nursing home with treatment that complies with the requirements of Article 3.3.3.5., or (d) a patients’ sleeping room and an adjacent room that serves the patients’ sleeping room, provided these rooms are within a fire compartment in a hospital or nursing home with treatment that complies with the requirements of Article 3.3.3.5. | obc2019_divb | Div B | 3.1.8.11.(4) | 3.1.8.11. Self-Closing Devices | In a building that is not more than 3 storeys in building height, a self-closing device is not required on a door between a public corridor and an adjacent room or suite of business and personal services occupancy if the door is not located in, (a) a dead-end portion of the corridor, or (b) a corridor that serves a hotel. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.1.8.13.(2) | Self-closing Devices | A self-closing device need not be provided on a door that is located between (a) a classroom and a corridor providing access to exit from the classroom in a building that is not more than 3 storeys in building height, (b) a public corridor and an adjacent room of business and personal services occupancy in a building that is not more than 3 storeys in building height provided the door is not located in a dead-end portion of the corridor, (c) a patients’ sleeping room and a corridor serving the patients’ sleeping room, provided the room and corridor are within a fire compartment in a hospital or nursing home with treatment that complies with the requirements of Article 3.3.3.5., or (d) a patients’ sleeping room and an adjacent room that serves the patients’ sleeping room, provided these rooms are within a fire compartment in a hospital or nursing home with treatment that complies with the requirements of Article 3.3.3.5. | obc2019_divb | Div B | 3.1.8.11.(3) | 3.1.8.11. Self-Closing Devices | In a building that is not more than 3 storeys in building height, a self-closing device is not required on a door that is located between a classroom and a corridor providing access to exit from the classroom, except that a self-closing device is required on a door between a hazardous classroom and the corridor in an elementary or secondary school. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.1.8.13.(2) | Self-closing Devices | A self-closing device need not be provided on a door that is located between (a) a classroom and a corridor providing access to exit from the classroom in a building that is not more than 3 storeys in building height, (b) a public corridor and an adjacent room of business and personal services occupancy in a building that is not more than 3 storeys in building height provided the door is not located in a dead-end portion of the corridor, (c) a patients’ sleeping room and a corridor serving the patients’ sleeping room, provided the room and corridor are within a fire compartment in a hospital or nursing home with treatment that complies with the requirements of Article 3.3.3.5., or (d) a patients’ sleeping room and an adjacent room that serves the patients’ sleeping room, provided these rooms are within a fire compartment in a hospital or nursing home with treatment that complies with the requirements of Article 3.3.3.5. | obc2019_divb | Div B | 3.1.8.11.(5) | 3.1.8.11. Self-Closing Devices | Within a fire compartment in a hospital or long-term care home that complies with the requirements of Article 3.3.3.5., a self-closing device is not required on a door that is located between, (a) a patient’s or resident’s sleeping room and a corridor serving the patient’s or resident’s sleeping room, or (b) a patient’s or resident’s sleeping room and an adjacent room that serves the patient’s or resident’s sleeping room. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.14.(1) | Hold-Open Devices | Except as provided in Sentences 3.1.8.10.(2) and Sentence 3.1.8.11.(3), a hold-open device is permitted to be used on a closure in a required fire separation, other than on an exit stair door in a building more than 3 storeys in building height and on a door for a vestibule required by Article 3.3.5.7., provided the device is designed to release the closure in conformance with this Article. | obc2019_divb | Div B | 3.1.8.12.(1) | 3.1.8.12. Hold-Open Devices | Except as provided in Sentences 3.1.8.9.(1) and 3.1.8.9A.(3), a hold-open device is permitted to be used on a closure in a required fire separation, other than on an exit stair door in a building more than 3 storeys in building height and on a door for a vestibule required by Article 3.3.5.7., provided the device is designed to release the closure in conformance with this Article. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.14.(2) | Hold-Open Devices | Except as provided in Sentences 3.1.8.14.(5) and 3.1.8.14.(6), where the building is provided with a fire alarm system, a hold-open device permitted by Sentence 3.1.8.14.(1) shall release (a) in a single-stage system, upon any signal from the fire alarm system, and (b) in a 2-stage system, (i) upon any alert signal from the fire alarm system, or (ii) upon actuation of any adjacent smoke detectors. | obc2019_divb | Div B | 3.1.8.12.(2) | 3.1.8.12. Hold-Open Devices | Except as provided in Sentences (5) and (6), where the building is provided with a fire alarm system, a hold-open device permitted by Sentence (1) shall release, (a) in a single-stage system, upon any signal from the fire alarm system, and (b) in a two-stage system, (i) upon any alert signal from the fire alarm system, or (ii) upon actuation of any adjacent smoke detectors. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.14.(3) | Hold-Open Devices | Where the building is provided with a fire alarm system, a hold-open device permitted by Sentence 3.1.8.14.(1) shall release upon a signal from a smoke detector connected to the fire alarm system and located as described in ULC CAN/ULC-S524-14 Installation of Fire Alarm Systems where the hold-open device is used on (a) an exit door, (b) a door opening into a public corridor, (c) an egress door referred to in Sentence 3.4.2.4.(2), (d) a closure serving an assembly, care, treatment, detention, or residential occupancy, (e) a door in a fire separation referred to in Sentence 3.3.1.7.(1) or Sentence 3.3.3.5.(4), or (f) a door required to function as part of a smoke control system. | obc2019_divb | Div B | 3.1.8.12.(3) | 3.1.8.12. Hold-Open Devices | Where the building is provided with a fire alarm system, a hold-open device permitted by Sentence (1) shall release upon a signal from a smoke detector connected to the fire alarm system and located as described in CAN/ULC-S524, "Installation of Fire Alarm Systems", where the hold-open device is used on, (a) an exit door, (b) a door opening into a public corridor, (c) an egress door referred to in Sentence 3.4.2.4.(2), (d) a door serving an assembly, care, care and treatment, detention, or residential occupancy, (e) a door in a fire separation referred to in Clause 3.3.1.7.(1)(b) or in Sentence 3.3.3.5.(4) or 3.3.4.11.(4), or (f) a door required to function as part of a smoke control system. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.1.8.14.(4) | Hold-Open Devices | Where the building is not provided with a fire alarm system, a hold-open device permitted by Sentence 3.1.8.14.(1) shall release upon a signal from a smoke alarm located on each side of the fire separation at ceiling level within 1.5 m horizontally of the closure opening in the fire separation, where the hold-open device is used on closures described in Clauses 3.1.8.14.(3)(a) to 3.1.8.14.(3)(e). | obc2019_divb | Div B | 3.1.8.12.(4) | 3.1.8.12. Hold-Open Devices | Where the building is not provided with a fire alarm system, a hold-open device permitted by Sentence (1) shall release upon a signal from a smoke alarm located on either side of the fire separation at ceiling level within 1.5 m horizontally of the closure opening in the fire separation, where the hold-open device is used on closures described in Clauses (3)(a) to (e). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.14.(5) | Hold-Open Devices | Where a hold-open device is used on closures other than those described in Sentences 3.1.8.14.(3) and 3.1.8.14.(4), it is permitted to be released upon actuation of a heat-actuated device. | obc2019_divb | Div B | 3.1.8.12.(5) | 3.1.8.12. Hold-Open Devices | Where a hold-open device is used on closures other than those described in Sentences (3) and (4), it is permitted to be released upon actuation of a heat-actuated device. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.14.(6) | Hold-Open Devices | A hold-open device used on a door located between a corridor used by the public and an adjacent sleeping room in a treatment occupancy need not release automatically as stated in Sentence 3.1.8.14.(2). | obc2019_divb | Div B | 3.1.8.12.(6) | 3.1.8.12. Hold-Open Devices | A hold-open device used on a door located between a corridor used by the public and an adjacent sleeping room in a care and treatment occupancy need not release automatically as described in Sentence (2). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.15.(1) | Door Latches | Except as permitted by Article 3.3.3.5., a swing-type door in a fire separation shall be equipped with a positive latching mechanism designed to hold the door in the closed position after each use. | obc2019_divb | Div B | 3.1.8.13.(1) | 3.1.8.13. Door Latches | Except as permitted by Sentence 3.3.3.2.(5) and Article 3.3.3.5., a swing-type door in a fire separation shall be equipped with a positive latching mechanism designed to hold the door in the closed position after each use. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.16.(1) | Wired Glass and Glass Block | Except as permitted by Articles 3.1.8.18. and 3.1.8.19. for the separation of exits, an opening in a fire separation having a fire-resistance rating not more than 1 h is permitted to be protected with fixed wired glass assemblies or glass blocks installed in conformance with NFPA 80-2013 Fire Doors and Other Opening Protectives | obc2019_divb | Div B | 3.1.8.14.(1) | 3.1.8.14. Wired Glass and Glass Block | Except as permitted by Articles 3.1.8.16. and 3.1.8.17. for the separation of exits, an opening in a fire separation having a fire-resistance rating not more than 1 h is permitted to be protected with fixed wired glass assemblies or glass blocks installed in conformance with NFPA 80, "Fire Doors and Other Opening Protectives". |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.16.(2) | Wired Glass and Glass Block | Wired glass assemblies permitted by Sentence 3.1.8.16.(1) and described in are permitted to be used as closures in vertical fire separations without being tested in accordance with Sentence 3.1.8.4.(1). | obc2019_divb | Div B | 3.1.8.14.(2) | 3.1.8.14. Wired Glass and Glass Block | Wired glass assemblies permitted by Sentence (1) and described in MMAH Supplementary Standard SB-2, "Fire Performance Ratings", are permitted to be used as closures in vertical fire separations without being tested in accordance with Sentence 3.1.8.4.(1). |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.1.8.16.(3) | Wired Glass and Glass Block | Glass blocks permitted by Sentence 3.1.8.16.(1) shall be installed in accordance with part 4. and reinforced with steel reinforcement in each horizontal joint. | obc2019_divb | Div B | 3.1.8.14.(3) | 3.1.8.14. Wired Glass and Glass Block | Glass blocks permitted by Sentence (1) shall be installed in accordance with Subsection 4.3.2. and reinforced with steel reinforcement in each horizontal joint. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.17.(1) | Temperature Rise Limit for Doors | Except as permitted by Article 3.1.8.19., the maximum temperature rise on the opaque portion of the unexposed side of a door used as a closure in a fire separation in a location shown in Table 3.1.8.17. shall conform to the Table when tested in conformance with Sentence 3.1.8.4.(1). | obc2019_divb | Div B | 3.1.8.15.(1) | 3.1.8.15. Temperature Rise Limit for Doors | Except as permitted by Article 3.1.8.17., the maximum temperature rise on the opaque portion of the unexposed side of a door used as a closure in a fire separation in a location shown in Table 3.1.8.15., shall conform to the Table when tested in conformance with Sentence 3.1.8.4.(1). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.18.(1) | Area Limits for Wired Glass and Glass Block | Except as permitted by Article 3.1.8.19., the maximum area of wired glass in a door used in the locations shown in Table 3.1.8.17. shall conform to the Table. (See Note A-3.1.8.18.(1).) | obc2019_divb | Div B | 3.1.8.16.(1) | 3.1.8.16. Area Limits for Wired Glass and Glass Block | Except as permitted by Article 3.1.8.17., the maximum area of wired glass in a door used in the locations shown in Table 3.1.8.15. shall conform to the Table. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.18.(2) | Area Limits for Wired Glass and Glass Block | Except as permitted by Article 3.1.8.19., the maximum area of glass block and wired glass panels not in a door, used in the locations shown in Table 3.1.8.17., shall conform to the Table. | obc2019_divb | Div B | 3.1.8.16.(2) | 3.1.8.16. Area Limits for Wired Glass and Glass Block | Except as permitted by Article 3.1.8.17., the maximum area of glass block and wired glass panels not in a door, used in the locations shown in Table 3.1.8.15., shall conform to the Table. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.19.(1) | Temperature Rise and Area Limits Waived | The temperature rise limits and glass area limits required by Articles 3.1.8.17. and 3.1.8.18. are waived for a closure between an exit enclosure and an enclosed vestibule or corridor, provided the vestibule or corridor is separated from the remainder of the floor area by a fire separation having a fire-resistance rating not less than 45 min, the fire separation required by Sentence 3.1.8.19.(1) contains no wired glass or glass block within 3 m of the closure into the exit enclosure, and the vestibule or corridor contains no occupancy. | obc2019_divb | Div B | 3.1.8.17.(1) | 3.1.8.17. Temperature Rise and Area Limits Waived | The temperature rise limits and glass area limits required by Articles 3.1.8.15. and 3.1.8.16. are waived for a closure between an exit enclosure and an enclosed vestibule or corridor provided, the vestibule or corridor is separated from the remainder of the floor area by a fire separation having a fire-resistance rating not less than 45 min, the fire separation required by Clause (a) contains no wired glass or glass block within 3 m of the closure into the exit enclosure, and the vestibule or corridor contains no occupancy. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.2.(1) | Combustible Construction Support | Combustible construction that abuts on or is supported by a noncombustiblefire separation shall be constructed so that its collapse under fire conditions will not cause the collapse of the fire separation. | obc2019_divb | Div B | 3.1.8.2.(1) | 3.1.8.2. Combustible Construction Support | Combustible construction that abuts on or is supported by a noncombustible fire separation shall be constructed so that its collapse under fire conditions will not cause the collapse of the fire separation. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.3.(1) | Continuity of Fire Separations | Except as permitted by Sentence 3.6.4.2.(2), a horizontal service space or other concealed space located above a required vertical fire separation, including the walls of a vertical shaft, shall be divided at the fire separation by an equivalent fire separation within the service space. | obc2019_divb | Div B | 3.1.8.3.(1) | 3.1.8.3. Continuity of Fire Separations | Except as permitted by Sentence 3.6.4.2.(2), a horizontal service space or other concealed space located above a required vertical fire separation, including the walls of a vertical shaft, shall be divided at the fire separation by an equivalent fire separation within the service space. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.3.(2) | Continuity of Fire Separations | The fire separation required by Sentence 3.1.8.3.(1) shall terminate so that smoke-tight joints are provided where it abuts on or intersects a floor, a roof slab, or a roof deck. | obc2019_divb | Div B | 3.1.8.3.(2) | 3.1.8.3. Continuity of Fire Separations | The fire separation required by Sentence (1) shall terminate so that smoke-tight joints are provided where it abuts on or intersects, (a) a floor, (b) a roof slab, or (c) a roof deck. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.3.(3) | Continuity of Fire Separations | Except as required by part 3. for a shaft penetrating a roof assembly, a shaft, including an exit enclosure, that penetrates a fire separation, shall extend through any horizontal service space or any other concealed space, and terminate so that smoke-tight joints are provided where the shaft abuts on or intersects a floor, a roof slab, or a roof deck. | obc2019_divb | Div B | 3.1.8.3.(3) | 3.1.8.3. Continuity of Fire Separations | Except as required by Subsection 3.6.3. for a shaft penetrating a roof assembly, a shaft, including an exit enclosure, that penetrates a fire separation, shall, (a) extend through any horizontal service space or any other concealed space, and (b) terminate so that smoke-tight joints are provided where the shaft abuts on or intersects, (i) a floor, (ii) a roof slab, or (iii) a roof deck. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.3.(4) | Continuity of Fire Separations | The continuity of a fire separation shall be maintained where it abuts another fire separation, a floor, a ceiling, a roof, or an exterior wall assembly. (See Note A-3.1.8.3.(4).) | obc2019_divb | Div B | 3.1.8.3.(4) | 3.1.8.3. Continuity of Fire Separations | The continuity of a fire separation shall be maintained where it abuts another fire separation, a floor, a ceiling, or an exterior wall assembly. (See Appendix A.) |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.1.8.4.(1) | Determination of Ratings and Classifications | Except as permitted by Sentences 3.1.8.4.(2) and 3.1.8.16.(1), the fire-protection rating of a closure shall be determined in accordance with (a) CAN/ULC-S104-15 Fire Tests of Door Assemblies (b) CAN/ULC-S106-15 Fire Tests of Window and Glass Block Assemblies or (c) CAN/ULC-S112-10 Fire Test of Fire Damper Assemblies | obc2019_divb | Div B | 3.1.8.4.(1) | 3.1.8.4. Determination of Ratings | Except as permitted by Sentences (2) and 3.1.8.14.(1), the fire-protection rating for a closure shall be determined in accordance with, (a) CAN/ULC-S104, "Fire Tests of Door Assemblies", (b) CAN/ULC-S106, "Fire Tests of Window and Glass Block Assemblies", or (c) CAN/ULC-S112, "Fire Test of Fire Damper Assemblies". |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.4.(2) | Determination of Ratings and Classifications | Except as permitted by Sentence 3.1.8.12.(1), the fire-protection rating of a closure shall conform to Table 3.1.8.4. for the required fire-resistance rating of the fire separation. | obc2019_divb | Div B | 3.1.8.4.(2) | 3.1.8.4. Determination of Ratings | Except as permitted by Sentence 3.1.8.10.(1), the fire-protection rating of a closure shall conform to Table 3.1.8.4. for the required fire-resistance rating of the fire separation. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.1.8.4.(3) | Determination of Ratings and Classifications | The leakage rate of smoke dampers and combination smoke/fire dampers shall (a) be determined in accordance with the applicable provisions in ULC CAN/ULC-S112.1-10 Leakage Rated Dampers for Use in Smoke Control Systems and (b) conform to Class I, II or III of that standard. | obc2019_divb | Div B | 3.1.8.4.(3) | 3.1.8.4. Determination of Ratings | The leakage rate of smoke dampers and combination smoke and fire dampers shall, (a) be determined in accordance with the applicable provisions in CAN/ULC-S112.1, "Leakage Rated Dampers for Use in Smoke Control Systems", and (b) conform to Class I, II or III of that standard. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.4.(4) | Determination of Ratings and Classifications | The leakage rate of a door assembly shall be determined in accordance with UL ANSI/UL-1784-04 Air Leakage Tests of Door Assemblies and Other Opening Protectives | obc2019_divb | Div B | 3.1.8.4.(4) | 3.1.8.4. Determination of Ratings | The leakage rate of a door assembly shall be determined in accordance with ANSI/UL-1784, "Air Leakage Tests of Door Assemblies and Other Opening Protectives". |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.5.(1) | Installation of Closures | Except where fire dampers, window assemblies and glass block are used as closures, closures of the same fire-protection rating installed on opposite sides of the same opening are deemed to have a fire-protection rating equal to the sum of the fire-protection ratings of the closures. (See Note A-3.1.8.1.(2).) | obc2019_divb | Div B | 3.1.8.5.(1) | 3.1.8.5. Installation of Closures | Except where fire dampers, window assemblies and glass block are used as closures, closures of the same fire-protection rating installed on opposite sides of the same opening are deemed to have a fire-protection rating equal to the sum of the fire-protection ratings of the closures. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.5.(2) | Installation of Closures | Except as otherwise specified in this Part, every door, fire damper , window assembly or glass block used as a closure in a required fire separation shall be installed in conformance with NFPA 80-2013 Fire Doors and Other Opening Protectives (See Note A-3.1.8.1.(2).) | obc2019_divb | Div B | 3.1.8.5.(2) | 3.1.8.5. Installation of Closures | Except as otherwise specified in this Part, every door, fire damper, window assembly or glass block used as a closure in a required fire separation, (a) shall be installed in conformance with NFPA 80, "Fire Doors and Other Opening Protectives", and (b) where required to have a fire-protection rating, shall have labels or classification marks to identify the testing laboratory. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.1.8.5.(3) | Installation of Closures | Except as otherwise specified in this Part, every smoke damper or combination smoke/fire damper used as a closure in a required fire separation shall be installed in conformance with NFPA 105-2013 Smoke Door Assemblies and Other Opening Protectives | obc2019_divb | Div B | 3.1.8.5.(3) | 3.1.8.5. Installation of Closures | Except as otherwise specified in this Part, every smoke damper used as a closure in a required fire separation shall be installed in conformance with NFPA 105, "Smoke Door Assemblies and Other Opening Protectives". |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.1.8.5.(4) | Installation of Closures | If a door is installed such that it could damage the integrity of a fire separation if its swing is unrestricted, door stops shall be installed to prevent the damage. | obc2019_divb | Div B | 3.1.8.5.(4) | 3.1.8.5. Installation of Closures | If a door is installed so that it could damage the integrity of a fire separation if its swing is unrestricted, door stops shall be installed to prevent the damage. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.5.(6) | Installation of Closures | A leakage-rated door assembly complying with Sentence 3.1.8.4.(4) shall be installed in (a) fire separations in protected floor areas referred to in Clause 3.3.1.7.(1)(b), (b) fire separations in care or treatment occupancies referred to in Sentence 3.3.3.5.(4), (c) except as provided in Sentence 3.1.8.5.(8), fire separations of public corridors serving dwelling units in storeys that are not sprinklered, and (d) firewalls that are a horizontal exit referred to in Sentence 3.3.3.5.(3). | obc2019_divb | Div B | 3.1.8.5.(5) | 3.1.8.5. Installation of Closures | A leakage-rated door assembly rated in accordance with Sentence 3.1.8.4.(4) shall, (a) be installed in fire separations in protected floor areas described in Clause 3.3.1.7.(1)(b), (b) be installed in fire separations in care or care and treatment occupancies referred to in Sentence 3.3.3.5.(4) and installed in fire separations in retirement homes referred to in Sentence 3.3.4.11.(4), (c) except as provided in Sentence (7), be installed in fire separations of public corridors serving dwelling units in storeys that are not sprinklered, and (d) be installed in firewalls that are a horizontal exit referred to in Sentence 3.3.3.5.(3). |  | Common Sentence | Yes | Retirement Homes
2015 | ON | NBC | Div B | 3.1.8.5.(7) | Installation of Closures | Leakage-rated door assemblies required by Sentence 3.1.8.5.(6) shall be installed in accordance with NFPA 105-2013 Smoke Door Assemblies and Other Opening Protectives | obc2019_divb | Div B | 3.1.8.5.(6) | 3.1.8.5. Installation of Closures | Leakage-rated door assemblies required by Sentence (5) shall conform to NFPA 105, "Smoke Door Assemblies and Other Opening Protectives". |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.5.(8) | Installation of Closures | A leakage-rated door assembly need not be installed where a dwelling unit served by a public corridor has a second and separate means of egress, or an open-air balcony that is sized to accommodate the number of occupants for which the dwelling unit is intended. | obc2019_divb | Div B | 3.1.8.5.(7) | 3.1.8.5. Installation of Closures | A leakage-rated door assembly need not be installed where a dwelling unit served by a public corridor has, a second and separate means of egress, or an open-air balcony that is sized to accommodate the number of occupants for which the dwelling unit is intended. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.6.(1) | Maximum Openings | The size of an opening in an interior fire separation required to be protected with a closure shall be not more than 11 m2, with no dimension more than 3.7 m, if a fire compartment on either side of the fire separation is not sprinklered. | obc2019_divb | Div B | 3.1.8.6.(1) | 3.1.8.6. Maximum Openings | The size of an opening in an interior fire separation required to be protected with a closure shall be not more than 11 m2, with no dimension more than 3.7 m, if a fire compartment on either side of the fire separation is not sprinklered. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.6.(2) | Maximum Openings | The size of an opening in an interior fire separation required to be protected with a closure shall be not more than 22 m2, with no dimension more than 6 m, provided the fire compartments on both sides of the fire separation are sprinklered. | obc2019_divb | Div B | 3.1.8.6.(2) | 3.1.8.6. Maximum Openings | The size of an opening in an interior fire separation required to be protected with a closure shall be not more than 22 m2, with no dimension more than 6 m, provided the fire compartments on both sides of the fire separation are sprinklered. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.7.(1) | Location of Fire Dampers and Smoke Dampers | Except as provided in Article 3.1.8.8., a fire damper having a fire-protection rating conforming to Sentence 3.1.8.4.(2) shall be installed in conformance with Article 3.1.8.10. in ducts or air-transfer openings that penetrate an assembly required to be a fire separation. | obc2019_divb | Div B | 3.1.8.7.(1) | 3.1.8.7. Location of Fire Dampers and Smoke Dampers | Except as provided in Article 3.1.8.8., a fire damper having a fire-protection rating conforming to Sentence 3.1.8.4.(2) shall be installed in conformance with Article 3.1.8.9. in ducts or air-transfer openings that penetrate an assembly required to be a fire separation. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.7.(2) | Location of Fire Dampers and Smoke Dampers | Except as provided in Article 3.1.8.9., a smoke damper or a combination smoke/fire damper shall be installed in conformance with Article 3.1.8.11. in ducts or air-transfer openings that penetrate an assembly required to be a fire separation, where the fire separation (a) separates a public corridor, (b) contains an egress door referred to in Sentence 3.4.2.4.(2), (c) serves an assembly, care, treatment, detention or residential occupancy, or (d) is installed to meet the requirements of Sentence 3.3.1.7.(1) or Sentence 3.3.3.5.(4). | obc2019_divb | Div B | 3.1.8.7.(2) | 3.1.8.7. Location of Fire Dampers and Smoke Dampers | Except as provided in Article 3.1.8.8A., a smoke damper or a combination smoke and fire damper shall be installed in conformance with Article 3.1.8.9A. in ducts or air-transfer openings that penetrate an assembly required to be a fire separation, where the fire separation, (a) separates a public corridor, (b) contains an egress door referred to in Sentence 3.4.2.4.(2), (c) serves an assembly, care, care and treatment, detention or residential occupancy, or (d) is installed to meet the requirements of Clause 3.3.1.7.(1)(b) or Sentence 3.3.3.5.(4) or 3.3.4.11.(4). |  | Common Sentence | Yes | Retirement Homes
2015 | ON | NBC | Div B | 3.1.8.8.(1) | Fire Dampers Waived | Except as provided in Sentence 3.1.8.8.(2), the requirement for fire dampers stated in Sentence 3.1.8.7.(1) is permitted to be waived for (a) ducts that serve commercial cooking equipment (see also Article 6.3.1.7.), (b) continuous noncombustible ducts having a melting point above 760Â°C that penetrate a vertical fire separation required by Sentence 3.3.1.1.(1) between suites of assembly, mercantile, low-hazard industrial, medium-hazard industrial or high-hazard industrial occupancy, (c) ducts or air-transfer openings that penetrate a vertical fire separation not required to have a fire-resistance rating, or (d) noncombustible ducts or air-transfer openings that penetrate a horizontal fire separation not required to have a fire-resistance rating. | obc2019_divb | Div B | 3.1.8.8.(1) | 3.1.8.8. Fire Dampers Waived | Except as permitted in Sentences (2) to (4), the requirement for fire dampers described in Sentence 3.1.8.7.(1) is permitted to be waived for, (a) ducts that serve commercial cooking equipment, (b) continuous noncombustible ducts having a melting point above 760Ã‚Â°C that penetrate a vertical fire separation required by Sentence 3.3.1.1.(1) between suites of assembly, mercantile, low hazard industrial, medium hazard industrial or high hazard industrial occupancy, (c) ducts or air-transfer openings that penetrate a vertical fire separation not required to have a fire-resistance rating, and (d) noncombustible ducts or air-transfer openings that penetrate a horizontal fire separation not required to have a fire-resistance rating. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.8.(2) | Fire Dampers Waived | The requirement for fire dampers stated in Sentence 3.1.8.7.(1) is permitted to be waived for noncombustible branch ducts having a melting point above 760Â°C that penetrate a fire separation, (a) provided the ducts (i) have a cross-sectional area not more than 0.013 m2 and serve only air-conditioning units or combined air-conditioning and heating units discharging air not more than 1.2 m above the floor, or (ii) extend not less than 500 mm inside exhaust duct risers that are under negative pressure and in which the airflow is upward as required by Article 3.6.3.4., or (b) where the fire separation separates a vertical service space from the remainder of the building, provided each individual duct exhausts directly to the outdoors at the top of the vertical service space. | obc2019_divb | Div B | 3.1.8.8.(2) | 3.1.8.8. Fire Dampers Waived | The requirement for fire dampers described in Sentence 3.1.8.7.(1) is permitted to be waived for noncombustible branch ducts having a melting point above 760Ã‚Â°C that penetrate a fire separation, (a) provided the ducts, (i) have a cross-sectional area not more than 130 cm2 and serve only air-conditioning units or combined air-conditioning and heating units discharging air not more than 1.2 m above the floor, or (ii) extend not less than 500 mm inside exhaust duct risers that are under negative pressure and in which the airflow is upward as required by Article 3.6.3.4., or (b) provided the fire separation separates a vertical service space from the remainder of the building and provided each individual duct exhausts directly to the outdoors at the top of the vertical service space. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.9.(1) | Smoke Dampers Waived | Except as provided in Sentence 3.1.8.9.(2), the requirement for smoke dampers or combination smoke/fire dampers stated in Sentence 3.1.8.7.(2) is permitted to be waived for ducts (a) that serve commercial cooking equipment (see also Article 6.3.1.7.), (b) in which all inlet and outlet openings serve not more than one fire compartment, or (c) that penetrate a vertical fire separation referred to in Sentence 3.3.1.7.(1) or in Sentence 3.3.3.5.(4), provided (i) the movement of air is continuous, and (ii) the configuration of the air-handling system prevents the recirculation of exhaust or return air under fire emergency conditions. | obc2019_divb | Div B | 3.1.8.8.(1) | 3.1.8.8A. Smoke Dampers Waived | Except as permitted in Sentence (2), the requirement for smoke dampers or combination smoke and fire dampers described in Sentence 3.1.8.7.(2) is permitted to be waived for ducts, (a) that serve commercial cooking equipment, (b) in which all inlet and outlet openings serve not more than one fire compartment, or (c) that penetrate a vertical fire separation referred to in Clause 3.3.1.7.(1)(b) or in Sentence 3.3.3.5.(4), provided, (i) the movement of air is continuous, (ii) and the configuration of the air-handling system prevents the recirculation of exhaust or return air under fire emergency conditions. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.8.9.(2) | Smoke Dampers Waived | The requirement for smoke dampers or combination smoke/fire dampers stated in Sentence 3.1.8.7.(2) is permitted to be waived for noncombustible branch ducts having a melting point above 760Â°C that penetrate a fire separation, (a) provided the ducts (i) have a cross-sectional area not more than 0.013 m2 and serve only air-conditioning units or combined air-conditioning and heating units discharging air not more than 1.2 m above the floor, (ii) extend not less than 500 mm inside exhaust duct risers that are under negative pressure and in which the airflow is upward as required by Article 3.6.3.4., or (iii) are required to function as part of a smoke control system, or (b) where the fire separation separates a vertical service space from the remainder of the building, provided each individual duct exhausts directly to the outdoors at the top of the vertical service space. | obc2019_divb | Div B | 3.1.8.8.(2) | 3.1.8.8A. Smoke Dampers Waived | The requirement for smoke dampers or combination smoke and fire dampers described in Sentence 3.1.8.7.(2) is permitted to be waived for noncombustible branch ducts having a melting point above 760Ã‚Â°C that penetrate a fire separation, (a) provided the ducts, (i) have a cross-sectional area not more than 130 cmÃ‚Â² and serve only air-conditioning units or combined air-conditioning and heating units discharging air not more than 1.2 m above the floor, (ii) extend not less than 500 mm inside exhaust duct risers that are under negative pressure and in which the airflow is upward as required by Article 3.6.3.4., or (iii) are required to function as part of a smoke control system, or (b) provided the fire separation separates a vertical service space from the remainder of the building and provided each individual duct exhausts directly to the outdoors at the top of the vertical service space. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.9.1.(1) | Fire Stops | Except as provided in Sentences 3.1.9.1.(2) to 3.1.9.1.(5) and Article 3.1.9.4., penetrations of a fire separation or a membrane forming part of an assembly required to have a fire-resistance rating shall be (a) sealed by a fire stop that, when subjected to the fire test method in ULC CAN/ULC-S115-11 Fire Tests of Firestop Systems has an F rating not less than the fire-protection rating required for closures in the fire separation in conformance with Table 3.1.8.4., or (b) cast in place (see Note A-3.1.9.1.(1)(b)). | obc2019_divb | Div B | 3.1.9.1.(1) | 3.1.9.1. Fire Stops | Except as provided in Sentences (2) to (5) and Article 3.1.9.3A., penetrations of a fire separation or a membrane forming part of an assembly required to have a fire-resistance rating shall be, (a) sealed by a fire stop that, when subjected to the fire test method in CAN/ULC-S115, "Fire Tests of Firestop Systems", has an F rating not less than the fire-protection rating required for closures in the fire separation in conformance with Table 3.1.8.4., or (b) tightly fitted. (See Appendix A.) |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.1.9.1.(2) | Fire Stops | Penetrations of a firewall or a horizontal fire separation that is required to have a fire-resistance rating in conformance with Article 3.2.1.2. shall be sealed at the penetration by a fire stop that, when subjected to the fire test method in ULC CAN/ULC-S115-11 Fire Tests of Firestop Systems has an FT rating not less than the fire-resistance rating for the fire separation. | obc2019_divb | Div B | 3.1.9.1.(2) | 3.1.9.1. Fire Stops | Penetrations of a firewall or a horizontal fire separation that is required to have a fire-resistance rating in conformance with Article 3.2.1.2. shall be sealed at the penetration by a fire stop that, when subjected to the fire test method in CAN/ULC-S115, "Fire Tests of Firestop Systems", has an FT rating not less than the fire-resistance rating required for the fire separation. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.9.1.(3) | Fire Stops | Penetrations of a fire separation in conformance with Sentence 3.6.4.2.(2) shall be sealed by a fire stop that, when subjected to the fire test method in ULC CAN/ULC-S115-11 Fire Tests of Firestop Systems has an FT rating not less than the fire-resistance rating for the fire separation of the assembly. | obc2019_divb | Div B | 3.1.9.1.(3) | 3.1.9.1. Fire Stops | Penetrations of a fire separation in conformance with Sentence 3.6.4.2.(2) shall be sealed by a fire stop that, when subjected to the fire test method in CAN/ULC-S115, "Fire Tests of Firestop Systems", has an FT rating not less than the fire-resistance rating required for the fire separation of the assembly. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.9.1.(4) | Fire Stops | Sprinklers are permitted to penetrate a fire separation or a membrane forming part of an assembly required to have a fire-resistance rating without having to meet the fire stop requirements of Sentences 3.1.9.1.(1)to 3.1.9.1.(3), provided the annular space created by the penetration of a fire sprinkler is covered by a metal escutcheon plate in accordance with NFPA 13-2013 Installation of Sprinkler Systems | obc2019_divb | Div B | 3.1.9.1.(4) | 3.1.9.1. Fire Stops | Sprinklers are permitted to penetrate a fire separation or a membrane forming part of an assembly required to have a fire-resistance rating without having to meet the fire stop requirements of Sentence (1), (2) or (3), provided the annular space created by the penetration of a fire sprinkler is covered by a metal escutcheon plate in accordance with NFPA 13, "Installation of Sprinkler Systems". |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.9.1.(5) | Fire Stops | Unless specifically designed with a fire stop, fire dampers are permitted to penetrate a fire separation or a membrane forming part of an assembly required to have a fire-resistance rating without having to meet the fire stop requirements of Sentences 3.1.9.1.(1) to 3.1.9.1.(3), provided the fire damper is installed in conformance with NFPA 80-2013 Fire Doors and Other Opening Protectives | obc2019_divb | Div B | 3.1.9.1.(5) | 3.1.9.1. Fire Stops | Unless specifically designed with a fire stop, fire dampers are permitted to penetrate a fire separation or a membrane forming part of an assembly required to have a fire-resistance rating without having to meet the fire stop requirements of Sentence (1), (2) or (3), provided the fire damper is installed in conformance with NFPA 80, "Fire Doors and Other Opening Protectives". |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.9.2.(1) | Combustibility of Service Penetrations | Except as permitted by Articles 3.1.9.3. and 3.1.9.5., pipes, ducts, electrical outlet boxes, totally enclosed raceways or other similar service equipment that penetrate an assembly required to have a fire-resistance rating shall be noncombustible, unless the assembly was tested incorporating that service equipment. (See Note A-3.1.9.2.(1).) | obc2019_divb | Div B | 3.1.9.2.(1) | 3.1.9.2. Combustibility of Service Penetrations | Except as permitted by Articles 3.1.9.3. and 3.1.9.4., pipes, ducts, electrical outlet boxes, totally enclosed raceways or other similar service equipment that penetrate an assembly required to have a fire-resistance rating shall be noncombustible unless the assembly has been tested incorporating that service equipment. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.9.3.(1) | Penetration by Wires, Cables and Outlet Boxes | Optical fibre cables and electrical wires and cables in totally enclosed noncombustible raceways are permitted to penetrate an assembly required to have a fire-resistance rating without being incorporated in the assembly at the time of testing as required by Article 3.1.9.2. | obc2019_divb | Div B | 3.1.9.3.(1) | 3.1.9.3. Penetration by Wires, Cables and Outlet Boxes | Optical fibre cables and electrical wires and cables in totally enclosed noncombustible raceways are permitted to penetrate an assembly required to have a fire-resistance rating without being incorporated in the assembly at the time of testing as required by Article 3.1.9.2. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.9.3.(2) | Penetration by Wires, Cables and Outlet Boxes | Except as permitted by Sentence 3.1.9.3.(3), totally enclosed non-metallic raceways conforming to Article 3.1.5.23., optical fibre cables, and electrical wires and cables, single or grouped, with combustible insulation, jackets or sheathes that conform to the requirements of Sentence 3.1.5.21.(1) and that are not installed in totally enclosed noncombustible raceways are permitted to penetrate an assembly required to have a fire-resistance rating without being incorporated in the assembly at the time of testing as required by Article 3.1.9.2., provided the overall diameter of the single or grouped wires or cables, or the raceways is not more than 25 mm. | obc2019_divb | Div B | 3.1.9.3.(2) | 3.1.9.3. Penetration by Wires, Cables and Outlet Boxes | Except as permitted by Sentence (3), totally enclosed nonmetallic raceways conforming to Article 3.1.5.20., optical fibre cables, and electrical wires and cables, single or grouped, with combustible insulation, jackets or sheathes that conform to the requirements of Clause 3.1.5.18.(1)(a) and that are not installed in totally enclosed noncombustible raceways are permitted to penetrate an assembly required to have a fire-resistance rating without being incorporated in the assembly at the time of testing as required by Article 3.1.9.2., provided the overall diameter of the single or grouped wires or cables, or the raceways is not more than 25 mm. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.9.3.(3) | Penetration by Wires, Cables and Outlet Boxes | Single conductor metal sheathed cables with combustible jacketting that are more than 25 mm in overall diameter are permitted to penetrate a fire separation required to have a fire-resistance rating without being incorporated in the assembly at the time of testing as required by Article 3.1.9.2., provided the cables are not grouped and are spaced a minimum of 300 mm apart. | obc2019_divb | Div B | 3.1.9.3.(3) | 3.1.9.3. Penetration by Wires, Cables and Outlet Boxes | Single conductor metal sheathed cables with combustible jacketing that are more than 25 mm in overall diameter are permitted to penetrate a fire separation required to have a fire-resistance rating without being incorporated in the assembly at the time of testing as required by Article 3.1.9.2., provided the cables are not grouped and are spaced a minimum of 300 mm apart. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.9.3.(4) | Penetration by Wires, Cables and Outlet Boxes | Combustible totally enclosed raceways that are embedded in a concrete floor slab are permitted in an assembly required to have a fire-resistance rating without being incorporated in the assembly at the time of testing as required by Article 3.1.9.2., provided the concrete cover between the raceway and the bottom of the slab is not less than 50 mm. | obc2019_divb | Div B | 3.1.9.3.(4) | 3.1.9.3. Penetration by Wires, Cables and Outlet Boxes | Combustible totally enclosed raceways that are embedded in a concrete floor slab are permitted in an assembly required to have a fire-resistance rating without being incorporated in the assembly at the time of testing as required by Article 3.1.9.2., provided the concrete cover between the raceway and the bottom of the slab is not less than 50 mm. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.9.3.(5) | Penetration by Wires, Cables and Outlet Boxes | Combustible outlet boxes are permitted in an assembly required to have a fire-resistance rating without being incorporated in the assembly at the time of testing as required by Article 3.1.9.2., provided the opening through the membrane into the box is not more than 0.016 m2 . | obc2019_divb | Div B | 3.1.9.3.(5) | 3.1.9.3. Penetration by Wires, Cables and Outlet Boxes | Combustible electrical outlet boxes are permitted in an assembly required to have a fire-resistance rating without being incorporated in the assembly at the time of testing as required by Article 3.1.9.2., provided the opening through the membrane into the box is not more than 160 cm2. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.9.4.(1) | Penetration by Outlet Boxes | Except as provided in Sentence 3.1.9.4.(2), outlet boxes are permitted to penetrate the membrane of an assembly required to have a fire-resistance rating, provided they are sealed at the penetration by a fire stop that has an FT rating not less than the fire-resistance rating of the fire separation when subjected to the fire test method in ULC CAN/ULC-S115-11 Fire Tests of Firestop Systems | obc2019_divb | Div B | 3.1.9.3.(1) | 3.1.9.3A. Penetration by Outlet Boxes | Except as provided in Sentences (2) and (3), outlet boxes are permitted to penetrate the membrane of an assembly required to have a fire-resistance rating, provided they are sealed at the penetration by a fire stop that has an FT rating not less than the fire-resistance rating of the fire separation when subjected to the fire test method in CAN/ULC-S115, "Fire Tests of Firestop Systems". |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.9.4.(2) | Penetration by Outlet Boxes | Except as provided in Sentences 3.1.9.1.(2) and 3.1.9.1.(3), noncombustible outlet boxes that penetrate a vertical fire separation or a membrane forming part of an assembly required to have a fire-resistance rating need not conform to Sentence 3.1.9.4.(1), provided they do not exceed 0.016 m2 in area, and an aggregate area of 0.065 m2 in any 9.3 m2 of surface area, and the annular space between the membrane and the noncombustible electrical outlet boxes does not exceed 3 mm. | obc2019_divb | Div B | 3.1.9.3.(6) | 3.1.9.3. Penetration by Wires, Cables and Outlet Boxes | Noncombustible electrical outlet boxes that penetrate a fire separation or a membrane forming part of an assembly required to have a fire-resistance rating need not meet the requirements of Article 3.1.9.1. provided, they do not exceed, 100 cm2 each in area, and an aggregate area of 650 cm2 in any 9.3 m2 of surface area, and the annular space between the membrane and the box does not exceed 3 mm. |  | Common Sentence | Yes | Construction Materials
2015 | ON | NBC | Div B | 3.1.9.4.(2) | Penetration by Outlet Boxes | Except as provided in Sentences 3.1.9.1.(2) and 3.1.9.1.(3), noncombustible outlet boxes that penetrate a vertical fire separation or a membrane forming part of an assembly required to have a fire-resistance rating need not conform to Sentence 3.1.9.4.(1), provided they do not exceed 0.016 m2 in area, and an aggregate area of 0.065 m2 in any 9.3 m2 of surface area, and the annular space between the membrane and the noncombustible electrical outlet boxes does not exceed 3 mm. | obc2019_divb | Div B | 3.1.9.3.(2) | 3.1.9.3A. Penetration by Outlet Boxes | Except as provided in Sentences 3.1.9.1.(2) and (3), noncombustible outlet boxes that penetrate a vertical fire separation or a membrane forming part of an assembly required to have a fire-resistance rating need not conform to Sentence (1), provided, they do not exceed, 160 cmÃ‚Â² in area, and an aggregate area of 650 cmÃ‚Â² in any 9.3 mÃ‚Â² of surface area, and the annular space between the membrane and noncombustible electrical outlet boxes does not exceed 3 mm. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.9.4.(3) | Penetration by Outlet Boxes | In addition to the requirements of Sentence (2), outlet boxes on opposite sides of vertical fire separation having a fire-resistance rating shall be separated by (a) a horizontal distance of not less than 600 mm, or (b) a fire block conforming to Article 3.1.11.7. | obc2019_divb | Div B | 3.1.9.3.(7) | 3.1.9.3. Penetration by Wires, Cables and Outlet Boxes | Unless provided with a fire stop in accordance with CAN/ULC-S115, "Fire Tests of Firestop Systems", electrical outlet boxes on opposite sides of a vertical fire separation required to have a fire-resistance rating shall be, separated by a horizontal distance of not less than 600 mm, or installed in adjacent stud cavities. |  | Common Sentence | Yes | Construction Materials
2015 | ON | NBC | Div B | 3.1.9.4.(3) | Penetration by Outlet Boxes | In addition to the requirements of Sentence 3.1.9.4.(2), outlet boxes on opposite sides of a vertical fire separation having a fire-resistance rating shall be separated by a horizontal distance of not less than 600 mm, or a fire block conforming to Article 3.1.11.7. | obc2019_divb | Div B | 3.1.9.3.(3) | 3.1.9.3A. Penetration by Outlet Boxes | (3) In addition to the requirements of Sentence (2), outlet boxes on opposite sides of a vertical fire separation having a fire-resistance rating shall be separated by, a horizontal distance of not less than 600 mm, or a fire block conforming to Article 3.1.11.7. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.1.9.5.(3) | Combustible Piping Penetrations | Except as permitted by Sentences 3.1.9.5.(4) to 3.1.9.5.(5), combustible piping shall not be used in a drain, waste and vent piping system if any part of that system penetrates (a) a fire separation required to have a fire-resistance rating, or (b) a membrane that forms part of an assembly required to have a fire-resistance rating. | obc2019_divb | Div B | 3.1.9.4.(1) | 3.1.9.4. Combustible Piping Penetrations | Except as permitted by Sentences (3) to (8), combustible piping shall not be used if any part of the piping system penetrates, a fire separation required to have a fire-resistance rating, or a membrane that forms part of an assembly required to have a fire-resistance rating. |  | Common Sentence | Yes | Construction Materials
2015 | ON | NBC | Div B | 3.1.9.5.(4) | Combustible Piping Penetrations | Combustible drain, waste and vent piping is permitted to penetrate a fire separation required to have a fire-resistance rating or a membrane that forms part of an assembly required to have a fire-resistance rating, provided the piping is sealed at the penetration by a fire stop that has an F rating not less than the fire-resistance rating required for the fire separation when subjected to the fire test method in ULC CAN/ULC-S115-11 Fire Tests of Firestop Systems with a pressure differential of 50 Pa between the exposed and unexposed sides, with the higher pressure on the exposed side, and the piping is not located in a vertical service space. | obc2019_divb | Div B | 3.1.9.4.(3) | 3.1.9.4. Combustible Piping Penetrations | Except as provided by Sentences (4) to (7), combustible piping is permitted to penetrate a fire separation required to have a fire-resistance rating or is permitted to penetrate a membrane that forms part of an assembly required to have a fire-resistance rating, provided the piping is sealed at the penetration by a fire stop that has an F rating not less than the fire-resistance rating required for the fire separation when subjected to the fire test method in CAN/ULC-S115, "Fire Tests of Firestop Systems", with a pressure differential of 50 Pa between the exposed and unexposed sides, with the higher pressure on the exposed side. |  | Common Sentence | Yes | Construction Materials
2015 | ON | NBC | Div B | 3.1.9.5.(5) | Combustible Piping Penetrations | Combustible drain, waste and vent piping is permitted on one side of a vertical fire separation provided it is not located in a vertical service space. | obc2019_divb | Div B | 3.1.9.4.(2) | 3.1.9.4. Combustible Piping Penetrations | Combustible piping that is part of a system described in Sentence (1) shall not be located in a vertical service space. |  | Common Sentence | Yes | Construction Materials
2015 | ON | NBC | Div B | 3.1.9.5.(6) | Combustible Piping Penetrations | Combustible piping for central vacuum systems is permitted to penetrate a fire separation provided the installation conforms to the requirements that apply to combustible drain, waste and vent piping specified in Sentence 3.1.9.5.(4). | obc2019_divb | Div B | 3.1.9.4.(8) | 3.1.9.4. Combustible Piping Penetrations | Combustible piping for central vacuum cleaning systems is permitted to penetrate a fire separation, provided the installation conforms to the requirements that apply to combustible piping specified in Sentence (3). |  | Common Sentence | Yes | Construction Materials
2015 | ON | NBC | Div B | 3.1.9.6.(1) | Openings through a Membrane Ceiling | A membrane ceiling forming part of an assembly assigned a fire-resistance rating on the basis of Appendix is permitted to be penetrated by openings leading into ducts within the ceiling space, provided (a) the ducts are sheet steel, and (b) the number of openings and their protection conform to the requirements of Appendix. | obc2019_divb | Div B | 3.1.9.5.(1) | 3.1.9.5. Openings Through a Membrane Ceiling | A membrane ceiling forming part of an assembly assigned a fire-resistance rating on the basis of MMAH Supplementary Standard SB-2, "Fire Performance Ratings", is permitted to be penetrated by openings leading into ducts within the ceiling space provided, (a) the ducts are sheet steel, and (b) the amount of openings and their protection conform to the requirements of MMAH Supplementary Standard SB-2, "Fire Performance Ratings". |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.1.9.7.(1) | Plenums | A ceiling assembly used as a plenum shall conform to Article 3.6.4.3. | obc2019_divb | Div B | 3.1.9.6.(1) | 3.1.9.5. Openings Through a Membrane Ceiling | A membrane ceiling forming part of an assembly assigned a fire-resistance rating on the basis of MMAH Supplementary Standard SB-2, "Fire Performance Ratings", is permitted to be penetrated by openings leading into ducts within the ceiling space provided, the ducts are sheet steel, and the amount of openings and their protection conform to the requirements of MMAH Supplementary Standard SB-2, "Fire Performance Ratings". |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.1.1.(1) | Exceptions in Determining Building Height | A roof-top enclosure provided for elevator machinery, a stairway or a service room used for no purpose other than for service to the building, shall not be considered as a storey in calculating the building height. | obc2019_divb | Div B | 3.2.1.1.(1) | 3.2.1.1. Exceptions in Determining Building Height | A rooftop enclosure provided for elevator machinery, a stairway or a service room used for no purpose other than for service to the building, shall not be considered as a storey in calculating the building height. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.1.1.(2) | Exceptions in Determining Building Height | Space under tiers of seats in a building of the arena type shall not be considered as adding to the building height provided the space is used only for dressing rooms, concession stands and similar purposes incidental to the major occupancy of the building. | obc2019_divb | Div B | 3.2.1.1.(2) | 3.2.1.1. Exceptions in Determining Building Height | Space under tiers of seats in a building of the arena type shall not be considered as adding to the building height provided the space is used only for dressing rooms, concession stands and similar purposes incidental to the major occupancy of the building. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.1.1.(3) | Exceptions in Determining Building Height | Except as required by Sentence 3.2.1.1.(5), the space above a mezzanine need not be considered as a storey in calculating the building height, provided the aggregate area of mezzanines that are not superimposed does not exceed 40% of the open area of the room in which they are located (see Note A-3.2.1.1.(3)(a)), and except as permitted in Sentences 3.2.1.1.(7) and 3.3.2.13.(3), the space above the mezzanine is used as an open area without partitions or subdividing walls higher than 1?070 mm above the mezzanine floor. | obc2019_divb | Div B | 3.2.1.1.(3) | 3.2.1.1. Exceptions in Determining Building Height | Except as required by Sentence (5), the space above a mezzanine need not be considered as a storey in calculating building height provided, the aggregate area of mezzanines that are not superimposed does not exceed 40% of the open area of the room in which they are located, and (See Appendix A.) except as permitted in Sentence (8) and Sentence 3.3.2.11.(3) the space above the mezzanine is used as an open area without partitions or subdividing walls higher than 1 070 mm above the mezzanine floor. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.1.1.(4) | Exceptions in Determining Building Height | Except as required by Sentence 3.2.1.1.(5), the space above a mezzanine need not be considered as a storey in calculating the building height, provided the aggregate area of mezzanines that are not superimposed and do not meet the conditions of Sentence 3.2.1.1.(3) does not exceed 10% of the floor area in which they are located, and the area of a mezzanine in a suite does not exceed 10% of the area of that suite. | obc2019_divb | Div B | 3.2.1.1.(4) | 3.2.1.1. Exceptions in Determining Building Height | Except as required by Sentence (5), the space above a mezzanine need not be considered as a storey in calculating the building height provided, the aggregate area of mezzanines that are not superimposed and do not meet the conditions of Sentence (3) does not exceed 10% of the floor area in which they are located, and the area of mezzanine in a suite does not exceed 10% of the area of that suite. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.1.1.(5) | Exceptions in Determining Building Height | Except as permitted by Sentence 3.2.1.1.(6), each level of mezzanine that is partly or wholly superimposed above the first level of mezzanine shall be considered as a storey in calculating the building height. | obc2019_divb | Div B | 3.2.1.1.(5) | 3.2.1.1. Exceptions in Determining Building Height | Except as permitted by Sentences (6) and (7), each level of mezzanine that is partly or wholly superimposed above the first level of mezzanine shall be considered as a storey in calculating the building height. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.1.1.(6) | Exceptions in Determining Building Height | Platforms intended solely for periodic inspection and elevated maintenance catwalks need not be considered as floor assemblies or mezzanines for the purpose of calculating building height, provided they are not used for storage, and they are constructed with noncombustible materials, unless the building is permitted to be of combustible construction. | obc2019_divb | Div B | 3.2.1.1.(6) | 3.2.1.1. Exceptions in Determining Building Height | Platforms intended solely for periodic inspection and elevated catwalks need not be considered as floor assemblies or mezzanines for the purpose of determining building height provided, they are not used for storage, they are constructed with noncombustible materials unless the building is permitted to be of combustible construction, and where they are intended to be occupied, they have an occupant load of not more than four persons. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.1.1.(7) | Exceptions in Determining Building Height | The space above a mezzanine conforming to Sentence 3.2.1.1.(3) is permitted to include an enclosed space whose area does not exceed 10% of the open area of the room in which the mezzanine is located provided the enclosed space does not obstruct visual communication between the open space above the mezzanine and the room in which it is located. (See Note A-3.2.1.1.(3)(a).) | obc2019_divb | Div B | 3.2.1.1.(8) | 3.2.1.1. Exceptions in Determining Building Height | The space above a mezzanine conforming to Sentence (3) is permitted to include an enclosed space whose area does not exceed 10% of the open area of the room in which the mezzanine is located, provided the enclosed space does not obstruct visual communication between the open space above the mezzanine and the room in which it is located. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.1.1.(8) | Exceptions in Determining Building Height | A service space in which facilities are included to permit a person to enter and to undertake maintenance and other operations pertaining to building services from within the service space need not be considered a storey if it conforms to Articles 3.2.5.14. and 3.3.1.24., and Sentences 3.2.4.18.(10), Sentence 3.2.7.3.(2), Sentence 3.3.1.3.(7), Sentence 3.4.2.4.(3) and 3.4.4.4.(9). (See Note A-3.2.1.1.(8).) | obc2019_divb | Div B | 3.2.1.1.(9) | 3.2.1.1. Exceptions in Determining Building Height | A service space in which facilities are included to permit a person to enter and to undertake maintenance and other operations pertaining to building services from within the service space need not be considered a storey if it conforms to Articles 3.2.5.15. and 3.3.1.23. and Sentences 3.2.4.20.(12), 3.2.7.3.(2), 3.3.1.3.(7), 3.4.2.4.(3) and 3.4.4.4.(9). (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.1.2.(1) | Storage Garage Considered as a Separate Building | A basement used primarily as a storage garage is permitted to be considered as a separate building for the purposes of part 3. and Sentences 3.2.5.12.(2) and 3.2.5.12.(3), provided the floor and roof assemblies above the basement and the exterior walls of the basement above the adjoining ground level are constructed as fire separations of noncombustible construction having a fire-resistance rating not less than 2 h and protected in conformance with Sentence 3.1.10.2.(4), except as permitted by Sentence 3.2.1.2.(2). (See Notes A-3.1.10.2.(4) and A-3.2.5.12.(2).) | obc2019_divb | Div B | 3.2.1.2.(1) | 3.2.1.2. Storage Garage Considered as a Separate Building | A basement used primarily as a storage garage is permitted to be considered as a separate building for the purposes of Subsection 3.2.2. and Sentences 3.2.5.13.(2) and (3), provided the floor and roof assemblies above the basement and, except as permitted by Sentence (2), the exterior walls of the basement above the adjoining ground level are constructed as fire separations of, masonry or concrete having a fire-resistance rating not less than 2 h, or noncombustible construction having a fire-resistance rating of not less than 2 h, where the building conforms to Clauses 3.1.10.2.(4)(a) and (c) to (e). |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.1.2.(2) | Storage Garage Considered as a Separate Building | The exterior wall of a basement that is required to be a fire separation with a fire-resistance rating in accordance with Sentence 3.2.1.2.(1) is permitted to be penetrated by openings that are not protected by closures provided (a) the storage garage is sprinklered throughout, (b) every opening in the exterior wall is separated from storeys above the opening by a projection of the floor or roof assembly above the basement, extending not less than (i) 1 m beyond the exterior face of the storage garage if the upper storeys are required to be of noncombustible construction, or (ii) 2 m beyond the exterior face of the storage garage if the upper storeys are permitted to be of combustible construction, or (c) the exterior walls of any storeys located above the floor or roof assembly referred to in Sentence 3.2.1.2.(1) are recessed behind the outer edge of the assembly by not less than (i) 1 m if the upper storeys are required to be of noncombustible construction, or (ii) 2 m if the upper storeys are permitted to be of combustible construction. | obc2019_divb | Div B | 3.2.1.2.(2) | 3.2.1.2. Storage Garage Considered as a Separate Building | The exterior wall of a basement that is required to be a fire separation with a fire-resistance rating in accordance with Sentence (1) is permitted to be penetrated by openings that are not protected by closures provided, (a) the storage garage is sprinklered, (b) every opening in the exterior wall is separated from storeys above the opening by a projection of the floor or roof assembly above the basement, extending not less than, (i) 1 m beyond the exterior face of the storage garage if the upper storeys are required to be of noncombustible construction, or (ii) 2 m beyond the exterior face of the storage garage if the upper storeys are permitted to be of combustible construction, or (c) the exterior walls of any storeys located above the floor or roof assembly referred to in Sentence (1) are recessed behind the outer edge of the assembly by not less than, (i) 1 m if the upper storeys are required to be of noncombustible construction, or (ii) 2 m if the upper storeys are permitted to be of combustible construction. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.1.2.(3) | Storage Garage Considered as a Separate Building | The floor or roof assembly projection referred to in Sentence 3.2.1.2.(2) shall have a fire-resistance rating not less than 2 h and shall have no openings within the projection. | obc2019_divb | Div B | 3.2.1.2.(3) | 3.2.1.2. Storage Garage Considered as a Separate Building | The floor or roof assembly projection referred to in Clause (2)(b) shall have a fire-resistance rating not less than 2 h and shall have no openings within the projection |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.1.3.(1) | Roof Considered as a Wall | For the purposes of this Section any part of a roof that is pitched at an angle of 60° or more to the horizontal and is adjacent to a space intended for occupancy within a building shall be considered as part of an exterior wall of the building. | obc2019_divb | Div B | 3.2.1.3.(1) | 3.2.1.3. Roof Considered as a Wall | For the purposes of this Section any part of a roof that is pitched at an angle of 60? or more to the horizontal and is adjacent to a space intended for occupancy within a building shall be considered as part of an exterior wall of the building. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.1.4.(1) | Floor Assembly over Basement | Except as permitted by Sentence 3.2.2.47.(3), Sentence 3.2.2.48.(3), Sentence 3.2.2.49.(3), Sentence 3.2.2.51.(3), Sentence 3.2.2.52.(3), Sentence 3.2.2.53.(3) or 3.2.2.54.(3), a floor assembly immediately above a basement shall be constructed as a fire separation having a fire-resistance rating conforming to the requirements of Articles 3.2.2.20. to 3.2.2.90. for a floor assembly, but not less than 45 min. | obc2019_divb | Div B | 3.2.1.4.(1) | 3.2.1.4. Floor Assembly Over Basement | Except as permitted by Sentence 3.2.2.42.(3), 3.2.2.43.(3), 3.2.2.44.(3), 3.2.2.45.(3), 3.2.2.46.(3), 3.2.2.47.(3) or 3.2.2.48.(3), a floor assembly immediately above a basement shall be constructed as a fire separation having a fire-resistance rating conforming to the requirements of Articles 3.2.2.20. to 3.2.2.83. for a floor assembly, but not less than 45 min. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.1.4.(2) | Floor Assembly over Basement | All loadbearing walls, columns and arches supporting a floor assembly immediately above a basement shall have a fire-resistance rating not less than that required by Sentence 3.2.1.4.(1) for the floor assembly. | obc2019_divb | Div B | 3.2.1.4.(2) | 3.2.1.4. Floor Assembly Over Basement | All loadbearing walls, columns and arches supporting a floor assembly immediately above a basement shall have a fire-resistance rating not less than that required by Sentence (1) for the floor assembly. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.1.5.(1) | Fire Containment in Basements | Except as permitted by Sentences 3.2.1.5.(2) and 3.2.2.15.(3), in a building in which an automatic sprinkler system is not required to be installed by Article 3.2.2.18., every basement shall (a) be sprinklered throughout, or (b) be subdivided into fire compartments not more than 600 m2 in area by a fire separation having a fire-resistance rating not less than that required for the floor assembly immediately above the basement. | obc2019_divb | Div B | 3.2.1.5.(1) | 3.2.1.5. Fire Containment in Basements | Except as permitted by Sentences (2) and 3.2.2.15.(3), in a building in which an automatic sprinkler system is not required to be installed by Articles 3.2.2.20. to 3.2.2.83., every basement shall, (a) be sprinklered, or (b) be subdivided into fire compartments not more than 600 m2 in area by a fire separation having a fire-resistance rating not less than that required for the floor assembly immediately above the basement. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.1.5.(2) | Fire Containment in Basements | An open-air storey need not conform to Sentence 3.2.1.5.(1). | obc2019_divb | Div B | 3.2.1.5.(2) | 3.2.1.5. Fire Containment in Basements | An open-air storey need not conform to Sentence (1). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.1.6.(1) | Mezzanines | The floor assembly of a mezzanine that is required to be considered as a storey in calculating the building height shall be constructed in conformance with the fire separation requirements for floor assemblies stated in Articles 3.2.2.20. to 3.2.2.90. | obc2019_divb | Div B | 3.2.1.6.(1) | 3.2.1.6. Mezzanines | The floor assembly of a mezzanine that is required to be considered as a storey in calculating building height shall be constructed in conformance with the fire separation requirements for floor assemblies in Articles 3.2.2.20. to 3.2.2.83. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.1.(1) | Application | Except as permitted by Article 3.2.2.3., a building shall be constructed in conformance with this Subsection to prevent fire spread and collapse caused by the effects of fire. (See part 3. for fire separations between major occupancies.) | obc2019_divb | Div B | 3.2.2.1.(1) | 3.2.2.1. Application | Except as permitted by Article 3.2.2.3., a building shall be constructed in conformance with this Subsection to prevent fire spread and collapse caused by the effects of fire. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.10.(1) | Streets | Every building shall face a street located in conformance with the requirements of Articles 3.2.5.4.and 3.2.5.5. for access routes. | obc2019_divb | Div B | 3.2.2.10.(1) | 3.2.2.10. Streets | Every building shall face a street located in conformance with the requirements of Articles 3.2.5.4 and 3.2.5.5 for access routes. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.10.(2) | Streets | For the purposes of Subsections 3. and 3. an access route conforming to part 3. is permitted to be considered as a street. | obc2019_divb | Div B | 3.2.2.10.(2) | 3.2.2.10. Streets | For the purposes of Subsections 3.2.2. and 3.2.5. an access route conforming to Subsection 3.2.5. is permitted to be considered as a street. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.10.(3) | Streets | A building conforming to Article 3.2.2.50. or 3.2.2.58. is considered to face 1 street where not less than 25% of the building perimeter is located within 15 m of a street or streets. | obc2019_divb | Div B | 3.2.2.10.(3) | 3.2.2.10. Streets | A building within the scope of Article 3.2.2.43A. or 3.2.2.50A. is considered to face one street provided not less than 10% of the building perimeter is located within 15 m of a street or streets. |  | Common Sentence | Yes | Mid-rise Wood
2015 | ON | NBC | Div B | 3.2.2.10.(4) | Streets | A building is considered to face 2 streets provided not less than 50% of the building perimeter is located within 15 m of the street or streets. | obc2019_divb | Div B | 3.2.2.10.(4) | 3.2.2.10. Streets | A building is considered to face two streets provided not less than 50% of the building perimeter is located within 15 m of a street or streets. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.10.(5) | Streets | A building is considered to face 3 streets provided not less than 75% of the building perimeter is located within 15 m of the street or streets. | obc2019_divb | Div B | 3.2.2.10.(5) | 3.2.2.10. Streets | A building is considered to face three streets provided not less than 75% of the building perimeter is located within 15 m of a street or streets. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.10.(6) | Streets | Enclosed spaces, tunnels, bridges and similar structures, even though used for vehicular or pedestrian traffic, are not considered as streets for the purpose of this Part. | obc2019_divb | Div B | 3.2.2.10.(6) | 3.2.2.10. Streets | Enclosed spaces, tunnels, bridges and similar structures, even though used for vehicular or pedestrian traffic, are not considered as streets for the purpose of this Part. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.11.(1) | Exterior Balconies | An exterior balcony shall be constructed in accordance with the type of construction required by Articles 3.2.2.20. to 3.2.2.90., as applicable to the occupancy classification of the building. | obc2019_divb | Div B | 3.2.2.11.(1) | 3.2.2.11. Exterior Balconies | An exterior balcony shall be constructed in accordance with the type of construction required by Articles 3.2.2.20. to 3.2.2.83., as applicable to the occupancy classification of the building. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.12.(1) | Exterior Passageways | An elevated exterior passageway used as part of a means of egress shall conform to the requirements of Articles 3.2.2.20. to 3.2.2.90. for mezzanines. | obc2019_divb | Div B | 3.2.2.12.(1) | 3.2.2.12. Exterior Passageways | An elevated exterior passageway used as part of a means of egress shall conform to the requirements of Articles 3.2.2.20. to 3.2.2.83. for mezzanines. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.13.(1) | Occupancy on Roof | A portion of a roof that supports an occupancy shall be constructed in conformance with the fire separation requirements of Articles 3.2.2.20. to 3.2.2.90. for floor assemblies, and not the fire-resistance rating for roof assemblies. | obc2019_divb | Div B | 3.2.2.13.(1) | 3.2.2.13. Occupancy on Roof | A portion of a roof that supports an occupancy shall be constructed in conformance with the fire separation requirements of Articles 3.2.2.20. to 3.2.2.83. for floor assemblies. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.14.(1) | Roof-Top Enclosures | A roof-top enclosure for elevator machinery or for a service room shall be constructed in accordance with the type of construction required by Articles 3.2.2.20. to 3.2.2.90. | obc2019_divb | Div B | 3.2.2.14.(1) | 3.2.2.14. Rooftop Enclosures | A rooftop enclosure for elevator machinery or for a service room shall be constructed in accordance with the type of construction required by Articles 3.2.2.20. to 3.2.2.83. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.14.(2) | Roof-Top Enclosures | A roof-top enclosure for elevator machinery or for a service room, not more than one storey high, is not required to have a fire-resistance rating. | obc2019_divb | Div B | 3.2.2.14.(2) | 3.2.2.14. Rooftop Enclosures | A rooftop enclosure for elevator machinery or for a service room, not more than 1 storey high, is not required to have a fire-resistance rating. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.14.(3) | Roof-Top Enclosures | A roof-top enclosure for a stairway shall be constructed in accordance with the type of construction required by Articles 3.2.2.20. to 3.2.2.90. | obc2019_divb | Div B | 3.2.2.14.(3) | 3.2.2.14. Rooftop Enclosures | A rooftop enclosure for a stairway shall be constructed in accordance with the type of construction required by Articles 3.2.2.20. to 3.2.2.83. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.14.(4) | Roof-Top Enclosures | A roof-top enclosure for a stairway need not have a fire-resistance rating nor be constructed as a fire separation. | obc2019_divb | Div B | 3.2.2.14.(4) | 3.2.2.14. Rooftop Enclosures | A rooftop enclosure for a stairway need not have a fire-resistance rating nor be constructed as a fire separation. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.15.(1) | Storeys below Ground | If a building is erected entirely below the adjoining finished ground level and does not extend more than one storey below that ground level, the minimum precautions against fire spread and collapse shall be the same as are required for basements under a building of 1 storey in building height having the same occupancy and building area. | obc2019_divb | Div B | 3.2.2.15.(1) | 3.2.2.15. Storeys Below Ground | If a building is erected entirely below the adjoining finished ground level and does not extend more than 1 storey below that ground level, the minimum precautions against fire spread and collapse shall be the same as are required for basements under a building of 1 storey in building height having the same occupancy and building area. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.15.(2) | Storeys below Ground | If any portion of a building is erected entirely below the adjoining finished ground level and extends more than one storey below that ground level, the following minimum precautions against fire spread and collapse shall be taken: (a) except as permitted by Sentence 3.2.2.15.(3), the basements shall be sprinklered throughout, (b) a floor assembly below the ground level shall be constructed as a fire separation with a fire-resistance rating not less than (i) 3 h if the basements are used as Group E or Group F, Division 1 or 2 occupancies, or (ii) 2 h if the basements are not used as Group E or Group F, Division 1 or 2 occupancies, and (c) all loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the construction that they support. | obc2019_divb | Div B | 3.2.2.15.(2) | 3.2.2.15. Storeys Below Ground | If any portion of a building is erected entirely below the adjoining finished ground level and extends more than 1 storey below that ground level, the following minimum precautions against fire spread and collapse shall be taken: (a) except as permitted by Sentence (3), the basements shall be sprinklered, (b) a floor assembly below the ground level shall be constructed as a fire separation with a fire-resistance rating not less than, (i) 3 h if the basements are intended for use as Group E or Group F, Division 1 or 2 occupancies, or (ii) 2 h if the basements are not intended for use as Group E or Group F, Division 1 or 2 occupancies, and (c) all loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the construction that they support. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.15.(2) | Storeys below Ground | If any portion of a building is erected entirely below the adjoining finished ground level and extends more than one storey below that ground level, the following minimum precautions against fire spread and collapse shall be taken: (a) except as permitted by Sentence (3), the basements shall be sprinklered throughout, (b) a floor assembly below the ground level shall be constructed as a fire separation with a fire-resistance rating not less than (i) 3 h if the basements are used as Group E or Group F, Division 1 or 2 occupancies, or (ii) 2 h if the basements are not used as Group E or Group F, Division 1 or 2 occupancies, and (c) all loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the construction that they support. | obc2019_divb | Div B | 3.2.2.15.(2) | 3.2.2.15. Storeys Below Ground | If any portion of a building is erected entirely below the adjoining finished ground level and extends more than 1 storey below that ground level, the following minimum precautions against fire spread and collapse shall be taken: (a) except as permitted by Sentence (3), the basements shall be sprinklered, (b) a floor assembly below the ground level shall be constructed as a fire separation with a fire-resistance rating not less than, (i) 3 h if the basements are intended for use as Group E or Group F, Division 1 or 2 occupancies, or (ii) 2 h if the basements are not intended for use as Group E or Group F, Division 1 or 2 occupancies, and (c) all loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the construction that they support. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.15.(3) | Storeys below Ground | If the first storey of a building is not required to be sprinklered, sprinklers are not required in the storey immediately below the first storey provided the storey below contains only residential occupancies, and has at least one unobstructed access opening conforming to Sentence 3.2.5.1.(2) installed on that storey for each 15 m of wall length in at least one wall required by this Subsection to face a street. | obc2019_divb | Div B | 3.2.2.15.(3) | 3.2.2.15. Storeys Below Ground | If the first storey of a building is not required to be sprinklered, sprinklers are not required in the storey immediately below the first storey, provided the storey below, contains only residential occupancies, and has at least one unobstructed access opening conforming to Sentence 3.2.5.1.(2) installed on that storey for each 15 m of wall length in at least one wall required by this Subsection to face a street. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.16.(1) | Heavy Timber Roof Permitted | Unless otherwise permitted by Articles 3.2.2.20. to 3.2.2.90., a roof assembly in a building up to 2 storeys in building height is permitted to be of heavy timber construction regardless of building area or type of construction required, provided the building is sprinklered throughout. | obc2019_divb | Div B | 3.2.2.16.(1) | 3.2.2.16. Heavy Timber Roof Permitted | Unless otherwise permitted by Articles 3.2.2.20. to 3.2.2.83., a roof assembly in a building up to 2 storeys in building height is permitted to be of heavy timber construction regardless of building area or type of construction required, provided the building is sprinklered. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.16.(2) | Heavy Timber Roof Permitted | If Sentence 3.2.2.16.(1) permits a roof assembly to be of heavy timber construction, structural members in the storey immediately below the roof assembly are permitted to be of heavy timber construction. | obc2019_divb | Div B | 3.2.2.16.(2) | 3.2.2.16. Heavy Timber Roof Permitted | If Sentence (1) permits a roof assembly to be of heavy timber construction, structural members in the storey immediately below the roof assembly are permitted to be of heavy timber construction. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.18.(1) | Automatic Sprinkler System Required | Except as permitted by Sentence (2), an automatic sprinkler system conforming to the requirements of Articles 3.2.4.7., 3.2.4.8., 3.2.4.9.and 3.2.5.12. shall be installed throughout a building regulated by one or more of Articles 3.2.2.20., 3.2.2.21., 3.2.2.22., 3.2.2.23., 3.2.2.24., 3.2.2.26., 3.2.2.27., 3.2.2.29., 3.2.2.31., 3.2.2.33., 3.2.2.36., 3.2.2.37., 3.2.2.38., 3.2.2.39., 3.2.2.40., 3.2.2.41., 3.2.2.42., 3.2.2.43., 3.2.2.44., 3.2.2.45., 3.2.2.46., 3.2.2.47., 3.2.2.48., 3.2.2.51., 3.2.2.54., 3.2.2.55., 3.2.2.57., 3.2.2.59., 3.2.2.61., 3.2.2.63., 3.2.2.64., 3.2.2.65., 3.2.2.67., 3.2.2.69., 3.2.2.70., 3.2.2.71., 3.2.2.72., 3.2.2.74., 3.2.2.75., 3.2.2.77.,3.2.2.79.,3.2.2.80.,3.2.2.82.,3.2.2.84.,3.2.2.86.and3.2.2.88. | obc2019_divb | Div B | 3.2.2.18.(1) | 3.2.2.18. Automatic Sprinkler System Required | If an automatic sprinkler system is required by Articles 3.2.2.20. to 3.2.2.83., the system shall conform to the requirements of Articles 3.2.4.8. to 3.2.4.10. and 3.2.5.13. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.19.(1) | Buildings Containing Impeded Egress Zones | A building containing an impeded egress zone and conforming to the appropriate requirements of Articles 3.2.2.20. to 3.2.2.90. is not required to conform to the requirements of Articles 3.2.2.36. and 3.2.2.37. for a Group B, Division 1 major occupancy provided (a) the building is sprinklered throughout, (b) it is not more than 1 storey in building height, (c) it does not include (i) a contained use area, (ii) sleeping accommodation, (iii) a high-hazard industrial occupancy, or (iv) a mercantile occupancy, (d) the building area is not more than 6400 m2 if the building includes a medium-hazard industrial occupancy, (e) the impeded egress zone does not extend beyond the boundaries of the fire compartment in which it is located, and (f) the occupant load of the impeded egress zone is not more than 100. | obc2019_divb | Div B | 3.2.2.19.(1) | 3.2.2.19. Buildings Containing Impeded Egress Zones | A building containing an impeded egress zone and conforming to the appropriate requirements of Articles 3.2.2.20. to 3.2.2.83. is not required to conform to the requirements of Articles 3.2.2.36. and 3.2.2.37. for a Group B, Division 1 major occupancy provided, (a) the building is sprinklered, (b) it is not more than 1 storey in building height, (c) it does not include, (i) a contained use area, (ii) sleeping accommodation, (iii) a high hazard industrial occupancy, or (iv) a mercantile occupancy, (d) the building area is not more than 6 400 m2 if the building includes a medium hazard industrial occupancy, (e) the impeded egress zone does not extend beyond the boundaries of the fire compartment in which it is located, and (f) the occupant load of the impeded egress zone is not more than 100. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.2.(1) | Special and Unusual Structures | A structure that cannot be identified with the characteristics of a building in Articles 3.2.2.20. to 3.2.2.90. shall be protected against fire spread and collapse in conformance with good fire protection engineering practice. (See Note A-3.2.2.2.(1).) (See also Notes A-3 and A-3.2.5.12.(1).) | obc2019_divb | Div B | 3.2.2.2.(1) | 3.2.2.2. Special and Unusual Structures | A structure that cannot be identified with the characteristics of a building in Articles 3.2.2.20. to 3.2.2.83. shall be protected against fire spread and collapse in conformance with good fire protection engineering practice. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.20.(1) | Group A, Division 1, Any Height, Any Area, Sprinklered | Except as permitted by Articles 3.2.2.21. and 3.2.2.22., a building classified as Group A, Division 1 shall conform to Sentence 3.2.2.20.(2). | obc2019_divb | Div B | 3.2.2.20.(1) | 3.2.2.20. Group A, Division 1, Any Height, Any Area, Sprinklered | Except as permitted by Articles 3.2.2.21. and 3.2.2.22., a building classified as Group A, Division 1 shall conform to Sentence (2). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.20.(2) | Group A, Division 1, Any Height, Any Area, Sprinklered | Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building shall be sprinklered throughout, (b) floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h, (c) mezzanines shall have a fire-resistance rating not less than 1 h, and (d) loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. | obc2019_divb | Div B | 3.2.2.20.(2) | 3.2.2.20. Group A, Division 1, Any Height, Any Area, Sprinklered | Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and, (a) except as permitted by Sentence 3.2.2.7.(1), the building shall be sprinklered, (b) floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h, (c) mezzanines shall have a fire-resistance rating not less than 1 h, and (d) loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.21.(1) | Group A, Division 1, One Storey, Limited Area, Sprinklered | A building classified as Group A, Division 1 is permitted to conform to Sentence 3.2.2.21.(2) provided (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout, (b) it is not more than 1 storey in building height, (c) it has less than 40% of the area of the building as 2 storeys for the purpose of (i) development of productions, including preparation of scenery and costumes and rehearsal of performers, (ii) organization of performers, scenery and sound equipment, (iii) preparation by performers for a performance, (iv) managerial functions, or (v) toilets, rest rooms and similar public facilities, (d) it has no occupancy above or below the auditorium other than one which serves it or is dependent on it, (e) it is not more than 600 m2 in building area, and (f) the occupant load is not more than 600. | obc2019_divb | Div B | 3.2.2.21.(1) | 3.2.2.21. Group A, Division 1, 1 Storey, Limited Area | A building classified as Group A, Division 1 is permitted to conform to Sentence (2) provided, (a) it is not more than 1 storey in building height, (b) it has less than 40% of the area of the building as 2 storeys for the purpose of, (i) development of productions including preparation of scenery and costumes and rehearsal of performers, (ii) organization of performers, scenery and sound equipment, (iii) preparation by performers for a performance, (iv) managerial functions, or (v) toilets, rest rooms and similar public facilities, (c) it has no occupancy above or below the auditorium other than one that serves it or is dependent on it, (d) it is not more than 600 m2 in building area, and (e) the occupant load is not more than 600. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.21.(2) | Group A, Division 1, One Storey, Limited Area, Sprinklered | The building referred to in Sentence 3.2.2.21.(1) is permitted to be of heavy timber construction or noncombustible construction used singly or in combination, and floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min, or of heavy timber construction, and loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly, or be of heavy timber construction. | obc2019_divb | Div B | 3.2.2.21.(2) | 3.2.2.21. Group A, Division 1, 1 Storey, Limited Area | The building referred to in Sentence (1) is permitted to be of heavy timber construction or noncombustible construction used singly or in combination, and, floor assemblies shall be fire separations, with a fire-resistance rating not less than 45 min, or of heavy timber construction, and loadbearing walls, columns and arches shall, have a fire-resistance rating not less than that required for the supported assembly, or be of heavy timber construction. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.22.(1) | Group A, Division 1, One Storey, Sprinklered | A building classified as Group A, Division 1 is permitted to conform to Sentence 3.2.2.22.(2) provided (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout, (b) it is not more than 1 storey in building height, (c) no part of an auditorium floor is more than 5 m above or below grade, (d) no occupancy is above or below the auditorium other than one which serves it or is dependent on it, and (e) the occupant load of the auditorium floor is not more than 300. | obc2019_divb | Div B | 3.2.2.22.(1) | 3.2.2.22. Group A, Division 1, 1 Storey | A building classified as Group A, Division 1 is permitted to conform to Sentence (2) provided, (a) it is not more than 1 storey in building height, (b) no part of an auditorium floor is more than 5 m above or below grade, (c) no occupancy is above or below the auditorium other than one that serves it or is dependent on it, and (d) the occupant load of the auditorium floor is not more than 300. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.22.(2) | Group A, Division 1, One Storey, Sprinklered | The building referred to in Sentence 3.2.2.22.(1) is permitted to be of combustible construction or noncombustible construction used singly, or in combination, and (a) floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min, (b) mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min,(c) loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall (i) have a fire-resistance rating not less than 45 min, or (ii) be of noncombustible construction, and (d) loadbearing walls, columns and arches supporting a fire separation shall have a fire-resistance rating not less than that required for the fire separation. | obc2019_divb | Div B | 3.2.2.22.(2) | 3.2.2.22. Group A, Division 1, 1 Storey | The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and, (a) floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min, (b) mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, (c) roof assemblies shall have, if of combustible construction, a fire-resistance rating not less than 45 min, and (d) loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall, (i) have a fire-resistance rating not less than 45 min, or (ii) be of noncombustible construction, and (e) loadbearing walls, columns and arches supporting a fire separation shall have a fire-resistance rating not less than that required for the fire separation. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.23.(1) | Group A, Division 2, Any Height, Any Area, Sprinklered | Except as permitted by Sentences 3.2.2.7.(3) and (4) and Articles 3.2.2.24. to 3.2.2.28.,a building classified as Group A, Division 2 shall conform to Sentence (2) | obc2019_divb | Div B | 3.2.2.23.(1) | 3.2.2.23. Group A, Division 2, Any Height, Any Area, Sprinklered | Except as permitted by Articles 3.2.2.24. to 3.2.2.28., a building classified as Group A, Division 2 shall conform to Sentence (2). |  | Common Sentence | Yes | Mid-rise Wood
2015 | ON | NBC | Div B | 3.2.2.23.(2) | Group A, Division 2, Any Height, Any Area, Sprinklered | Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building shall be sprinklered throughout, (b) floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h, (c) mezzanines shall have a fire-resistance rating not less than 1 h, and (d) loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. | obc2019_divb | Div B | 3.2.2.23.(2) | 3.2.2.23. Group A, Division 2, Any Height, Any Area, Sprinklered | Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and, (a) except as permitted by Sentence 3.2.2.7.(1), the building shall be sprinklered, (b) floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h, (c) mezzanines shall have a fire-resistance rating not less 1 h, and (d) loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.24.(1) | Group A, Division 2, up to 6 Storeys, Any Area, Sprinklered | Except as permitted by Sentences 3.2.2.7.(3) and 3.2.2.7.(4), a building classified as Group A, Division 2, that is not limited by building area, is permitted to conform to Sentence 3.2.2.24.(2), provided (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout, and (b) it is not more than 6 storeys in building height. | obc2019_divb | Div B | 3.2.2.24.(1) | 3.2.2.24. Group A, Division 2, up to 6 Storeys, Any Area, Sprinklered | A building classified as Group A, Division 2, that is not limited by building area, is permitted to conform to Sentence (2) provided, (a) except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered, and (b) it is not more than 6 storeys in building height. |  | Common Sentence | Yes | Mid-rise Wood
2015 | ON | NBC | Div B | 3.2.2.24.(2) | 3.2.2.24. Group A, Division 2, up to 6 Storeys, Any Area, Sprinklered | Except as permitted by Article 3.2.2.16., the building referred to in Sentence 3.2.2.75.(1) shall be of noncombustible construction, and floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, mezzanines shall have a fire-resistance rating not less than 1 h, and loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. | obc2019_divb | Div B | 3.2.2.24.(2) | 3.2.2.24. Group A, Division 2, up to 6 Storeys, Any Area, Sprinklered | Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and, (a) floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, (b) mezzanines shall have a fire-resistance rating not less than 1 h, and (c) all loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.25.(1) | Group A, Division 2, up to 2 Storeys | A building classified as Group A, Division 2 is permitted to conform to Sentence 3.2.2.25.(2) provided it is not more than 2 storeys in building height, and it has a building area not more than the value in Table 3.2.2.25. | obc2019_divb | Div B | 3.2.2.25.(1) | 3.2.2.25. Group A, Division 2, up to 2 Storeys | A building classified as Group A, Division 2 is permitted to conform to Sentence (2) provided, it is not more than 2 storeys in building height, and it has a building area not more than the value in Table 3.2.2.25. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.25.(2) | Group A, Division 2, up to 2 Storeys | The building referred to in Sentence 3.2.2.32.(1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, roof assemblies shall have, if of combustible construction, a fire-resistance rating not less than 45 min, except that the fire-resistance rating is permitted to be waived provided the roof assembly is constructed as a fire-retardant-treated wood roof system conforming to Article 3.1.14.1., and the building area is not more than 1?200 m2 if facing one street, 1?500 m2 if facing 2 streets , or 1?800 m2 if facing 3 streets , and loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall have a fire-resistance rating not less than 45 min, or be of noncombustible construction. | obc2019_divb | Div B | 3.2.2.25.(2) | 3.2.2.25. Group A, Division 2, up to 2 Storeys | The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and, floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, mezzanines shall have, if of combustible construction, a fire-resistance rating not less 45 min, roof assemblies shall have, if of combustible construction, a fire-resistance rating not less than 45 min, except that in a building not more than 1 storey in building height, the fire-resistance rating is permitted to be waived provided the roof assembly is constructed as a fire-retardant treated wood roof system conforming to Article 3.1.14.1., and the building area is not more than, 800 m2 if facing one street, 1 000 m2 if facing two streets, or 1 200 m2 if facing three streets, and loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall, have a fire-resistance rating not less than 45 min, or be of noncombustible construction. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.26.(1) | Group A, Division 2, up to 2 Storeys, Increased Area, Sprinklered | A building classified as Group A, Division 2 is permitted to conform to Sentence (2) provided (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout, (b) it is not more than 2 storeys in building height, and (c) it has a building area not more than (i) 4 800 m2 if 1 storey in building height, or (ii) 2 400 m2 if 2 storeys in building height. | obc2019_divb | Div B | 3.2.2.26.(1) | 3.2.2.26. Group A, Division 2, up to 2 Storeys, Increased Area, | A building classified as Group A, Division 2 is permitted to conform to Sentence (2) provided, except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered, it is not more than 2 storeys in building height, and it has a building area not more than, 4 800 m2 if 1 storey in building height, or 2 400 m2 if 2 storeys in building height. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.26.(2) | Group A, Division 2, up to 2 Storeys, Increased Area, Sprinklered | The building referred to in Sentence 3.2.2.26.(1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, and loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall have a fire-resistance rating not less than 45 min, or be of noncombustible construction. | obc2019_divb | Div B | 3.2.2.26.(2) | 3.2.2.26. Group A, Division 2, up to 2 Storeys, Increased Area, | The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and, floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, mezzanines shall have, if of combustible construction, a fire-resistance rating not less 45 min, and loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall, have a fire-resistance rating not less than 45 min, or be of noncombustible construction. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.27.(1) | Group A, Division 2, up to 2 Storeys, Sprinklered | A building classified as Group A, Division 2 is permitted to be of combustible construction or noncombustible construction, used singly or in combination, provided (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout, (b) it is not more than 2 storeys in building height, and (c) it has a building area not more than (i) 2 400 m2 if 1 storey in building height with no basement, (ii) 1 200 m2 if 1 storey in building height, or (iii) 600 m2 if 2 storeys in building height. | obc2019_divb | Div B | 3.2.2.27.(1) | 3.2.2.27. Group A, Division 2, up to 2 Storeys, Sprinklered | A building classified as Group A, Division 2 is permitted to be of combustible construction or noncombustible construction used singly or in combination, provided, except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered, it is not more than 2 storeys in building height, and it has a building area not more than, 2 400 m2 if 1 storey in building height with no basement, 1 200 m2 if 1 storey in building height, or 600 m2 if 2 storeys in building height. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.28.(1) | Group A, Division 2, One Storey | A building classified as Group A, Division 2 is permitted to be of combustible construction or noncombustible construction, used singly or in combination, provided it is not more than 1 storey in building height, and except as permitted by Sentence 3.2.2.28.(2), it has a building area not more than 400 m2 if facing one street, 500 m2 if facing 2 streets, or 600 m2 if facing 3 streets. | obc2019_divb | Div B | 3.2.2.28.(1) | 3.2.2.28. Group A, Division 2, 1 Storey | A building classified as Group A, Division 2 is permitted to be of combustible construction or noncombustible construction used singly or in combination, provided, it is not more than 1 storey in building height, and except as permitted by Sentence (2), it has a building area not more than, 400 m2 if facing one street, 500 m2 if facing two streets, or 600 m2 if facing three streets. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.28.(2) | Group A, Division 2, One Storey | In a building referred to in Sentence 3.2.2.28.(1) without a basement, the building area limits of Sentence 3.2.2.28.(1) are permitted to be doubled provided a fire separation with a fire-resistance rating not less than 1 h is used to separate the building into fire compartments, each one of which does not exceed the limits of Clause 3.2.2.28.(1)(b). | obc2019_divb | Div B | 3.2.2.28.(2) | 3.2.2.28. Group A, Division 2, 1 Storey | In a building referred to in Sentence (1) without a basement, the building area limits of Sentence (1) are permitted to be doubled provided a fire separation with a fire-resistance rating not less than 1 h is used to separate the building into fire compartments, each one of which does not exceed the area limits of Clause (1)(b). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.29.(1) | Group A, Division 3, Any Height, Any Area, Sprinklered | Except as permitted by Articles 3.2.2.30. to 3.2.2.34., a building classified as Group A, Division 3 shall conform to Sentence 3.2.2.29.(2). | obc2019_divb | Div B | 3.2.2.29.(1) | 3.2.2.29. Group A, Division 3, Any Height, Any Area | Except as permitted by Articles 3.2.2.30. to 3.2.2.34., a building classified as Group A, Division 3 shall conform to Sentences (2) and (3). |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.29.(2) | Group A, Division 3, Any Height, Any Area, Sprinklered | Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building shall be sprinklered throughout, (b) floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h, (c) mezzanines shall have a fire-resistance rating not less than 1 h, and (d) loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. | obc2019_divb | Div B | 3.2.2.29.(2) | 3.2.2.29. Group A, Division 3, Any Height, Any Area | Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and, except as permitted by Sentence 3.2.2.7.(1), the building shall be sprinklered if it is regulated by Subsection 3.2.6., floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h, mezzanines shall have a fire-resistance rating not less than 1 h, if the building is not sprinklered, roof assemblies shall have a fire-resistance rating not less than 1 h, and loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.3.(1) | Exceptions to Structural Fire Protection | Fire protection is not required for steel lintels above openings not more than 2 m wide in loadbearing walls and not more than 3 m wide in non-loadbearing walls, steel lintels above openings more than 2 m wide in loadbearing walls and more than 3 m wide in non-loadbearing walls provided the lintels are supported at intervals of not more than 2 m by structural members with the required fire-resistance rating, the bottom flanges of shelf angles and plates that are not a part of the structural frame, steel members for framework around elevator hoistway doorways, steel for the support of elevator and dumbwaiter guides, counterweights and other similar equipment, that are entirely enclosed in a hoistway and are not a part of the structural frame of the building, steel members of stairways and escalators that are not a part of the structural frame of a building, steel members of porches, exterior balconies, exterior stairways, fire escapes, cornices, marquees and other similar appurtenances, provided they are outside an exterior wall of a building, and loadbearing steel or concrete members wholly or partly outside a building face in a building not more than 4 storeys in building height and classified as Group A, B, C, D or F, Division 3 major occupancy provided the members are not less than 1 m away from any unprotected opening in an exterior wall, or shielded from heat radiation in the event of a fire within the building by construction that will provide the same degree of protection that would be necessary if the member was located inside the building, with the protection extending on either side of the member a distance equal to the projection of the member from the face of the wall. (See also Article 3.2.3.9.) | obc2019_divb | Div B | 3.2.2.3.(1) | 3.2.2.3. Exceptions to Structural Fire Protection | Fire protection is not required for, steel lintels above openings not more than 2 m wide in loadbearing walls and not more than 3 m wide in non-loadbearing walls, steel lintels above openings more than 2 m wide in loadbearing walls and more than 3 m wide in non-loadbearing walls, provided the lintels are supported at intervals of not more than 2 m by structural members with the required fire-resistance rating, the bottom flanges of shelf angles and plates that are not a part of the structural frame, steel members for framework around elevator hoistway doorways, steel for the support of elevator and dumbwaiter guides, counterweights and other similar equipment, that are entirely enclosed in a hoistway and are not a part of the structural frame of the building, steel members of stairways and escalators that are not a part of the structural frame of a building, steel members of porches, exterior balconies, exterior stairways, fire escapes, cornices, marquees and other similar appurtenances, provided they are outside an exterior wall of a building, and loadbearing steel or concrete members wholly or partly outside a building face in a building not more than 4 storeys in building height and classified as Group A, B, C, D or F, Division 3 major occupancy provided the members are, not less than 1 m away from any unprotected opening in an exterior wall, or shielded from heat radiation in the event of a fire within the building by construction that will provide the same degree of protection that would be necessary if the member was located inside the building, with the protection extending on either side of the member a distance equal to the projection of the member from the face of the wall. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.30.(1) | Group A, Division 3, up to 2 Storeys | A building classified as Group A, Division 3 is permitted to conform to Sentence 3.2.2.30.(2) provided it is not more than 2 storeys in building height, and it has a building area not more than the value in Table 3.2.2.30. | obc2019_divb | Div B | 3.2.2.30.(1) | 3.2.2.30. Group A, Division 3, up to 2 Storeys | A building classified as Group A, Division 3 is permitted to conform to Sentence (2) provided, it is not more than 2 storeys in building height, and it has a building area not more than the value in Table 3.2.2.30. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.30.(2) | Group A, Division 1, One Storey, Sprinklered | The building referred to in Sentence 3.2.2.22.(1) is permitted to be of combustible construction or noncombustible construction used singly, or in combination, and floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min, mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall have a fire-resistance rating not less than 45 min, or be of noncombustible construction, and loadbearing walls, columns and arches supporting a fire separation shall have a fire-resistance rating not less than that required for the fire separation. | obc2019_divb | Div B | 3.2.2.30.(2) | 3.2.2.30. Group A, Division 3, up to 2 Storeys | Except as permitted by Clauses (c) and (d), the building referred to in Sentence (1) shall be of noncombustible construction, and, floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, mezzanines shall have a fire-resistance rating not less than 1 h, roof assemblies shall, have a fire-resistance rating not less than 45 min, or be of heavy timber construction, and loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly, except that arches and structural members within the storey immediately below a roof assembly are permitted to be of heavy timber construction. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.30.(3) | Group A, Division 3, up to 2 Storeys | If intended for occasional use for trade shows and similar exhibition purposes, a building referred to in Sentence 3.2.2.30.(1) that is more than 1?500 m2 in building area shall be sprinklered throughout. | obc2019_divb | Div B | 3.2.2.30.(3) | 3.2.2.30. Group A, Division 3, up to 2 Storeys | If intended for occasional use for trade shows and similar exhibition purposes, the building referred to in Sentence (1) that is more than 1 500 m2 in building area shall be sprinklered. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.30.(3) | Group A, Division 3, One Storey, Increased Area | If intended for occasional use for trade shows and similar exhibition purposes, a building referred to in Sentence 3.2.2.30.(1) that is more than 1500 m2 in building area shall be sprinklered throughout. | obc2019_divb | Div B | 3.2.2.32.(3) | 3.2.2.32. Group A, Division 3, 1 Storey, Increased Area | If intended for occasional use for trade shows and similar exhibition purposes, the building referred to in Sentence (1) that is more than 1 500 m2 in building area shall be sprinklered. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.31.(1) | Group A, Division 3, up to 2 Storeys, Sprinklered | A building classified as Group A, Division 3 is permitted to conform to Sentence 3.2.2.31.(2) provided except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout, it is not more than 2 storeys in building height, and it has a building area not more than 12?000 m2 if 1 storey in building height, or 6?000 m2 if 2 storeys in building height. | obc2019_divb | Div B | 3.2.2.31.(1) | 3.2.2.31. Group A, Division 3, up to 2 Storeys, Sprinklered | A building classified as Group A, Division 3 is permitted to conform to Sentence (2) provided, except as permitted by Sentence 3.2.2.7.(1), the building shall be sprinklered, it is not more than 2 storeys in building height, and it has a building area not more than, 12 000 m2 if 1 storey in building height, or 6 000 m2 if 2 storeys in building height. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.31.(2) | Group A, Division 3, up to 2 Storeys, Sprinklered | Except as permitted by Article 3.2.2.16., the building referred to in Sentence 3.2.2.75.(1) shall be of noncombustible construction, and floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, mezzanines shall have a fire-resistance rating not less than 1 h, and loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. | obc2019_divb | Div B | 3.2.2.31.(2) | 3.2.2.31. Group A, Division 3, up to 2 Storeys, Sprinklered | Except as permitted by Clause (c) and Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and, floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, mezzanines shall have a fire-resistance rating not less than 1 h, and loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly, except that arches are permitted to be of heavy timber construction. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.32.(1) | Group A, Division 3, One Storey, Increased Area | A building classified as Group A, Division 3 is permitted to conform to Sentence 3.2.2.32.(2) provided it is not more than 1 storey in building height, and it has a building area not more than 2?400 m2 if facing one street, 3?000 m2 if facing 2 streets, or 3?600 m2 if facing 3 streets. | obc2019_divb | Div B | 3.2.2.32.(1) | 3.2.2.32. Group A, Division 3, 1 Storey, Increased Area | A building classified as Group A, Division 3 is permitted to conform to Sentences (2) and (3) provided, it is not more than 1 storey in building height, and it has a building area not more than, 2 400 m2 if facing one street, 3 000 m2 if facing two streets, or 3 600 m2 if facing three streets. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.32.(2) | Group A, Division 3, One Storey, Increased Area | The building referred to in Sentence 3.2.2.32.(1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, roof assemblies shall have, if of combustible construction, a fire-resistance rating not less than 45 min, except that the fire-resistance rating is permitted to be waived provided the roof assembly is constructed as a fire-retardant-treated wood roof system conforming to Article 3.1.14.1., and the building area is not more than 1?200 m2 if facing one street, 1?500 m2 if facing 2 streets , or 1?800 m2 if facing 3 streets , and loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall have a fire-resistance rating not less than 45 min, or be of noncombustible construction. | obc2019_divb | Div B | 3.2.2.32.(2) | 3.2.2.32. Group A, Division 3, 1 Storey, Increased Area | The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and, mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, roof assemblies shall have, if of combustible construction, a fire-resistance rating not less than 45 min, except that the fire-resistance rating is permitted to be waived provided the roof assembly is constructed as a fire-retardant treated wood roof system conforming to Article 3.1.14.1., and the building area is not more than, 1 200 m2 if facing one street, 1 500 m2 if facing two streets, or 1 800 m2 if facing three streets, and loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall, have a fire-resistance rating not less than 45 min, or be of noncombustible construction. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.33.(1) | Group A, Division 3, One Storey, Sprinklered | A building classified as Group A, Division 3 is permitted to be of combustible construction or noncombustible construction used singly or in combination provided except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout, it is not more than 1 storey in building height, and it has a building area not more than 7?200 m2 . | obc2019_divb | Div B | 3.2.2.33.(1) | 3.2.2.33. Group A, Division 3, 1 Storey, Sprinklered | A building classified as Group A, Division 3 is permitted to be of combustible construction or noncombustible construction used singly or in combination, provided, except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered, it is not more than 1 storey in building height, and it has a building area not more than 7 200 m2. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.34.(1) | Group A, Division 3, One Storey | A building classified as Group A, Division 3 is permitted to be of combustible construction or noncombustible construction used singly or in combination provided it is not more than 1 storey in building height, and it has a building area not more than 1?000 m2 if facing one street, 1?250 m2 if facing 2 streets, or 1?500 m2 if facing 3 streets. | obc2019_divb | Div B | 3.2.2.34.(1) | 3.2.2.34. Group A, Division 3, 1 Storey | A building classified as Group A, Division 3 is permitted to be of combustible construction or noncombustible construction used singly or in combination, provided, it is not more than 1 storey in building height, and it has a building area not more than, 1 000 m2 if facing one street, 1 250 m2 if facing two streets, or 1 500 m2 if facing three streets. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.35.(1) | Group A, Division 4 | Except as permitted by Sentences 3.2.2.35.(2) and 3.2.2.35.(3), a building classified as Group A, Division 4 shall be of noncombustible construction. | obc2019_divb | Div B | 3.2.2.35.(1) | 3.2.2.35. Group A, Division 4 | Except as permitted by Sentences (2) and (3), a building classified as Group A, Division 4 shall be of noncombustible construction. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.35.(2) | Group A, Division 4 | Roof assemblies and supporting arches and columns are permitted to be of heavy timber construction. | obc2019_divb | Div B | 3.2.2.35.(2) | 3.2.2.35. Group A, Division 4 | Roof assemblies and supporting arches and columns are permitted to be of heavy timber construction. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.35.(3) | Group A, Division 4 | A building classified as Group A, Division 4 is permitted to be of combustible construction provided the occupant load is less than 1?500, and the building has a limiting distance not less than 6 m. | obc2019_divb | Div B | 3.2.2.35.(3) | 3.2.2.35. Group A, Division 4 | A building classified as Group A, Division 4 is permitted to be of combustible construction provided, the occupant load is less than 1 500, and the building has a limiting distance not less than 6 m. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.35.(4) | Group A, Division 4 | Sprinklers shall be installed in all spaces below tiers of seats in a building classified as Group A, Division 4 if those spaces are used for occupancy. (See Note A-3.2.2.35.(4).) | obc2019_divb | Div B | 3.2.2.35.(4) | 3.2.2.35. Group A, Division 4 | Sprinklers shall be installed in all spaces below tiers of seats in a building classified as Group A, Division 4 if those spaces are used for occupancy. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.36.(1) | Group B, Division 1, Any Height, Any Area, Sprinklered | Except as permitted by Article 3.2.2.37., a building classified as Group B, Division 1 shall conform to Sentence 3.2.2.36.(2). | obc2019_divb | Div B | 3.2.2.36.(1) | 3.2.2.36. Group B, Division 1, Any Height, Any Area, Sprinklered | Except as permitted by Article 3.2.2.37., a building classified as Group B, Division 1 shall conform to Sentence (2). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.36.(2) | Group B, Division 1, Any Height, Any Area, Sprinklered | Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building shall be sprinklered throughout, (b) floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h, (c) mezzanines shall have a fire-resistance rating not less than 1 h, and (d) loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. | obc2019_divb | Div B | 3.2.2.36.(2) | 3.2.2.36. Group B, Division 1, Any Height, Any Area, Sprinklered | Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and, except as permitted by Sentence 3.2.2.7.(1), the building shall be sprinklered, floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h, mezzanines shall have a fire-resistance rating not less 1 h, and loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.37.(1) | Group B, Division 1, up to 3 Storeys, Sprinklered | A building classified as Group B, Division 1 is permitted to conform to Sentence (2) provided (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout, (b) it is not more than 3 storeys in building height, and (c) it has a building area (i) that is not limited if the building is not more than 1 storey in building height, (ii) not more than 12 000 m2 if 2 storeys in building height, or (iii) not more than 8 000 m2 if 3 storeys in building height. | obc2019_divb | Div B | 3.2.2.37.(1) | 3.2.2.37. Group B, Division 1, up to 3 Storeys, Sprinklered | A building classified as Group B, Division 1 is permitted to conform to Sentence (2) provided, (a) except as permitted by Sentence 3.2.2.7.(1) the building is sprinklered, (b) it is not more than 3 storeys in building height, and (c) it has a building area, (i) that is not limited if the building is not more than 1 storey in building height, (ii)not more than 12 000 m2 if 2 storeys in building height, or (iii) not more than 8 000 m2 if 3 storeys in building height. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.37.(2) | Group B, Division 1, up to 3 Storeys, Sprinklered | Except as permitted by Article 3.2.2.16., the building referred to in Sentence 3.2.2.75.(1) shall be of noncombustible construction, and floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, mezzanines shall have a fire-resistance rating not less than 1 h, and loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. | obc2019_divb | Div B | 3.2.2.37.(2) | 3.2.2.37. Group B, Division 1, up to 3 Storeys, Sprinklered | Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and, floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, mezzanines shall have a fire-resistance rating not less than 1 h, and loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.38.(1) | Group B, Division 2, Any Height, Any Area, Sprinklered Group B, Division 3, Any Height, Any Area, Sprinklered | Except as permitted by Articles 3.2.2.39. to 3.2.2.41., a building classified as Group B, Division 2 shall conform to Sentence (2). Except as permitted by Articles 3.2.2.43. to 3.2.2.46., a building classified as Group B, Division 2 shall conform to Sentence (2). | obc2019_divb | Div B | 3.2.2.38.(1) | 3.2.2.38. Group B, Division 2 or Division 3, Any Height, Any | Except as permitted by Articles 3.2.2.39. to 3.2.2.41., a building classified as Group B, Division 2 or Division 3 shall conform to Sentence (2). |  | Common Sentence | No | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.38.(2) | Group B, Division 2, Any Height, Any Area, Sprinklered Group B, Division 3, Any Height, Any Area, Sprinklered | Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building shall be sprinklered throughout, (b) floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h, (c) mezzanines shall have a fire-resistance rating not less than 1 h, and (d) loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building shall be sprinklered throughout, (b) floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h, (c) mezzanines shall have a fire-resistance rating not less than 1 h, and (d) loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. | obc2019_divb | Div B | 3.2.2.38.(2) | 3.2.2.38. Group B, Division 2 or Division 3, Any Height, Any | Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and, except as permitted by Sentence 3.2.2.7.(1), the building shall be sprinklered, floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h, mezzanines shall have a fire-resistance rating not less 1 h, and loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.39.(1) | Group B, Division 2, up to 3 Storeys, Sprinklered Group B, Division 3, up to 3 Storeys (Noncombustible), Sprinklered | A building classified as Group B, Division 2 is permitted to conform to Sentence (2) provided (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout, (b) it is not more than 3 storeys in building height, and (c) it has a building area (i) that is not limited if the building is not more than 1 storey in building height, (ii) not more than 12 000 m2 if 2 storeys in building height, or (iii) not more than 8 000 m2 if 3 storeys in building height. A building classified as Group B, Division 3 is permitted to conform to Sentence (2) provided (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout, (b) it is not more than 3 storeys in building height, and (c) it has a building area (i) that is not limited if the building is not more than 1 storey in building height, (ii) not more than 12 000 m2 if 2 storeys in building height, or (iii) not more than 8 000 m2 if 3 storeys in building height. | obc2019_divb | Div B | 3.2.2.39.(1) | 3.2.2.39. Group B, Division 2 or Division 3, up to 3 Storeys, Sprinklered | A building classified as Group B, Division 2 or Division 3 is permitted to conform to Sentence (2) provided, (a) except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered, (b) it is not more than 3 storeys in building height, and (c) it has a building area, (i) that is not limited if the building is not more than 1 storey in building height, (ii) not more than 12 000 m2 if 2 storeys in building height, or (iii) not more than 8 000 m2 if 3 storeys in building height. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.39.(2) | Group B, Division 2, up to 3 Storeys, Sprinklered Group B, Division 3, up to 3 Storeys (Noncombustible), Sprinklered | Except as permitted by Article 3.2.2.16., the building referred to in Sentence 3.2.2.75.(1) shall be of noncombustible construction, and floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, mezzanines shall have a fire-resistance rating not less than 1 h, and loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. | obc2019_divb | Div B | 3.2.2.39.(2) | 3.2.2.39. Group B, Division 2 or Division 3, up to 3 Storeys, Sprinklered | Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and, (a) floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, (b) mezzanines shall have a fire-resistance rating not less than 1 h, and (c) loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.4.(1) | Buildings with Multiple Major Occupancies | The requirements restricting fire spread and collapse for a building of a single major occupancy classification are provided in this Subsection according to its building height and building area. | obc2019_divb | Div B | 3.2.2.4.(1) | 3.2.2.4. Buildings with Multiple Major Occupancies | The requirements restricting fire spread and collapse for a building of a single major occupancy classification are provided in this Subsection according to its building height and building area. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.4.(2) | Buildings with Multiple Major Occupancies | If a building contains more than one major occupancy, classified in more than one Group or Division, the requirements of this Subsection concerning building size and construction relative to major occupancy shall apply according to Articles 3.2.2.5.to 3.2.2.8. | obc2019_divb | Div B | 3.2.2.4.(2) | 3.2.2.4. Buildings with Multiple Major Occupancies | If a building contains more than one major occupancy, classified in more than one Group or Division, the requirements of this Subsection concerning building size and construction relative to major occupancy shall apply according to Articles 3.2.2.5. to 3.2.2.8. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.40.(1) | Group B, Division 2, up to 2 Storeys, Sprinklered Group B, Division 3, up to 2 Storeys, Sprinklered | A building classified as Group B, Division 2 is permitted to conform to Sentence (2) provided (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout, (b) it is not more than 2 storeys in building height, and (c) it has a building area not more than (i) 2 400 m2 if 1 storey in building height, or (ii) 1 600 m2 if 2 storeys in building height. A building classified as Group B, Division 3 is permitted to conform to Sentence (2) provided (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout, (b) it is not more than 2 storeys in building height, and (c) it has a building area not more than (i) 2 400 m2 if 1 storey in building height, or (ii) 1 600 m2 if 2 storeys in building height. | obc2019_divb | Div B | 3.2.2.40.(1) | 3.2.2.40. Group B, Division 2 or Division 3, up to 2 Storeys, | A building classified as Group B, Division 2 or Division 3 is permitted to conform to Sentence (2) provided, (a) except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered, (b) it is not more than 2 storeys in building height, and (c) it has a building area not more than, (i) 2 400 m2 if 1 storey in building height, or (ii) 1 600 m2 if 2 storeys in building height. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.40.(2) | Group B, Division 2, up to 2 Storeys, Sprinklered Group B, Division 3, up to 2 Storeys, Sprinklered | The building referred to in Sentence 3.2.2.40.(1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and (a) floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, (b) mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, and (c) loadbearing walls, columns and arches shall have a fire-resistance rating not less than required for the supported assembly. | obc2019_divb | Div B | 3.2.2.40.(2) | 3.2.2.40. Group B, Division 2 or Division 3, up to 2 Storeys, Sprinklered | The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and, (a) floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min, (b) mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, and (c) loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.41.(1) | Group B, Division 2, One Storey, Sprinklered Group B, Division 3, One Storey, Sprinklered | A building classified as Group B, Division 2 is permitted to be of combustible construction or noncombustible construction, used singly or in combination, provided (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout, (b) it is not more than 1 storey in building height, and (c) it has a building area not more than 500 m2 . A building classified as Group B, Division 3 is permitted to be of combustible construction or noncombustible construction, used singly or in combination, provided (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout, (b) it is not more than 1 storey in building height, and (c) it has a building area not more than 600 m2 . | obc2019_divb | Div B | 3.2.2.41.(1) | 3.2.2.41. Group B, Division 2 or Division 3, 1 Storey, Sprinklered | A building classified as Group B, Division 2 or Division 3 is permitted to be of combustible construction or noncombustible construction used singly or in combination, provided, except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered, it is not more than 1 storey in building height, and it has a building area not more than 500 m2. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.47.(1) | Group C, Any Height, Any Area, Sprinklered | Except as permitted by Articles 3.2.2.48. to 3.2.2.54., a building classified as Group C shall conform to Sentence (2). | obc2019_divb | Div B | 3.2.2.42.(1) | 3.2.2.42. Group C, Any Height, Any Area, Sprinklered | Except as permitted by Articles 3.2.2.43. to 3.2.2.48., a building classified as Group C other than a retirement home shall conform to Sentence (2). |  | Common Sentence | Yes | Retirement Homes
2015 | ON | NBC | Div B | 3.2.2.47.(2) | Group C, Any Height, Any Area, Sprinklered | Except as permitted by Article 3.2.2.16., the building referred to in Sentence 3.2.2.47.(1) shall be of noncombustible construction, and except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building shall be sprinklered throughout, except as permitted by Sentence 3.2.2.47.(3), floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h, mezzanines shall have a fire-resistance rating not less than 1 h, and loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. | obc2019_divb | Div B | 3.2.2.42.(2) | 3.2.2.42. Group C, Any Height, Any Area, Sprinklered | Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and, except as permitted by Sentence 3.2.2.7.(1), the building shall be sprinklered, except as permitted by Sentence (3), floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h, mezzanines shall have a fire-resistance rating not less than 1 h, and loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.47.(3) | Group C, Any Height, Any Area, Sprinklered | In a building that contains dwelling units that have more than one storey, subject to the requirements of Sentence 3.3.4.2.(3), the floor assemblies, including floors over basements, which are entirely contained within these dwelling units, shall have a fire-resistance rating not less than 1 h but need not be constructed as fire separations. | obc2019_divb | Div B | 3.2.2.42.(3) | 3.2.2.42. Group C, Any Height, Any Area, Sprinklered | In a building that contains dwelling units that have more than 1 storey, subject to the requirements of Sentence 3.3.4.2.(3), the floor assemblies, including floors over basements, which are entirely contained within these dwelling units, shall have a fire-resistance rating not less than 1 h but need not be constructed as fire separations. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.48.(1) | Group C, up to 6 Storeys, Sprinklered, Noncombustible | A building classified as Group C is permitted to conform to Sentence 3.2.2.48.(2) provided (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout, (b) it is not more than 6 storeys in building height, and (c) it has a building area (i) that is not limited if the building is not more than 2 storeys in building height, (ii) not more than 12000 m2 if 3 storeys in building height, (iii) not more than 9000 m2 if 4 storeys in building height, (iv) not more than 7200 m2 if 5 storeys in building height, or (v) not more than 6000 m2 if 6 storeys in building height. | obc2019_divb | Div B | 3.2.2.43.(1) | 3.2.2.43. Group C, up to 6 Storeys, Sprinklered, Noncombustible | A building classified as Group C other than a retirement home is permitted to conform to Sentence (2) provided, (a) except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered, (b) it is not more than 6 storeys in building height, and (c) it has a building area, (i) that is not limited if the building is not more than 2 storeys in building height, (ii) not more than 12 000 m2 if 3 storeys in building height, (iii) not more than 9 000 m2 if 4 storeys in building height, (iv) not more than 7 200 m2 if 5 storeys in building height, or (v) not more than 6 000 m2 if 6 storeys in building height. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.48.(2) | Group F, Division 2, up to 4 Storeys, Increased Area, Sprinklered | Except as permitted by Article 3.2.2.16., the building referred to in Sentence 3.2.2.75.(1) shall be of noncombustible construction, and floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, mezzanines shall have a fire-resistance rating not less than 1 h, and loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. | obc2019_divb | Div B | 3.2.2.43.(2) | 3.2.2.43. Group C, up to 6 Storeys, Sprinklered, Noncombustible | Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and, except as permitted by Sentence (3), floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, mezzanines shall have a fire-resistance rating not less than 1 h, and loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.48.(3) | Group C, up to 6 Storeys, Sprinklered, Noncombustible | In a building that contains dwelling units that have more than one storey, subject to the requirements of Sentence 3.3.4.2.(3), the floor assemblies, including floors over basements, which are entirely contained within these dwelling units, shall have a fire-resistance rating not less than 1 h but need not be constructed as fire separations. | obc2019_divb | Div B | 3.2.2.43.(3) | 3.2.2.43. Group C, up to 6 Storeys, Sprinklered, Noncombustible | In a building that contains dwelling units that have more than 1 storey, subject to the requirements of Sentence 3.3.4.2.(3), the floor assemblies, including floors over basements, which are entirely contained within these dwelling units, shall have a fire-resistance rating not less than 1 h but need not be constructed as fire separations. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.5.(1) | Applicable Building Height and Area | In determining the fire safety requirements of a building in relation to each of the major occupancies contained therein, the building height and building area of the entire building shall be used. | obc2019_divb | Div B | 3.2.2.5.(1) | 3.2.2.5. Applicable Building Height and Area | In determining the fire safety requirements of a building in relation to each of the major occupancies contained in it, the building height and building area of the entire building shall be used. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.50.(1) | Group C, up to 6 Storeys, Sprinklered | A building classified as Group C is permitted to conform to Sentence 3.2.2.50.(2), provided (a) it is sprinklered throughout, (b) it is not more than 6 storeys in building height, (c) it has a height not more than 18 m measured between the floor of the first storey and the uppermost floor level that does not serve a rooftop enclosure for elevator machinery, a stairway or a service room used only for service to the building, and (d) it has a building area not more than (i) 9 000 m2 if 1 storey in building height, (ii) 4 500 m2 if 2 storeys in building height, (iii) 3 000 m2 if 3 storeys in building height, (iv) 2 250 m2 if 4 storeys in building height, (v) 1 800 m2 if 5 storeys in building height, or (vi) 1 500 m2 if 6 storeys in building height. | obc2019_divb | Div B | 3.2.2.43.(1) | 3.2.2.43A. Group C, up to 6 Storeys, Sprinklered, Combustible | A building classified as Group C other than a retirement home is permitted to conform to Sentence (2) provided, (a) it is sprinklered, (b) it is not more than 6 storeys in building height, (c) it has a height of not more than 18 m, measured between the floor level of the first storey and the floor level of the uppermost storey or mezzanine that is not a rooftop enclosure, provided for elevator machinery, a stairway or a service room used for no purpose other than for service to the building, and (d) it has a building area of not more than, (i) 9 000 m2 if 1 storey in building height, (ii) 4 500 m2 if 2 storeys in building height, (iii) 3 000 m2 if 3 storeys in building height, (iv) 2 250 m2 if 4 storeys in building height, (v) 1 800 m2 if 5 storeys in building height, or (vi) 1 500 m2 if 6 storeys in building height. |  | Common Sentence | Yes | Mid-rise Wood
2015 | ON | NBC | Div B | 3.2.2.50.(2) | Group C, up to 6 Storeys, Sprinklered | Buildings referred to in Sentence 3.2.2.50.(1) are permitted to be of combustible construction or noncombustible construction, used singly or in combination, and except as provided in Sentence 3.2.2.50.(3), floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, roof assemblies shall have a fire-resistance rating not less than 1 h, except as provided in Sentence 3.2.2.50.(4), where the roof assembly has a height greater than 25 m measured from the floor of the first storey to the highest point of the roof assembly, the roof assembly shall be constructed of noncombustible construction or fire-retardant-treated wood conforming to Article 3.1.4.5., mezzanines shall have a fire-resistance rating not less than 1 h, and loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. | obc2019_divb | Div B | 3.2.2.43.(2) | 3.2.2.43A. Group C, up to 6 Storeys, Sprinklered, Combustible | The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction, used singly or in combination, and, except as permitted by Sentence (3), floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, roof assemblies shall have a fire-resistance rating not less than 1 h, except as provided by Sentence (4), where the roof assembly has a height greater than 25 m measured from the floor level of the first storey to the highest point of the roof assembly, the roof assembly shall, be of noncombustible construction, or be constructed of fire-retardant treated wood conforming to Article 3.1.4.5., mezzanines shall have a fire-resistance rating not less than 1 h, the fire separation of exits described in Sentence 3.4.4.1.(3) shall be of noncombustible construction, and loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | Common Sentence | Yes | Mid-rise Wood
2015 | ON | NBC | Div B | 3.2.2.50.(3) | Group C, up to 6 Storeys, Sprinklered | In a building that contains dwelling units that have more than one storey, subject to the requirements of Sentence 3.3.4.2.(3), the floor assemblies, including floors over basements, which are entirely contained within these dwelling units, shall have a fire-resistance rating not less than 1 h but need not be constructed as fire separations. | obc2019_divb | Div B | 3.2.2.43.(3) | 3.2.2.43A. Group C, up to 6 Storeys, Sprinklered, Combustible | In a building that contains dwelling units that have more than 1 storey, subject to the requirements of Sentence 3.3.4.2.(3), the floor assemblies, including floors over basements, which are entirely contained within these dwelling units, shall have a fire-resistance rating not less than 1 h but need not be constructed as fire separations. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.50.(4) | Group C, up to 6 Storeys, Sprinklered | Where buildings conforming to Sentence 3.2.2.50.(2) include non-contiguous roof assemblies at different elevations, the roof assemblies are permitted to be evaluated separately to determine which ones are required to be constructed in accordance with Sentence 3.2.2.50.(2). | obc2019_divb | Div B | 3.2.2.43.(4) | 3.2.2.43A. Group C, up to 6 Storeys, Sprinklered, Combustible | The construction of non-contiguous roof assemblies at different elevations is permitted to be evaluated separately to determine which roof assemblies are required to be constructed in accordance with Clause (2)(c). |  | Common Sentence | No | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.51.(1) | Group C, up to 3 Storeys, Noncombustible Construction | A building classified as Group C is permitted to conform to Sentence (2) provided (a) it is not more than 3 storeys in building height, and (b) it has a building area not more than the value in Table 3.2.2.49. | obc2019_divb | Div B | 3.2.2.44.(1) | 3.2.2.44. Group C, up to 4 Storeys, Noncombustible Construction | A building classified as Group C other than a retirement home is permitted to conform to Sentence (2) provided, it is not more than, 3 storeys in building height, or 4 storeys in building height provided there is not more than one dwelling unit above another dwelling unit, and vertical fire separations of adjacent dwelling units conform to Sentence (4), and it has a building area not more than the value in Table 3.2.2.44. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.51.(2) | Group C, up to 3 Storeys, Noncombustible Construction | The building referred to in Sentence (1) shall be of noncombustible construction, and (a) except as permitted by Sentence (3), floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, (b) mezzanines shall have a fire-resistance rating not less than 1 h, (c) roof assemblies shall have a fire-resistance rating not less than 1 h, and (d) loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. | obc2019_divb | Div B | 3.2.2.44.(2) | 3.2.2.44. Group C, up to 4 Storeys, Noncombustible Construction | The building referred to in Sentence (1) shall be of noncombustible construction, and, except as permitted by Sentence (3), floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, mezzanines shall have a fire-resistance rating not less than 1 h, roof assemblies shall have a fire-resistance rating not less than 1 h, and loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.51.(3) | Group C, up to 3 Storeys, Noncombustible Construction | In a building that contains dwelling units that have more than one storey, subject to the requirements of Sentence 3.3.4.2.(3), the floor assemblies, including floors over basements, which are entirely contained within these dwelling units, shall have a fire-resistance rating not less than 1 h but need not be constructed as fire separations. | obc2019_divb | Div B | 3.2.2.44.(3) | 3.2.2.44. Group C, up to 4 Storeys, Noncombustible Construction | In a building that contains dwelling units that have more than 1 storey, subject to the requirements of Sentence 3.3.4.2.(3), the floor assemblies, including floors over basements, which are entirely contained within these dwelling units, shall have a fire-resistance rating not less than 1 h but need not be constructed as fire separations. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.51.(4) | Group C, up to 4 Storeys, Sprinklered | In a building in which there is no dwelling unit above another dwelling unit, the fire-resistance rating for floor assemblies entirely within the dwelling unit is waived. | obc2019_divb | Div B | 3.2.2.45.(4) | 3.2.2.44. Group C, up to 4 Storeys, Noncombustible Construction | The dwelling units described in Subclause (1)(a)(ii) shall be separated by continuous vertical fire separations that extend through all storeys and service spaces of the separated portions. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.52.(1) | Group C, up to 4 Storeys, Sprinklered | A building classified as Group C is permitted to conform to Sentence (2) provided (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout, (b) it is not more than 4 storeys in building height, and (c) it has a building area not more than (i) 7 200 m2 if 1 storey in building height, (ii) 3 600 m2 if 2 storeys in building height, (iii) 2 400 m2 if 3 storeys in building height, or (iv) 1 800 m2 if 4 storeys in building height. | obc2019_divb | Div B | 3.2.2.45.(1) | 3.2.2.45. Group C, up to 4 Storeys, Sprinklered | A building classified as Group C other than a retirement home is permitted to conform to Sentence (2) provided, (a) except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered, (b) it is not more than 4 storeys in building height, and (c) it has a building area not more than, (i) 7 200 m2 if 1 storey in building height, (ii) 3 600 m2 if 2 storeys in building height, (iii) 2 400 m2 if 3 storeys in building height, or (iv) 1 800 m2 if 4 storeys in building height. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.52.(2) | Group C, up to 3 Storeys, Increased Area | The building referred to in Sentence 3.2.2.52.(1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and except as permitted by Sentences 3.2.2.52.(3) and 3.2.2.52.(4), floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, mezzanines shall have a fire-resistance rating not less than 1 h, roof assemblies shall have a fire-resistance rating not less than 1 h, and loadbearing walls, columns, and arches shall have a fire-resistance rating not less than that required for the supported assembly. | obc2019_divb | Div B | 3.2.2.46.(2) | 3.2.2.46. Group C, up to 3 Storeys, Increased Area | (2) The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and, except as permitted by Sentences (3) and (4), floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, mezzanines shall have a fire-resistance rating not less than 1 h, roof assemblies shall have a fire-resistance rating not less than 1 h, and loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.52.(3) | Group C, up to 4 Storeys, Sprinklered | In a building that contains dwelling units that have more than one storey, subject to the requirements of Sentence 3.3.4.2.(3), the floor assemblies, including floors over basements, which are entirely contained within these dwelling units, shall have a fire-resistance rating not less than 1 h but need not be constructed as fire separations. | obc2019_divb | Div B | 3.2.2.45.(3) | 3.2.2.45. Group C, up to 4 Storeys, Sprinklered | In a building that contains dwelling units that have more than 1 storey, subject to the requirements of Sentence 3.3.4.2.(3), the floor assemblies, including floors over basements, that are entirely contained within these dwelling units, shall have a fire-resistance rating not less than 1 h but need not be constructed as fire separations. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.52.(3) | Group C, up to 3 Storeys, Increased Area | In a building that contains dwelling units that have more than one storey, subject to the requirements of Sentence 3.3.4.2.(3), the floor assemblies, including floors over basements, which are entirely contained within these dwelling units, shall have a fire-resistance rating not less than 1 h but need not be constructed as fire separations. | obc2019_divb | Div B | 3.2.2.46.(3) | 3.2.2.46. Group C, up to 3 Storeys, Increased Area | In a building that contains dwelling units that have more than 1 storey, subject to the requirements of Sentence 3.3.4.2.(3), the floor assemblies, including floors over basements, that are entirely contained within these dwelling units, shall have a fire-resistance rating not less than 1 h but need not be constructed as fire separations. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.52.(4) | Group C, up to 3 Storeys, Increased Area | In a building in which there is no dwelling unit above another dwelling unit, the fire-resistance rating for floor assemblies entirely within the dwelling unit is waived. | obc2019_divb | Div B | 3.2.2.46.(4) | 3.2.2.45. Group C, up to 4 Storeys, Sprinklered | In a building in which there is no dwelling unit above another dwelling unit, the fire-resistance rating for floor assemblies entirely within the dwelling unit is waived. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.53.(1) | Group C, up to 3 Storeys, Increased Area | A building classified as Group C is permitted to conform to Sentence (2) provided (a) it is not more than 3 storeys in building height, and (b) it has a building area not more than the value in Table 3.2.2.52. | obc2019_divb | Div B | 3.2.2.46.(1) | 3.2.2.46. Group C, up to 3 Storeys, Increased Area | A building classified as Group C other than a retirement home is permitted to conform to Sentence (2) provided, it is not more than 3 storeys in building height, and it has a building area not more than the value in Table 3.2.2.46. |  | Common Sentence | Yes | Retirement Homes
2015 | ON | NBC | Div B | 3.2.2.53.(4) | Group C, up to 3 Storeys | In a building in which there is no dwelling unit above another dwelling unit, the fire-resistance rating for floor assemblies entirely within the dwelling unit is waived. | obc2019_divb | Div B | 3.2.2.47.(4) | 3.2.2.46. Group C, up to 3 Storeys, Increased Area | In a building in which there is no dwelling unit above another dwelling unit, the fire-resistance rating for floor assemblies entirely within the dwelling unit is waived. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.54.(1) | Group C, up to 3 Storeys | A building classified as Group C is permitted to conform to Sentence (2) provided (a) it is not more than 3 storeys in building height, and (b) it has a building area not more than the value in Table 3.2.2.53. | obc2019_divb | Div B | 3.2.2.47.(1) | 3.2.2.47. Group C, up to 3 Storeys | A building classified as Group C other than a retirement home is permitted to conform to Sentence (2) provided, it is not more than 3 storeys in building height, and it has a building area not more than the value in Table 3.2.2.47. |  | Common Sentence | Yes | Retirement Homes
2015 | ON | NBC | Div B | 3.2.2.54.(1) | Group C, up to 3 Storeys | In a building that contains dwelling units that have more than one storey, subject to the requirements of Sentence 3.3.4.2.(3), the floor assemblies, including floors over basements, which are entirely contained within these dwelling units, shall have a fire-resistance rating not less than 45 min but need not be constructed as fire separations. | obc2019_divb | Div B | 3.2.2.47.(3) | 3.2.2.47. Group C, up to 3 Storeys | In a building that contains dwelling units that have more than 1 storey, subject to the requirements of Sentence 3.3.4.2.(3), the floor assemblies, including floors over basements, that are entirely contained within these dwelling units, shall have a fire-resistance rating not less than 45 min but need not be constructed as fire separations. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.54.(2) | Group C, up to 3 Storeys | The building referred to in Sentence 3.2.2.26.(1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, and loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall have a fire-resistance rating not less than 45 min, or be of noncombustible construction. | obc2019_divb | Div B | 3.2.2.47.(2) | 3.2.2.47. Group C, up to 3 Storeys | (2) The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and, except as permitted by Sentences (3) and (4), floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min, mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, and loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.54.(3) | Group C, up to 3 Storeys, Sprinklered | In a building that contains dwelling units that have more than one storey, subject to the requirements of Sentence 3.3.4.2.(3), the floor assemblies, including floors over basements, which are entirely contained within these dwelling units, shall have a fire-resistance rating not less than 45 min but need not be constructed as fire separations. | obc2019_divb | Div B | 3.2.2.48.(3) | 3.2.2.48. Group C, up to 3 Storeys, Sprinklered | In a building that contains dwelling units that have more than 1 storey, subject to the requirements of Sentence 3.3.4.2.(3), the floor assemblies, including floors over basements, that are entirely contained within these dwelling units, shall have a fire-resistance rating not less than 45 min but need not be constructed as fire separations. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.54.(4) | Group C, up to 3 Storeys, Sprinklered | In a building in which there is no dwelling unit above another dwelling unit, the fire-resistance rating for floor assemblies entirely within the dwelling unit is waived. | obc2019_divb | Div B | 3.2.2.48.(4) | 3.2.2.47. Group C, up to 3 Storeys | In a building in which there is no dwelling unit above another dwelling unit, the fire-resistance rating for floor assemblies entirely within the dwelling unit is waived. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.55.(1) | Group C, up to 3 Storeys, Sprinklered | A building classified as Group C is permitted to conform to Sentence (2) provided ( a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout, (b) it is not more than 3 storeys in building height, and (c) it has a building area not more than (i) 5 400 m2 if 1 storey in building height, (ii) 2 700 m2 if 2 storeys in building height, or (iii) 1 800 m2 if 3 storeys in building height. | obc2019_divb | Div B | 3.2.2.49 3.2.2.48.(1) | 3.2.2.48. Group C, up to 3 Storeys, Sprinklered | A building classified as Group C other than a retirement home is permitted to conform to Sentence (2) provided, (a) except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered, (b) it is not more than 3 storeys in building height, and (c) it has a building area not more than, (i) 5 400 m2 if 1 storey in building height, (ii) 2 700 m2 if 2 storeys in building height, or (iii) 1 800 m2 if 3 storeys in building height. |  | Common Sentence | Yes | Retirement Homes
2015 | ON | NBC | Div B | 3.2.2.55.(1) | Group D, Any Height, Any Area, Sprinklered | Except as permitted by Articles 3.2.2.56. to 3.2.2.63., a building classified as Group D shall conform to Sentence (2). | obc2019_divb | Div B | 3.2.2.49.(1) | 3.2.2.49. Group D, Any Height, Any Area | Except as permitted by Articles 3.2.2.50. to 3.2.2.56., a building classified as Group D shall conform to Sentence (2). |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.55.(2) | Group C, up to 3 Storeys, Sprinklered | The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and (a) except as permitted by Sentences (3) and (4), floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min, (b) mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, and (c) loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. | obc2019_divb | Div B | 3.2.2.48.(2) | 3.2.2.48. Group C, up to 3 Storeys, Sprinklered | The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and, (a) except as permitted by Sentences (3) and (4), floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min, (b) mezzanines shall have, if of combustible construction a fire-resistance rating not less than 45 min, and (c) loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.55.(2) | Group C, up to 4 Storeys, Sprinklered | The building referred to in Sentence 3.2.2.44.(1) is permitted to be of combustible construction or noncombustible construction, used singly or in combination, and floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, mezzanines shall have a fire-resistance rating not less than 1 h, and loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. | obc2019_divb | Div B | 3.2.2.45.(2) | 3.2.2.45. Group C, up to 4 Storeys, Sprinklered | The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and, except as permitted by Sentences (3) and (4), floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, mezzanines shall have a fire-resistance rating not less than 1 h, and loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.58.(3) | Group C, up to 6 Storeys, Sprinklered | Where buildings conforming to Sentence 3.2.2.50.(2) include non-contiguous roof assemblies at different elevations, the roof assemblies are permitted to be evaluated separately to determine which ones are required to be constructed in accordance with Clause 3.2.2.50.(2)(c). | obc2019_divb | Div B | 3.2.2.50.(3) | 3.2.2.50A. Group D, up to 6 Storeys, Sprinklered, Combustible | The construction of non-contiguous roof assemblies at different elevations is permitted to be evaluated separately to determine which roof assemblies are required to be constructed in accordance with Clause (2)(c). |  | Common Sentence | No | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.6.(1) | Multiple Major Occupancies | Except as permitted by Articles 3.2.2.7. and 3.2.2.8., in a building containing more than one major occupancy, the requirements of this Subsection for the most restricted major occupancy contained shall apply to the whole building. | obc2019_divb | Div B | 3.2.2.6.(1) | 3.2.2.6. Multiple Major Occupancies | Except as permitted by Articles 3.2.2.7. and 3.2.2.8. and Sentences 3.2.2.43A.(5) and 3.2.2.50A.(4), in a building containing more than one major occupancy, the requirements of this Subsection for the most restricted major occupancy contained shall apply to the whole building. |  | Common Sentence | Yes | Mid-rise Wood
2015 | ON | NBC | Div B | 3.2.2.60.(1) | Group D, up to 3 Storeys | A building classified as Group C is permitted to conform to Sentence 3.2.2.53.(2) provided it is not more than 3 storeys in building height, and it has a building area not more than the value in Table 3.2.2.53. | obc2019_divb | Div B | 3.2.2.53.(1) | 3.2.2.53. Group D, up to 3 Storeys | A building classified as Group D is permitted to conform to Sentence (2) provided, it is not more than 3 storeys in building height, and it has a building area not more than the value in Table 3.2.2.53. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.60.(2) | Group D, up to 3 Storeys | The building referred to in Sentence 3.2.2.60.(1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and (a) floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, (b) mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, (c) roof assemblies shall have, if of combustible construction, a fire-resistance rating not less than 45 min, except that in a building not more than 1 storey in building height, the fire-resistance rating is permitted to be waived provided the roof assembly is constructed as a fire-retardant-treated wood roof system conforming to Article 3.1.14.1. and the building area is not more than (i) 2400 m2 if facing one street, (ii) 3000 m2 if facing 2 streets, or (iii) 3600 m2 if facing 3 streets, and (d) loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall (i) have a fire-resistance rating not less than 45 min, or (ii) be of noncombustible construction. | obc2019_divb | Div B | 3.2.2.53.(2) | 3.2.2.53. Group D, up to 3 Storeys | (2) The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and, (a) floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, (b) mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, (c) roof assemblies shall have, if of combustible construction, a fire-resistance rating not less than 45 min, except that in a building not more than 1 storey in building height, the fire-resistance rating is permitted to be waived provided the roof assembly is constructed as a fire-retardant treated wood roof system conforming to Article 3.1.14.1., and the building area is not more than, (i) 2 400 m2 if facing one street, (ii) 3 000 m2 if facing two streets, or (iii) 3 600 m2 if facing three streets, and (d) loadbearing walls, columns and arches supporting an assembly required to (i) have a fire-resistance rating shall, have a fire-resistance rating not less than 45 min, or (ii) be of noncombustible construction. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.61.(1) | Group D, up to 3 Storeys, Sprinklered | A building classified as Group D is permitted to conform to Sentence (2) provided (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout, (b) it is not more than 3 storeys in building height, and (c) it has a building area not more than (i) 14 400 m2 if 1 storey in building height, (ii) 7 200 m2 if 2 storeys in building height, or (iii) 4 800 m2 if 3 storeys in building height. | obc2019_divb | Div B | 3.2.2.54.(1) | 3.2.2.54. Group D, up to 3 Storeys, Sprinklered | A building classified as Group D is permitted to conform to Sentence (2) provided, (a) except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered, (b) it is not more than 3 storeys in building height, and (c) it has a building area not more than (i) 14 400 m2 if 1 storey in building height, (ii) 7 200 m2 if 2 storeys in building height, or (iii) 4 800 m2 if 3 storeys in building height. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.61.(2) | Group D, up to 3 Storeys, Sprinklered | The building referred to in Sentence 3.2.2.26.(1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, and loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall have a fire-resistance rating not less than 45 min, or be of noncombustible construction. | obc2019_divb | Div B | 3.2.2.54.(2) | 3.2.2.54. Group D, up to 3 Storeys, Sprinklered | The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and, floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, and loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall, have a fire-resistance rating not less than 45 min, or be of noncombustible construction. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.62.(1) | Group D, up to 2 Storeys | A building classified as Group D is permitted to conform to Sentence 3.2.2.62.(2) provided (a) it is not more than 2 storeys in building height, and (b) it has a building area not more than the value in Table 3.2.2.62. | obc2019_divb | Div B | 3.2.2.55.(1) | 3.2.2.55. Group D, up to 2 Storeys | A building classified as Group D is permitted to conform to Sentence (2) provided, it is not more than 2 storeys in building height, and it has a building area not more than the value in Table 3.2.2.55. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.62.(2) | Group D, Any Height, Any Area, Sprinklered | Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building shall be sprinklered throughout, (b) floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h, (c) mezzanines shall have a fire-resistance rating not less than 1 h, and (d) loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. | obc2019_divb | Div B | 3.2.2.55.(2) 3.2.2.49.(2) | 3.2.2.49. Group D, Any Height, Any Area | Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and, (a) except as permitted by Sentence 3.2.2.7.(1), the building shall be sprinklered if it is regulated by Subsection 3.2.6., (b) floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h, (c) mezzanines shall have a fire-resistance rating not less 1 h, (d) if the building is not sprinklered, roof assemblies shall have a fire-resistance rating not less than 1 h, except that in a building not more than 1 storey in building height this requirement is waived, and (e) loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.62.(2) | Group D, up to 2 Storeys | The building referred to in Sentence 3.2.2.62.(1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, and loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall have a fire-resistance rating not less than 45 min, or be of noncombustible construction. | obc2019_divb | Div B | 3.2.2.55.(2) | 3.2.2.55. Group D, up to 2 Storeys | (2) The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and, floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, and loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall, have a fire-resistance rating not less than 45 min, or be of noncombustible construction. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.63.(1) | Group D, up to 2 Storeys, Sprinklered | A building classified as Group D is permitted to conform to Sentence (2) provided (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout, (b) it is not more than 2 storeys in building height, and (c) it has a building area not more than (i) 3 000 m2 if 1 storey in building height, or (ii) 2 400 m2 if 2 storeys in building height. | obc2019_divb | Div B | 3.2.2.56.(1) | 3.2.2.56. Group D, up to 2 Storeys, Sprinklered | A building classified as Group D is permitted to conform to Sentence (2) provided, except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered, it is not more than 2 storeys in building height, and it has a building area not more than, 3 000 m2 if 1 storey in building height, or 2 400 m2 if 2 storeys in building height. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.63.(1) | Group D, up to 6 Storeys | A building classified as Group D is permitted to conform to Sentence 3.2.2.56.(2) provided (a) it is not more than 6 storeys in building height, and (b) it has a building area not more than the value in Table 3.2.2.56. | obc2019_divb | Div B | 3.2.2.56.(1) 3.2.2.50.(1) | 3.2.2.50. Group D, up to 6 Storeys | A building classified as Group D is permitted to conform to Sentence (2) provided, (a) it is not more than 6 storeys in building height, and (b) it has a building area not more than the value in Table 3.2.2.50. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.63.(2) | Group D, up to 6 Storeys | The building referred to in Sentence 3.2.2.56.(1) shall be of noncombustible construction, and floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, mezzanines shall have a fire-resistance rating not less than 1 h, roof assemblies shall have a fire-resistance rating not less than 1 h, except that in a building not more than 1 storey in building height this requirement is waived, and loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. | obc2019_divb | Div B | 3.2.2.56.(2) 3.2.2.50.(2) | 3.2.2.50. Group D, up to 6 Storeys | The building referred to in Sentence (1) shall be of noncombustible construction, and, floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, mezzanines shall have a fire-resistance rating not less than 1 h, roof assemblies shall have a fire-resistance rating not less than 1 h, except that in a building not more than 1 storey in building height this requirement is waived, and loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.63.(2) | Group D, up to 2 Storeys, Sprinklered | The building referred to in Sentence 3.2.2.62.(1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, and loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall have a fire-resistance rating not less than 45 min, or be of noncombustible construction. | obc2019_divb | Div B | 3.2.2.56.(2) | 3.2.2.56. Group D, up to 2 Storeys, Sprinklered | The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and, floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, and loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall, have a fire-resistance rating not less than 45 min, or be of noncombustible construction. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.64.(1) | Group D, up to 6 Storeys, Sprinklered | A building classified as Group D is permitted to conform to Sentence 3.2.2.58.(2), provided (a) it is sprinklered throughout, (b) it is not more than 6 storeys in building height, (c) it has a height not more than 18 m measured between the floor of the first storey and the uppermost floor level that does not serve a rooftop enclosure for elevator machinery, a stairway or a service room used only for service to the building, and (d) it has a building area not more than (i) 18 000 m2 if 1 storey in building height, (ii) 9 000 m2 if 2 storeys in building height, (iii) 6 000 m2 if 3 storeys in building height, (iv) 4 500 m2 if 4 storeys in building height, (v) 3 600 m2 if 5 storeys in building height, or (vi) 3 000 m2 if 6 storeys in building height. | obc2019_divb | Div B | 3.2.2.57.(1) 3.2.2.50.(1) | 3.2.2.50A. Group D, up to 6 Storeys, Sprinklered, Combustible | A building classified as Group D is permitted to conform to Sentence (2) provided, (a) it is sprinklered, (b) it is not more than 6 storeys in building height, (c) it has a height of not more than 18 m, measured between the floor level of the first storey and the floor level of the uppermost storey or mezzanine that is not a rooftop enclosure, provided for elevator machinery, a stairway or a service room used for no purpose other than for service to the building, and (d) it has a building area of not more than, (i) 18 000 m2 if 1 storey in building height, (ii) 9 000 m2 if 2 storeys in building height, (iii) 6 000 m2 if 3 storeys in building height, (iv) 4 500 m2 if 4 storeys in building height, (v) 3 600 m2 if 5 storeys in building height, or (vi) 3 000 m2 if 6 storeys in building height. |  | Common Sentence | Yes | Mid-rise Wood
2015 | ON | NBC | Div B | 3.2.2.64.(1) | Group E, Any Height, Any Area, Sprinklered | Except as permitted by Sentences 3.2.2.7.(3) and (4) and Articles 3.2.2.65. to 3.2.2.69., a building classified as Group E shall conform to Sentence (2). | obc2019_divb | Div B | 3.2.2.57.(1) | 3.2.2.57. Group E, Any Height, Any Area, Sprinklered | Except as permitted by Articles 3.2.2.58. to 3.2.2.62., a building classified as Group E shall conform to Sentence (2). |  | Common Sentence | Yes | Mid-rise Wood
2015 | ON | NBC | Div B | 3.2.2.64.(2) | Group E, Any Height, Any Area, Sprinklered | Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building shall be sprinklered throughout, (b) floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h, (c) mezzanines shall have a fire-resistance rating not less than 1 h, and (d) loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. | obc2019_divb | Div B | 3.2.2.57.(2) | 3.2.2.57. Group E, Any Height, Any Area, Sprinklered | Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and, (a) except as permitted by Sentence 3.2.2.7.(1), the building shall be sprinklered, (b) floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h, (c) mezzanines shall have a fire-resistance rating not less 1 h, and (d) loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.64.(2) | Group D, up to 6 Storeys, Sprinklered | The building referred to in Sentence 3.2.2.58.(1) is permitted to be of combustible construction or noncombustible construction, used singly or in combination, and (a) floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, (b) roof assemblies shall have a fire-resistance rating not less than 1 h, (c) except as provided in Sentence 3.2.2.58.(3), where the roof assembly has a height greater than 25 m measured from the floor of the first storey to the highest point of the roof assembly, the roof assembly shall be constructed of noncombustible construction or fire-retardant-treated wood conforming to Article 3.1.4.5., (d) mezzanines shall have a fire-resistance rating not less than 1 h, and (e) loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. | obc2019_divb | Div B | 3.2.2.57.(2) 3.2.2.50.(2) | 3.2.2.50A. Group D, up to 6 Storeys, Sprinklered, Combustible | The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and, (a) floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, (b) roof assemblies shall have a fire-resistance rating not less than 1 h, (c) except as provided by Sentence (3), where the roof assembly has a height greater than 25 m measured from the floor level of the first storey to the highest point of the roof assembly, the roof assembly shall, (i) be of noncombustible construction, or (ii) be constructed of fire-retardant treated wood conforming to Article 3.1.4.5., (d) mezzanines shall have a fire-resistance rating not less than 1 h, (e) the fire separation of exits described in Sentence 3.4.4.1.(3) shall be of noncombustible construction, and (f) loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | Common Sentence | Yes | Mid-rise Wood
2015 | ON | NBC | Div B | 3.2.2.65.(1) | Group D, up to 6 Storeys, Sprinklered, Noncombustible | A building classified as Group D is permitted to conform to Sentence 3.2.2.57.(2) provided (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout, (b) it is not more than 6 storeys in building height, and (c) it has a building area (i) that is not limited if the building is not more than 2 storeys in building height, (ii) not more than 14400 m2 if 3 storeys in building height, (iii) not more than 10800 m2 if 4 storeys in building height, (iv) not more than 8640 m2 if 5 storeys in building height, or (v) not more than 7200 m2 if 6 storeys in building height. | obc2019_divb | Div B | 3.2.2.58.(1) 3.2.2.51.(1) | 3.2.2.51. Group D, up to 6 Storeys, Sprinklered, Noncombustible | A building classified as Group D is permitted to conform to Sentence (2) provided, (a) except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered, (b) it is not more than 6 storeys in building height, and (c) it has a building area, (i) that is not limited if the building is not more than 2 storeys in building height, (ii) not more than 14 400 m2 if 3 storeys in building height, (iii) not more than 10 800 m2 if 4 storeys in building height, (iv) not more than 8 640 m2 if 5 storeys in building height, or (v) not more than 7 200 m2 if 6 storeys in building height. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.65.(1) | Group E, up to 4 Storeys, Sprinklered | A building classified as Group E is permitted to conform to Sentence (2) provided (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout, (b) it is not more than 4 storeys in building height, and (c) it has a building area not more than 1 800 m2. | obc2019_divb | Div B | 3.2.2.58.(1) | 3.2.2.58. Group E, up to 4 Storeys, Sprinklered | A building classified as Group E is permitted to conform to Sentence (2) provided, (a) except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered, (b) it is not more than 4 storeys in building height, and (c) it has a building area not more than 1 800 m2. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.65.(2) | Group D, up to 6 Storeys, Sprinklered, Noncombustible | Except as permitted by Article 3.2.2.16., the building referred to in Sentence 3.2.2.75.(1) shall be of noncombustible construction, and floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, mezzanines shall have a fire-resistance rating not less than 1 h, and loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. | obc2019_divb | Div B | 3.2.2.58.(2) 3.2.2.51.(2) | 3.2.2.51. Group D, up to 6 Storeys, Sprinklered, Noncombustible | Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and, floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, mezzanines shall have a fire-resistance rating not less than 1 h, and loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.65.(2) | Group E, up to 4 Storeys, Sprinklered | The building referred to in Sentence 3.2.2.44.(1) is permitted to be of combustible construction or noncombustible construction, used singly or in combination, and floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, mezzanines shall have a fire-resistance rating not less than 1 h, and loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. | obc2019_divb | Div B | 3.2.2.58.(2) | 3.2.2.58. Group E, up to 4 Storeys, Sprinklered | The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and, floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, mezzanines shall have a fire-resistance rating not less than 1 h, and loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.66.(1) | Group D, up to 4 Storeys, Sprinklered | A building classified as Group D is permitted to conform to Sentence 3.2.2.59.(2) provided (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout, (b) it is not more than 4 storeys in building height, and (c) it has a building area not more than 3600 m2 . | obc2019_divb | Div B | 3.2.2.59.(1) 3.2.2.52.(1) | 3.2.2.52. Group D, up to 4 Storeys, Sprinklered | A building classified as Group D is permitted to conform to Sentence (2) provided, (a) except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered, (b) it is not more than 4 storeys in building height, and (c) it has a building area not more than 3 600 m2. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.66.(1) | Group E, up to 3 Storeys | A building classified as Group E is permitted to conform to Sentence (2) provided (a) it is not more than 3 storeys in building height, and (b) it has a building area not more than the value in Table 3.2.2.66. | obc2019_divb | Div B | 3.2.2.59.(1) | 3.2.2.59. Group E, up to 3 Storeys | A building classified as Group E is permitted to conform to Sentence (2) provided, it is not more than 3 storeys in building height, and it has a building area not more than the value in Table 3.2.2.59. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.66.(2) | Group E, up to 3 Storeys | The building referred to in Sentence 3.2.2.22.(1) is permitted to be of combustible construction or noncombustible construction used singly, or in combination, and floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min, mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall have a fire-resistance rating not less than 45 min, or be of noncombustible construction, and loadbearing walls, columns and arches supporting a fire separation shall have a fire-resistance rating not less than that required for the fire separation. | obc2019_divb | Div B | 3.2.2.59.(2) | 3.2.2.59. Group E, up to 3 Storeys | The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and, floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min, mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, roof assemblies shall have a fire-resistance rating not less than 45 min, except that in a building not more than 1 storey in building height, the fire-resistance rating is permitted to be waived provided the roof assembly is of noncombustible construction or is constructed as a fire-retardant treated wood roof system conforming to Article 3.1.14.1., loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall, have a fire-resistance rating not less than 45 min, or be of noncombustible construction, and loadbearing walls, columns and arches supporting a fire separation shall have a fire-resistance rating not less than that required for the fire separation. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.67.(1) | Group E, up to 3 Storeys, Sprinklered | A building classified as Group E is permitted to conform to Sentence 3.2.2.67.(2) provided (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout, (b) it is not more than 3 storeys in building height, and (c) it has a building area not more than (i) 7200 m2 if 1 storey in building height, (ii) 3600 m2 if 2 storeys in building height, or (iii) 2400 m2 if 3 storeys in building height. | obc2019_divb | Div B | 3.2.2.60.(1) | 3.2.2.60. Group E, up to 3 Storeys, Sprinklered | A building classified as Group E is permitted to conform to Sentence (2) provided, (a) except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered, (b) it is not more than 3 storeys in building height, and (c) it has a building area not more than, (i) 7 200 m2 if 1 storey in building height, (ii) 3 600 m2 if 2 storeys in building height, or (iii) 2 400 m2 if 3 storeys in building height. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.67.(2) | Group E, up to 3 Storeys, Sprinklered | The building referred to in Sentence 3.2.2.22.(1) is permitted to be of combustible construction or noncombustible construction used singly, or in combination, and floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min, mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall have a fire-resistance rating not less than 45 min, or be of noncombustible construction, and loadbearing walls, columns and arches supporting a fire separation shall have a fire-resistance rating not less than that required for the fire separation. | obc2019_divb | Div B | 3.2.2.60.(2) | 3.2.2.60. Group E, up to 3 Storeys, Sprinklered | The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and, floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min, mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall, have a fire-resistance rating not less than 45 min, or be of noncombustible construction, and loadbearing walls, columns and arches supporting a fire separation shall have a fire-resistance rating not less than that required for the fire separation. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.68.(1) | Group E, up to 2 Storeys | A building classified as Group E is permitted to conform to Sentence 3.2.2.68.(2) provided (a) it is not more than 2 storeys in building height, and (b) it has a building area not more than the value in Table 3.2.2.68. | obc2019_divb | Div B | 3.2.2.61.(1) | 3.2.2.61. Group E, up to 2 Storeys | A building classified as Group E is permitted to conform to Sentence (2) provided, it is not more than 2 storeys in building height, and it has a building area not more than the value in Table 3.2.2.61. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.68.(2) | Group E, up to 2 Storeys | The building referred to in Sentence 3.2.2.63.(1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, and loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall have a fire-resistance rating not less than 45 min, or be of noncombustible construction. | obc2019_divb | Div B | 3.2.2.61.(2) | 3.2.2.61. Group E, up to 2 Storeys | The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and, floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min, and loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.69.(1) | Group E, up to 2 Storeys, Sprinklered | A building classified as Group E is permitted to conform to Sentence (2) provided (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout, (b) it is not more than 2 storeys in building height, and (c) it has a building area not more than (i) 3 000 m2 if 1 storey in building height, or (ii) 1 800 m2 if 2 storeys in building height. | obc2019_divb | Div B | 3.2.2.62.(1) | 3.2.2.62. Group E, up to 2 Storeys, Sprinklered | A building classified as Group E is permitted to conform to Sentence (2) provided, (a) except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered, (b) it is not more than 2 storeys in building height, and (c) it has a building area not more than, (i) 3 000 m2 if 1 storey in building height, or (ii) 1 800 m2 if 2 storeys in building height. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.69.(2) | Group E, up to 2 Storeys, Sprinklered | The building referred to in Sentence 3.2.2.63.(1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, and loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall have a fire-resistance rating not less than 45 min, or be of noncombustible construction. | obc2019_divb | Div B | 3.2.2.62.(2) | 3.2.2.62. Group E, up to 2 Storeys, Sprinklered | The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and, floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min, and loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.7.(1) | Superimposed Major Occupancies | Except as provided in Article 3.2.2.8. and Sentence 3.2.2.18.(2), in a building in which one major occupancy is located entirely above another major occupancy, the requirements in this Subsection for each portion of the building containing a major occupancy shall apply to that portion as if the entire building were of that major occupancy. | obc2019_divb | Div B | 3.2.2.7.(1) | 3.2.2.7. Superimposed Major Occupancies | Except as permitted by Article 3.2.2.8. and Sentences 3.2.2.43A.(5) and 3.2.2.50A.(4), in a building in which one major occupancy is located entirely above another major occupancy, the requirements in this Subsection for each portion of the building containing a major occupancy shall apply to that portion as if the entire building was of that major occupancy. |  | Common Sentence | Yes | Mid-rise Wood
2015 | ON | NBC | Div B | 3.2.2.7.(2) | Superimposed Major Occupancies | If one major occupancy is located above another major occupancy, the fire-resistance rating of the floor assembly between the major occupancies shall be determined on the basis of the requirements of this Subsection for the lower major occupancy. (See also Article 3.1.3.1.) | obc2019_divb | Div B | 3.2.2.7.(2) | 3.2.2.7. Superimposed Major Occupancies | If one major occupancy is located above another major occupancy, the fire-resistance rating of the floor assembly between the major occupancies shall be determined on the basis of the requirements of this Subsection for the lower major occupancy. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.7.(3) | Superimposed Major Occupancies | A building that is wholly constructed in accordance with the building area and construction requirements of Article 3.2.2.50. shall not contain (a) Group A, Division 2 and Group E major occupancies above the second storey, or (b) a storage garage above the third storey (see also Sentence 4.4.2.1.(1)). | obc2019_divb | Div B | 3.2.2.43.(5) | 3.2.2.43A. Group C, up to 6 Storeys, Sprinklered, Combustible | Group A, Division 2 major occupancies, Group E major occupancies and storage garages located in a building within the scope of this Article are permitted to be constructed in accordance with this Article provided they are located below the third storey of the building. (See Appendix A.) |  | Common Sentence | Yes | Mid-rise Wood
2015 | ON | NBC | Div B | 3.2.2.7.(4) | Superimposed Major Occupancies | A building that is wholly constructed in accordance with the building area and construction requirements of Article 3.2.2.58. shall no tcontain (a) Group A, Division 2,Group E, and Group F, Division 2 or 3 major occupancies above the second storey, or (b) a storage garage above the third storey (see also Sentence 4.4.2.1.(1)). | obc2019_divb | Div B | 3.2.2.50.(4) | 3.2.2.50A. Group D, up to 6 Storeys, Sprinklered, Combustible | Group A, Division 2 major occupancies, Group E major occupancies and storage garages located in a building within the scope of this Article are permitted to be constructed in accordance with this Article provided they are located below the third storey of the building. (See Appendix A.) |  | Common Sentence | Yes | Mid-rise Wood
2015 | ON | NBC | Div B | 3.2.2.70.(1) | Group F, Division 1, up to 4 Storeys, Sprinklered | Except as permitted by Articles 3.2.2.71. to 3.2.2.73., a building classified as Group F, Division 1 shall conform to Sentence 3.2.2.70.(2) provided (a) it is not more than 4 storeys in building height, and (b) it has a building area not more than (i) 9000 m2 if 1 storey in building height, (ii) 4500 m2 if 2 storeys in building height, (iii) 3000 m2 if 3 storeys in building height, or (iv) 2250 m2 if 4 storeys in building height. | obc2019_divb | Div B | 3.2.2.63.(1) | 3.2.2.63. Group F, Division 1, up to 4 Storeys, Sprinklered | Except as permitted by Articles 3.2.2.64. to 3.2.2.66., a building classified as Group F, Division 1 shall conform to Sentence (2) provided, (a) it is not more than 4 storeys in building height, and (b) it has a building area not more than, (i) 9 000 m2 if 1 storey in building height, (ii) 4 500 m2 if 2 storeys in building height, (ii) 3 000 m2 if 3 storeys in building height, or (iv) 2 250 m2 if 4 storeys in building height. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.70.(2) | Group F, Division 1, up to 4 Storeys, Sprinklered | Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building shall be sprinklered throughout, (b) floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h, (c) mezzanines shall have a fire-resistance rating not less than 1 h, and (d) loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. | obc2019_divb | Div B | 3.2.2.63.(2) | 3.2.2.63. Group F, Division 1, up to 4 Storeys, Sprinklered | Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and, (a) except as permitted by Sentence 3.2.2.7.(1), the building shall be sprinklered, (b) floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h, (c) mezzanines shall have a fire-resistance rating not less than 1 h, and (d) loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.71.(1) | Group F, Division 1, up to 3 Storeys, Sprinklered | A building classified as Group F, Division 1 is permitted to conform to Sentence 3.2.2.71.(2) provided (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout, (b) it is not more than 3 storeys in building height, and (c) it has a building area not more than (i) 3600 m2 if 1 storey in building height, (ii) 1800 m2 if 2 storeys in building height, or (iii) 1200 m2 if 3 storeys in building height. | obc2019_divb | Div B | 3.2.2.64.(1) | 3.2.2.64. Group F, Division 1, up to 3 Storeys, Sprinklered | A building classified as Group F, Division 1 is permitted to conform to Sentence (2) provided, (a) except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered, (b) it is not more than 3 storeys in building height, and (c) it has a building area not more than, (i) 3 600 m2 if 1 storey in building height, (ii) 1 800 m2 if 2 storeys in building height, or (iii) 1 200 m2 if 3 storeys in building height. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.71.(2) | Group F, Division 1, up to 3 Storeys, Sprinklered | The building referred to in Sentence 3.2.2.71.(1) is permitted to be of heavy timber construction or noncombustible construction used singly or in combination, and floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min, and loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. | obc2019_divb | Div B | 3.2.2.64.(2) | 3.2.2.64. Group F, Division 1, up to 3 Storeys, Sprinklered | The building referred to in Sentence (1) is permitted to be of heavy timber construction or noncombustible construction used singly or in combination, and, floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min, loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.72.(1) | Group F, Division 1, up to 2 Storeys, Sprinklered | A building classified as Group F, Division 1 is permitted to conform to Sentence (2) provided (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout, (b) it is not more than 2 storeys in building height, and (c) it has a building area not more than (i) 2 400 m2 if 1 storey in building height, or (ii) 1 200 m2 if2 storeys in building height. | obc2019_divb | Div B | 3.2.2.65.(1) | 3.2.2.65. Group F, Division 1, up to 2 Storeys, Sprinklered | A building classified as Group F, Division 1 is permitted to conform to Sentence (2) provided, (a) except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered, (b) it is not more than 2 storeys in building height, and (c) it has a building area not more than, (i) 2 400 m2 if 1 storey in building height, or (ii) 1 200 m2 if 2 storeys in building height. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.72.(2) | Group F, Division 1, up to 2 Storeys, Sprinklered | The building referred to in Sentence 3.2.2.62.(1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, and loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall have a fire-resistance rating not less than 45 min, or be of noncombustible construction. | obc2019_divb | Div B | 3.2.2.65.(2) | 3.2.2.65. Group F, Division 1, up to 2 Storeys, Sprinklered | The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and, floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall, have a fire-resistance rating not less than 45 min, or be of noncombustible construction. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.73.(1) | Group F, Division 1, One Storey | A building classified as Group F, Division 1 is permitted to be of combustible construction or noncombustible construction used singly or in combination provided it is not more than 1 storey in building height, and it has a building area not more than 800 m2. | obc2019_divb | Div B | 3.2.2.66.(1) | 3.2.2.59. Group E, up to 3 Storeys | A building classified as Group E is permitted to conform to Sentence (2) provided, it is not more than 3 storeys in building height, and it has a building area not more than the value in Table 3.2.2.59. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.74.(1) | Group F, Division 2, Any Height, Any Area, Sprinklered | Except as permitted by Sentence 3.2.2.7.(4) and Articles 3.2.2.75. to 3.2.2.79., a building classified as Group F , Division 2 shall conform to Sentence (2). | obc2019_divb | Div B | 3.2.2.67.(1) | 3.2.2.67. Group F, Division 2, Any Height, Any Area, Sprinklered | Except as permitted by Articles 3.2.2.68. to 3.2.2.72., a building classified as Group F, Division 2 shall conform to Sentence (2). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.74.(2) | 3.2.2.67. Group F, Division 2, Any Height, Any Area, Sprinklered | Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building shall be sprinklered throughout, (b) floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h, (c) mezzanines shall have a fire-resistance rating not less than 1 h, and (d) loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. | obc2019_divb | Div B | 3.2.2.67.(2) | 3.2.2.67. Group F, Division 2, Any Height, Any Area, Sprinklered | Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and, (a) except as permitted by Sentence 3.2.2.7.(1), the building shall be sprinklered, (b) floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h, (c) mezzanines shall have a fire-resistance rating not less 1 h, and (d) loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.75.(1) | Group F, Division 2, up to 4 Storeys, Increased Area, Sprinklered | A building classified as Group F, Division 2 is permitted to conform to Sentence (2) provided (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout, (b) it is not more than 4 storeys in building height, and (c) it has a building area not more than (i) 18 000 m2 if1 storey in building height, (ii) 9 000 m2 if2 storeys in building height, (iii) 6 000 m2 if 3 storeys in building height, or (iv) 4 500 m2 if 4 storeys in building height. | obc2019_divb | Div B | 3.2.2.69.(1) | 3.2.2.69. Group F, Division 2, up to 4 Storeys, Increased Area | A building classified as Group F, Division 2 is permitted to conform to Sentence (2) provided, (a) it is not more than 4 storeys in building height, and (b) it has a building area not more than the value in Table 3.2.2.69.A. or Table 3.2.2.69.B. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.75.(2) | Group F, Division 2, up to 4 Storeys, Increased Area, Sprinklered | The building referred to in Sentence 3.2.2.81.(1) shall be of noncombustible construction, and floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, mezzanines shall have a fire-resistance rating not less than 1 h, roof assemblies shall have a fire-resistance rating not less than 1 h, and loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. | obc2019_divb | Div B | 3.2.2.69.(2) | 3.2.2.69. Group F, Division 2, up to 4 Storeys, Increased Area | Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and, floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, mezzanines shall have a fire-resistance rating not less than 1 h, if the building is not sprinklered, roof assemblies shall have a fire-resistance rating not less than 1 h, and loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.77.(1) | Group F, Division 2, up to 4 Storeys, Sprinklered | A building classified as Group F, Division 2 is permitted to conform to Sentence (2) provided (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout, (b) it is not more than 4 storeys in building height, and (c) it has a building area not more than (i) 9 600 m2 if 1 storey in building height, (ii) 4 800 m2 if2 storeys in building height, (iii) 3 200 m2 if 3 storeys in building height, or (iv) 2 400 m2 if 4 storeys in building height. | obc2019_divb | Div B | 3.2.2.70.(1) | 3.2.2.70. Group F, Division 2, up to 4 Storeys | A building classified as Group F, Division 2 is permitted to conform to Sentence (2) provided, (a) it is not more than 4 storeys in building height, and (b) it has a building area not more than the value in Table 3.2.2.70.A. or Table 3.2.2.70.B. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.77.(2) | Group F, Division 2, up to 4 Storeys, Sprinklered | The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and (a) floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min, (b) mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, (c) loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall (i) have a fire-resistance rating not less than 45 min, or (ii) be of noncombustible construction, and (d) loadbearing walls, columns and arches supporting a fire separation shall have a fire-resistance rating not less than that required for the fire separation. | obc2019_divb | Div B | 3.2.2.70.(2) | 3.2.2.70. Group F, Division 2, up to 4 Storeys | The building referred to in Sentence (1) shall be of combustible construction or noncombustible construction used singly or in combination, and, (a) floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min,(b) mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, (c) if the building is not sprinklered, roof assemblies shall have, if of combustible construction, a fire-resistance rating not less than 45 min, except that in buildings not more than 1 storey in building height, the fire-resistance rating is permitted to be waived provided the roof assembly is constructed as a fire-retardant treated wood roof system conforming to Article 3.1.14.1., and the building area is not more than, (i) 1 600 m2 if facing one street, (ii) 2 000 m2 if facing two streets, or (iii) 2 400 m2 if facing three streets, (d) loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall, (i) have a fire-resistance rating not less than 45 min, or (ii) be of noncombustible construction, and (e) loadbearing walls, columns and arches supporting a fire separation shall have a fire-resistance rating not less than that required for the supported assembly. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.78.(1) | Group F, Division 2, up to 2 Storeys | A building classified as Group F, Division 2 is permitted to conform to Sentence (2) provided (a) it is not more than 2 storeys in building height, and (b) it has a building area not more than the value in Table 3.2.2.78. | obc2019_divb | Div B | 3.2.2.71.(1) | 3.2.2.71. Group F, Division 2, up to 2 Storeys | A building classified as Group F, Division 2 is permitted to conform to Sentence (2) provided, (a) it is not more than 2 storeys in building height, and (b) it has a building area not more than the value in Table 3.2.2.71. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.78.(2) | Group F, Division 2, up to 2 Storeys | The building referred to in Sentence 3.2.2.62.(1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, and loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall have a fire-resistance rating not less than 45 min, or be of noncombustible construction. | obc2019_divb | Div B | 3.2.2.71.(2) | 3.2.2.71. Group F, Division 2, up to 2 Storeys | (2) The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and, floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, and loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall, have a fire-resistance rating not less than 45 min, or be of noncombustible construction. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.79.(1) | Group F, Division 2, up to 2 Storeys, Sprinklered | A building classified as Group F, Division 2 is permitted to conform to Sentence (2) provided (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout, (b) it is not more than 2 storeys in building height, and (c) it has a building area not more than (i) 4 500 m2 if 1 storey in building height, or (ii) 1 800 m2 if 2 storeys in building height | obc2019_divb | Div B | 3.2.2.72.(1) | 3.2.2.72. Group F, Division 2, up to 2 Storeys, Sprinklered | A building classified as Group F, Division 2 is permitted to conform to Sentence (2) provided, (a) except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered, (b) it is not more than 2 storeys in building height, and (c) it has a building area not more than, (i) 4 500 m2 if 1 storey in building height, or (ii) 1 800 m2 if 2 storeys in building height. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.79.(2) | Group F, Division 2, up to 2 Storeys, Sprinklered | The building referred to in Sentence 3.2.2.62.(1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, and loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall have a fire-resistance rating not less than 45 min, or be of noncombustible construction. | obc2019_divb | Div B | 3.2.2.72.(2) | 3.2.2.72. Group F, Division 2, up to 2 Storeys, Sprinklered | The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and, floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, and loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall, have a fire-resistance rating not less than 45 min, or be of noncombustible construction. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.8.(1) | Exceptions for Major Occupancies | In a building in which the aggregate area of all major occupancies in a particular Group or Division is not more than 10% of the floor area of the storey in which they are located, these major occupancies need not be considered as major occupancies for the purposes of this Subsection, provided they are not classified as Group F, Division 1 or 2 occupancies. | obc2019_divb | Div B | 3.2.2.8.(1) | 3.2.2.8. Exceptions for Major Occupancies | In a building in which the aggregate area of all major occupancies in a particular Group or Division is not more than 10% of the floor area of the storey in which they are located, these major occupancies need not be considered as major occupancies for the purposes of this Subsection, provided they are not classified as Group F, Division 1 or 2 occupancies. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.80.(1) | Group F, Division 3, Any Height, Any Area | Except as permitted by Sentences 3.2.2.7.(3) and (4) and Articles 3.2.2.81 to 3.2.2.90.,a building classified as Group F, Division 3 shall conform to Sentence (2). | obc2019_divb | Div B | 3.2.2.73.(1) | 3.2.2.73. Group F, Division 3, Any Height, Any Area | Except as permitted by Articles 3.2.2.74. to 3.2.2.83., a building classified as Group F, Division 3 shall conform to Sentence (2). |  | Common Sentence | Yes | Mid-rise Wood
2015 | ON | NBC | Div B | 3.2.2.80.(2) | Group F, Division 3, Any Height, Any Area | Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building shall be sprinklered throughout, (b) floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h, except that floor assemblies are permitted to be fire separations with a fire-resistance rating not less than 1 h in a storage garage with all storeys constructed as open-air storeys, (c) mezzanines shall have a fire-resistance rating not less than 1 h, and (d) loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. | obc2019_divb | Div B | 3.2.2.73.(2) | 3.2.2.73. Group F, Division 3, Any Height, Any Area | Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and, (a) except as permitted by Sentence 3.2.2.7.(1), the building shall be sprinklered if it is regulated by Subsection 3.2.6., (b) floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h, except that floor assemblies are permitted to be fire separations with a fire-resistance rating not less than 1 h in a storage garage with all storeys constructed as open-air storeys, (c) mezzanines shall have a fire-resistance rating not less 1 h, (d) if the building is not sprinklered, roof assemblies shall have a fire-resistance rating not less than 1 h, and (e) loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.81.(1) | Group F, Division 3, up to 6 Storeys | Except as permitted by Sentences 3.2.2.7.(3) and (4), a building classified as Group F, Division 3 is permitted to conform to Sentence (2) provided (a) it is not more than 6 storeys in building height, and (b) it has a building area not more than the value in Table 3.2.2.81. | obc2019_divb | Div B | 3.2.2.74.(1) | 3.2.2.74. Group F, Division 3, up to 6 Storeys | A building classified as Group F, Division 3 is permitted to conform to Sentence (2) provided, (a) it is not more than 6 storeys in building height, and (b) it has a building area not more than the value in Table 3.2.2.74. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.81.(2) | Group F, Division 3, up to 6 Storeys | The building referred to in Sentence 3.2.2.81.(1) shall be of noncombustible construction, and floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, mezzanines shall have a fire-resistance rating not less than 1 h, roof assemblies shall have a fire-resistance rating not less than 1 h, and loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. | obc2019_divb | Div B | 3.2.2.74.(2) | 3.2.2.74. Group F, Division 3, up to 6 Storeys | (2) The building referred to in Sentence (1) shall be of noncombustible construction, and, floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, mezzanines shall have a fire-resistance rating not less than 1 h, roof assemblies shall have a fire-resistance rating not less than 1 h, and loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.82.(1) | Group F, Division 3, up to 6 Storeys, Sprinklered | Except as permitted by Sentences 3.2.2.7.(3) and 3.2.2.7.(4), a building classified as Group F, Division 3 is permitted to conform to Sentence 3.2.2.82.(2) provided (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout, (b) it is not more than 6 storeys in building height, and (c) it has a building area (i) that is not limited if the building is not more than 1 storey in building height, (ii)not more than 21 600 m2 if 2 storeys in building height, (iii) not more than 14 400 m2 if 3 storeys in building height, (iv) not more than 10 800 m2 if 4 storeys in building height, (v) not more than 8 640 m2 if 5 storeys in building height, or (vi) not more than 7 200 m2 if 6 storeys in building height. | obc2019_divb | Div B | 3.2.2.75.(1) | 3.2.2.75. Group F, Division 3, up to 6 Storeys, Sprinklered | A building classified as Group F, Division 3 is permitted to conform to Sentence (2) provided, (a) except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered, (b) it is not more than 6 storeys in building height, and (c) it has a building area, (i) that is not limited if the building is not more than 1 storey in building height, (ii) not more than 21 600 m2 if 2 storeys in building height, (iii) not more than 14 400 m2 if 3 storeys in building height, (iv) not more than 10 800 m2 if 4 storeys in building height, (v) not more than 8 640 m2 if 5 storeys in building height, or (v) not more than 7 200 m2 if 6 storeys in building height. |  | Common Sentence | Yes | Mid-rise Wood
2015 | ON | NBC | Div B | 3.2.2.83.(1) | Group F, Division 3, up to 4 Storeys | A building classified as Group F, Division 3 is permitted to conform to Sentence (2) provided (a) it is not more than 4 storeys in building height, and (b) it has a building area not more than the value in Table 3.2.2.83. | obc2019_divb | Div B | 3.2.2.76.(1) | 3.2.2.76. Group F, Division 3, up to 4 Storeys | A building classified as Group F, Division 3 is permitted to conform to Sentence (2) provided, (a) it is not more than 4 storeys in building height, and (b) it has a building area not more than the value in Table 3.2.2.76. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.83.(2) | Group F, Division 3, up to 4 Storeys | The building referred to in Sentence 3.2.2.60.(1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, roof assemblies shall have, if of combustible construction, a fire-resistance rating not less than 45 min, except that in a building not more than 1 storey in building height, the fire-resistance rating is permitted to be waived provided the roof assembly is constructed as a fire-retardant-treated wood roof system conforming to Article 3.1.14.1. and the building area is not more than 2?400 m2 if facing one street, 3?000 m2 if facing 2 streets, or 3?600 m2 if facing 3 streets, and loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall have a fire-resistance rating not less than 45 min, or be of noncombustible construction. | obc2019_divb | Div B | 3.2.2.76.(2) | 3.2.2.76. Group F, Division 3, up to 4 Storeys | The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and, floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, roof assemblies shall have, if of combustible construction, a fire-resistance rating not less than 45 min, except that in a building not more than 1 storey in building height, the fire-resistance rating is permitted to be waived provided the roof assembly is constructed as a fire-retardant treated wood roof system conforming to Article 3.1.14.1., and the building area is not more than, 2 400 m2 if facing one street, 3 000 m2 if facing two streets, or 3 600 m2 if facing three streets, and loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall, have a fire-resistance rating not less than 45 min, or be of noncombustible construction. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.84.(1) | Group F, Division 3, up to 4 Storeys, Sprinklered | A building classified as Group F, Division 3 is permitted to conform to Sentence (2) provided (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout, (b) it is not more than 4 storeys in building height, and (c) it has a building area not more than (i) 14 400 m2 if 1 storey in building height, (ii) 7 200 m2 if 2 storeys in building height, (iii) 4 800 m2 if 3 storeys in building height, or (iv) 3 600 m2 if 4 storeys in building height. | obc2019_divb | Div B | 3.2.2.77.(1) | 3.2.2.77. Group F, Division 3, up to 4 Storeys, Sprinklered | A building classified as Group F, Division 3 is permitted to conform to Sentence (2) provided, (a) except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered, (b) it is not more than 4 storeys in building height, and (c) it has a building area not more than, (i) 14 400 m2 if 1 storey in building height, (ii) 7 200 m2 if 2 storeys in building height, (iii) 4 800 m2 if 3 storeys in building height, or (iv) 3 600 m2 if 4 storeys in building height. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.84.(2) | Group F, Division 3, up to 4 Storeys, Sprinklered | The building referred to in Sentence 3.2.2.26.(1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, and loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall have a fire-resistance rating not less than 45 min, or be of noncombustible construction. | obc2019_divb | Div B | 3.2.2.77.(2) | 3.2.2.77. Group F, Division 3, up to 4 Storeys, Sprinklered | The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and, floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, and loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall, have a fire-resistance rating not less than 45 min, or be of noncombustible construction. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.85.(1) | Group F, Division 3, up to 2 Storeys | A building classified as Group F, Division 3 is permitted to conform to Sentence (2) provided (a) it is not more than 2 storeys in building height, and (b) it has a building area not more than the value in Table 3.2.2.85. | obc2019_divb | Div B | 3.2.2.78.(1) | 3.2.2.78. Group F, Division 3, up to 2 Storeys | A building classified as Group F, Division 3 is permitted to conform to Sentence (2) provided, (a) it is not more than 2 storeys in building height, and (b) it has a building area not more than the value in Table 3.2.2.78. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.85.(2) | Group F, Division 3, up to 2 Storeys | The building referred to in Sentence 3.2.2.62.(1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, and loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall have a fire-resistance rating not less than 45 min, or be of noncombustible construction. | obc2019_divb | Div B | 3.2.2.78.(2) | 3.2.2.78. Group F, Division 3, up to 2 Storeys | (2) The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and, floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall, have a fire-resistance rating not less than 45 min, or be of noncombustible construction. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.86.(1) | Group F, Division 3, up to 2 Storeys, Sprinklered | A building classified as Group F, Division 3 is permitted to conform to Sentence (2) provided (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout, (b) it is not more than 2 storeys in building height, and (c) it has a building area not more than (i) 7 200 m2 if 1 storey in building height, or (ii) 2 400 m2 if2 storeys in building height. | obc2019_divb | Div B | 3.2.2.79.(1) | 3.2.2.79. Group F, Division 3, up to 2 Storeys, Sprinklered | A building classified as Group F, Division 3 is permitted to conform to Sentence (2) provided, (a) except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered, (b) it is not more than 2 storeys in building height, and (c) it has a building area not more than, (i) 7 200 m2 if 1 storey in building height, or (ii) 2 400 m2 if 2 storeys in building height. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.86.(2) | Group F, Division 3, up to 2 Storeys, Sprinklered | The building referred to in Sentence 3.2.2.62.(1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, and loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall have a fire-resistance rating not less than 45 min, or be of noncombustible construction. | obc2019_divb | Div B | 3.2.2.79.(2) | 3.2.2.79. Group F, Division 3, up to 2 Storeys, Sprinklered | The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and, floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall, have a fire-resistance rating not less than 45 min, or be of noncombustible construction. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.87.(1) | Group F, Division 3, One Storey | A building classified as Group F, Division 3 is permitted to be of heavy timber construction or noncombustible construction used singly or in combination provided (a) it is not more than 1 storey in building height, and (b) it has a building area not more than (i) 5?600 m2 if facing one street, (ii) 7?000 m2 if facing 2 streets, or (iii) 8?400 m2 if facing 3 streets. | obc2019_divb | Div B | 3.2.2.80.(1) | 3.2.2.80. Group F, Division 3, 1 Storey | A building classified as Group F, Division 3 is permitted to be of heavy timber construction or noncombustible construction used singly or in combination provided, (a) it is not more than 1 storey in building height, and (b) it has a building area not more than, (i) 600 m2 if facing one street, (ii) 7 000 m2 if facing two streets, or (iii) 8 400 m2 if facing three streets. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.88.(1) | Group F, Division 3, One Storey, Sprinklered | A building classified as Group F, Division 3 is permitted to be of heavy timber construction or noncombustible construction used singly or in combination provided (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout, (b) it is not more than 1 storey in building height, and (c) it has a building area not more than 16?800 m2 . | obc2019_divb | Div B | 3.2.2.81.(1) | 3.2.2.81. Group F, Division 3, 1 Storey, Sprinklered | A building classified as Group F, Division 3 is permitted to be of heavy timber construction or noncombustible construction used singly or in combination provided, (a) except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered, (b) it is not more than 1 storey in building height, and (c) it has a building area not more than 16 800 m2. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.89.(1) | Group F, Division 3, One Storey, Any Area, Low Fire Load Occupancy | A building classified as Group F, Division 3 is permitted to conform to Sentence 3.2.2.89.(2) provided it is not more than 1 storey in building height, used solely for low fire load occupancies such as power generating plants, or plants for the manufacture or storage of noncombustible materials, and not limited in building area. | obc2019_divb | Div B | 3.2.2.82.(1) | 3.2.2.82. Group F, Division 3, 1 Storey, Any Area, Low Fire Load Occupancy | A building classified as Group F, Division 3 is permitted to conform to Sentence (2) provided it is, not more than 1 storey in building height, used solely for low fire load occupancies such as, power generating plants, or plants for the manufacture or storage of noncombustible materials, and not limited in building area. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.89.(2) | Group F, Division 3, One Storey, Any Area, Low Fire Load Occupancy | The building referred to in Sentence 3.2.2.89.(1) shall be of noncombustible construction. | obc2019_divb | Div B | 3.2.2.82.(2) | 3.2.2.82. Group F, Division 3, 1 Storey, Any Area, Low Fire Load Occupancy | The building referred to in Sentence (1) shall be of noncombustible construction. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.9.(1) | Crawl Spaces | For the purposes of Articles 3.1.11.6. , 3.2.1.4. and 3.2.1.5., a crawl space shall be considered as a basement if it is (a) more than 1.8 m high between the lowest part of the floor assembly and the ground or other surface below, (b) used for any occupancy, (c) used for the passage of flue pipes, or (d) used as a plenum in combustible construction. | obc2019_divb | Div B | 3.2.2.9.(1) | 3.2.2.9. Crawl Spaces | For the purposes of Articles 3.2.1.4. and 3.2.1.5., a crawl space shall be considered as a basement if it is, (a) more than 1 800 mm high between the lowest part of the floor assembly and the ground or other surface below, (b) used for any occupancy, (c) used for the passage of flue pipes, or (d) used as a plenum in combustible construction. |  | Common Sentence | No | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.9.(2) | Crawl Spaces | A floor assembly immediately above a crawl space is not required to be constructed as a fire separation and is not required to have a fire-resistance rating provided the crawl space is not required to be considered as a basement by Sentence 3.2.2.9.(1). | obc2019_divb | Div B | 3.2.2.9.(2) | 3.2.2.9. Crawl Spaces | A floor assembly immediately above a crawl space is not required to be constructed as a fire separation and is not required to have a fire-resistance rating provided the crawl space is not required to be considered as a basement by Sentence (1). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.2.90.(1) | Group F, Division 3, Storage Garages up to 22 m High | A building used as a storage garage with all storeys constructed as open-air storeys and having no other occupancy above it is permitted to have its floor, wall, ceiling and roof assemblies constructed without a fire-resistance rating provided it is of noncombustible construction, not more than 22 m high, measured between grade and the ceiling level of the top storey, not more than 10?000 m2 in building area, and designed so that every portion of each floor area is within 60 m of an exterior wall opening. (See Note A-3.2.3.) | obc2019_divb | Div B | 3.2.2.83.(1) | 3.2.2.76. Group F, Division 3, up to 4 Storeys | A building classified as Group F, Division 3 is permitted to conform to Sentence (2) provided, it is not more than 4 storeys in building height, and it has a building area not more than the value in Table 3.2.2.76. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.1.(1) | Limiting Distance and Area of Unprotected Openings | Except as permitted by Articles 3.2.3.10. to 3.2.3.12., the area of unprotected openings in an exposing building face for the applicable limiting distance shall be not more than the value determined in accordance with Table 3.2.3.1.-B or 3.2.3.1.-C for an exposing building face conforming to Article 3.2.3.2. of a building or fire compartment which is not sprinklered, or Table 3.2.3.1.-D or 3.2.3.1.-E for an exposing building face conforming to Article 3.2.3.2. of a sprinklered fire compartment that is part of a building which is sprinklered in conformance with part 3. | obc2019_divb | Div B | 3.2.3.1.(1) | 3.2.3.1. Limiting Distance and Area of Unprotected Openings | Except as permitted by Articles 3.2.3.10. to 3.2.3.12., the area of unprotected openings in an exposing building face for the applicable limiting distance shall be not more than the value determined in accordance with, Table 3.2.3.1.B. or Table 3.2.3.1.C. for an exposing building face conforming to Article 3.2.3.2. of a building or fire compartment that is not sprinklered, or Table 3.2.3.1.D. or Table 3.2.3.1.E. for an exposing building face conforming to Article 3.2.3.2. of a sprinklered fire compartment that is part of a building that is sprinklered in conformance with Section 3.2. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.1.(10) | Limiting Distance and Area of Unprotected Openings | Unless a closure used to protect an opening in an exposing building face has a protective performance equivalent to that required for the wall assembly in which it is located, an equivalent area of unprotected opening, determined in accordance with the procedures of Sentence 3.2.3.1.(9) shall be added to the greater of the actual area of unprotected openings, or the corrected area of unprotected openings. | obc2019_divb | Div B | 3.2.3.1.(10) | 3.2.3.1. Limiting Distance and Area of Unprotected Openings | Unless a closure used to protect an opening in an exposing building face has a protective performance equivalent to that required for the wall assembly in which it is located, an equivalent area of unprotected opening, determined in accordance with the procedures of Sentence (9) shall be added to the greater of, the actual area of unprotected openings, or the corrected area of unprotected openings. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.1.(2) | Limiting Distance and Area of Unprotected Openings | The area of the unprotected openings in an exposing building face shall be the aggregate area of unprotected openings expressed as a percentage of the area of the exposing building face in Table 3.2.3.1.-B , 3.2.3.1.-C , 3.2.3.1.-D or 3.2.3.1.-E. (See Sentence 3.2.3.2.(1).) | obc2019_divb | Div B | 3.2.3.1.(2) | 3.2.3.1. Limiting Distance and Area of Unprotected Openings | The area of the unprotected openings in an exposing building face shall be the aggregate area of unprotected openings expressed as a percentage of the area of the exposing building face in Table 3.2.3.1.B., Table 3.2.3.1.C., Table 3.2.3.1.D. or Table 3.2.3.1.E. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.1.(3) | Limiting Distance and Area of Unprotected Openings | For the purpose of determining the type of construction and cladding and the fire-resistance rating of an exterior wall, the exposing building face shall be taken as the projection of the exterior wall onto a vertical plane located so that no portion of the exterior wall of the building or of a fire compartment, if the fire compartment complies with the requirements of Article 3.2.3.2., is between the vertical plane and the line to which the limiting distance is measured, and the area of unprotected openings shall be determined from Table 3.2.3.1.-B , 3.2.3.1.-C , 3.2.3.1.-D or 3.2.3.1.-E. | obc2019_divb | Div B | 3.2.3.1.(3) | 3.2.3.1. Limiting Distance and Area of Unprotected Openings | For the purpose of determining the type of construction and cladding and the fire-resistance rating of an exterior wall, the exposing building face shall be taken as the projection of the exterior wall onto a vertical plane located so that no portion of the exterior wall of the building or of a fire compartment, if the fire compartment complies with the requirements of Article 3.2.3.2., is between the vertical plane and the line to which the limiting distance is measured, and the area of unprotected openings shall be determined from Table 3.2.3.1.B., Table 3.2.3.1.C., Table 3.2.3.1.D. or Table 3.2.3.1.E. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.1.(4) | Limiting Distance and Area of Unprotected Openings | For the purpose of determining the actual percentage of unprotected openings permitted in an exterior wall, the location of the exposing building face is permitted to be taken at a vertical plane located so that there are no unprotected openings between the vertical plane and the line to which the limiting distance is measured. (See Note A-3.2.3.1.(4).) | obc2019_divb | Div B | 3.2.3.1.(4) | 3.2.3.1. Limiting Distance and Area of Unprotected Openings | For the purpose of determining the actual percentage of unprotected openings permitted in an exterior wall, the location of the exposing building face is permitted to be taken at a vertical plane located so that there are no unprotected openings between the vertical plane and the line to which the limiting distance is measured. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.1.(5) | Limiting Distance and Area of Unprotected Openings | Except for buildings that are sprinklered, where the limiting distance is 2 m or less, individual unprotected openings in an exposing building face shall be no greater than the area stated in Table 3.2.3.1.-A, or where the limiting distance is equal to or greater than 1.2 m, the area calculated by Area=0.24 2Ã—LD-1.22whereArea= area of the unprotected opening, and LD= limiting distance. | obc2019_divb | Div B | 3.2.3.1.(5) | 3.2.3.1. Limiting Distance and Area of Unprotected Openings | Except for buildings that are sprinklered, where the limiting distance is 2 m or less, the area of each individual unprotected opening in an exposing building face shall not be greater than, the area in Table 3.2.3.1.A., or for a limiting distance equal to or greater than 1.2 m, the area calculated as follows: Area = 0.24 [(2 x LD) - 1.2]2 where, Area = area of the unprotected opening in m2, and LD = limiting distance in m. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.1.(6) | Limiting Distance and Area of Unprotected Openings | The spacing between individual unprotected openings described in Sentence 3.2.3.1.(5) that serve a single room or space described in Sentence 3.2.3.1.(7) shall not be less than 2 m horizontally of another unprotected opening that is on the same exposing building face and serves the single room or space, or 2 m vertically of another unprotected opening that serves the single room or space, or another room or space on the same storey. | obc2019_divb | Div B | 3.2.3.1.(6) | 3.2.3.1. Limiting Distance and Area of Unprotected Openings | The distance between individual unprotected openings described in Sentence (5) that serve a single room or space described in Sentence (7) shall not be less than, 2 m measured horizontally where the unprotected openings are on the same exposing building face, or 2 m measured vertically where the unprotected openings both serve, the single room or space, or another room or space on the same storey. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.1.(7) | Limiting Distance and Area of Unprotected Openings | For the purpose of Sentence 3.2.3.1.(6), "single room or space" shall mean two or more adjacent spaces having a full-height separating wall extending less than 1.5 m from the interior face of the exterior wall, or two or more stacked spaces that are on the same storey. | obc2019_divb | Div B | 3.2.3.1.(7) | 3.2.3.1. Limiting Distance and Area of Unprotected Openings | For the purpose of Sentence (6), "single room or space" means a room or space that, is not divided by a wall, is divided by, a wall that extends less than 1.5 m from the interior face of the exterior wall, or a partial height wall, or consists of two or more stacked spaces that are on the same storey. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.3.1.(8) | Limiting Distance and Area of Unprotected Openings | A limiting distance equal to half the actual limiting distance shall be used as input to Tables 3.2.3.1.-B and 3.2.3.1.-C, where (a) the time from receipt of notification of a fire by the fire department until the arrival of the first fire department vehicle at the building exceeds 10min in 10% or more of all fire department calls to the building, and (b) any storey in the building is not sprinklered. (See Notes A-3.2.3.1.(8) and A-3.2.3.) | obc2019_divb | Div B | 3.2.3.1.(8) | 3.2.3.1. Limiting Distance and Area of Unprotected Openings | If a building has any storey that is not sprinklered and firefighting facilities cannot reach it within 10 min of the alarm being received, the required limiting distance shall be doubled. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.3.1.(9) | Limiting Distance and Area of Unprotected Openings | If the surface temperature on the unexposed surface of a wall assembly exceeds the temperature limit of a standard fire test as permitted by Article 3.1.7.2., an allowance shall be made for the radiation from the hot unexposed wall surface by adding an equivalent area of unprotected opening to the area of actual openings as follows: AC=A+AFÃ—FEOwhere AC = corrected area of unprotected openings including actual and equivalent openings, A= actual area of unprotected openings, AF = area of exterior surface of the exposing building face, exclusive of openings, on which the temperature limit of the standard test is exceeded, and FEO = an equivalent opening factor derived from the following expression: FEO=Tu+273 4Te+273 4 Tu = average temperature in degrees Celsius of the unexposed wall surface at the time the required fire-resistance rating is reached under test conditions, Te = 892Â°C for a fire-resistance rating not less than 45 min, 927Â°C for a fire-resistance rating not less than 1 h, and 1?010Â°C for a fire-resistance rating not less than 2 h. | obc2019_divb | Div B | 3.2.3.1.(9) | 3.2.3.1. Limiting Distance and Area of Unprotected Openings | If the surface temperature on the unexposed surface of a wall assembly exceeds the temperature limit of a standard fire test as permitted by Article 3.1.7.2., an allowance shall be made for the radiation from the hot unexposed wall surface by adding an equivalent area of unprotected opening to the area of actual openings as follows: AC = A + (AF Ãƒâ€” FEO) where, AC = corrected area of unprotected openings including actual and equivalent openings, A = actual area of unprotected openings, AF = area of exterior surface of the exposing building face, exclusive of openings, on which the temperature limit of the standard test is exceeded, and FEO = an equivalent opening factor derived from the following expression: FEO = where, Tu = average temperature in degrees Celsius of the unexposed wall surface at the time the required fire-resistance rating is reached under test conditions, Te = 892Ã‚Â°C for a fire-resistance rating not less than 45 min, 927Ã‚Â°C for a fire-resistance rating not less than 1 h, and 1 010Ã‚Â°C for a fire-resistance rating not less than 2 h. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.10.(1) | Unlimited Unprotected Openings | An exposing building face in a storage garage with all storeys constructed as open-air storeys is permitted to have unlimited unprotected openings provided it has a limiting distance not less than 3 m. | obc2019_divb | Div B | 3.2.3.10.(1) | 3.2.3.10. Unlimited Unprotected Openings | An exposing building face of an open-air storey in a storage garage is permitted to have unlimited unprotected openings provided it has a limiting distance not less than 3 m. |  | Common Sentence | Yes | Fire containment
2015 | ON | NBC | Div B | 3.2.3.10.(2) | Unlimited Unprotected Openings | The exposing building face of a storey that faces a street and is at the same level as the street is permitted to have unlimited unprotected openings if the limiting distance is not less than 9 m. | obc2019_divb | Div B | 3.2.3.10.(2) | 3.2.3.10. Unlimited Unprotected Openings | The exposing building face of a storey that faces a street and is at the same level as the street is permitted to have unlimited unprotected openings if the limiting distance is not less than 9 m. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.11.(1) | Low Fire Load, One Storey Building | An exposing building face of a building of low-hazard industrial occupancy conforming to Article 3.2.2.89. is permitted to be of noncombustible construction without a fire-resistance rating provided it is not a loadbearing wall, and the limiting distance is not less than 3 m. | obc2019_divb | Div B | 3.2.3.11.(1) | 3.2.3.11. Low Fire Load, 1 Storey Building | An exposing building face of a building of low hazard industrial occupancy conforming to Article 3.2.2.82. is permitted to be of noncombustible construction without a fire-resistance rating provided, it is not a loadbearing wall, and the limiting distance is not less than 3 m. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.12.(1) | Area Increase for Unprotected Openings | Except as required by Sentence 3.2.3.7.(5), the maximum area of unprotected openings in any exposing building face of an unsprinklered building is permitted to be doubled if the openings are glazed with glass block conforming to the requirements of Article 3.1.8.16., or wired glass assemblies conforming to apparticle D-2.2.3.15. in Appendix D. | obc2019_divb | Div B | 3.2.3.12.(1) | 3.2.3.12. Area Increase for Unprotected Openings | Except as required by Sentence 3.2.3.7.(8), the maximum area of unprotected openings in any exposing building face or fire compartment of a building that is not sprinklered is permitted to be doubled if the openings are glazed with, glass block conforming to the requirements of Article 3.1.8.14., or wired glass assemblies conforming to MMAH Supplementary Standard SB-2, "Fire Performance Ratings". |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.3.13.(1) | Protection of Exit Facilities | Except as required by Sentence 3.2.3.13.(3) and as permitted by Sentence 3.4.4.3.(1), if the plane of an exterior wall of an exit enclosure forms an angle less than 135Â° with the plane of an exterior wall of the building it serves, and an opening in the exterior wall of the exit enclosure could be exposed to fire from an opening in the exterior wall of the building, the opening in either the exterior wall of the exit or the exterior wall of the building shall be protected in conformance with the requirements of Sentence 3.2.3.13.(4) where the opening in the exterior wall of the building is within 3 m horizontally and less than 10 m below an opening in the exterior wall of the exit, or less than 2 m above an opening in the exterior wall of the exit. | obc2019_divb | Div B | 3.2.3.13.(1) | 3.2.3.13. Protection of Exit Facilities | Except as required by Sentence (3) and as permitted by Sentence 3.4.4.3.(1), if the plane of an exterior wall of an exit enclosure forms an angle less than 135Ã¯â€šÂ° with the plane of an exterior wall of the building it serves, and an opening in the exterior wall of the exit enclosure could be exposed to fire from an opening in the exterior wall of the building, the opening in either the exterior wall of the exit or the exterior wall of the building shall be protected in conformance with the requirements of Sentence (4) where the opening in the exterior wall of the building is within 3 m horizontally and, less than 10 m below an opening in the exterior wall of the exit, or less than 2 m above an opening in the exterior wall of the exit. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.13.(2) | Protection of Exit Facilities | If an unenclosed exterior exit stair or ramp could be exposed to fire from an opening in the exterior wall of the building it serves, the opening in the exterior wall of the building shall be protected in conformance with the requirements of Sentence 3.2.3.13.(4) where the opening in the exterior wall of the building is within 3 m horizontally and less than 10 m below the exit stair or ramp, or less than 5 m above the exit stair or ramp. | obc2019_divb | Div B | 3.2.3.13.(2) | 3.2.3.13. Protection of Exit Facilities | If an unenclosed exterior exit stair or ramp could be exposed to fire from an opening in the exterior wall of the building it serves, the opening in the exterior wall of the building shall be protected in conformance with the requirements of Sentence (4) where the opening in the exterior wall of the building is within 3 m horizontally and, less than 10 m below the exit stair or ramp, or less than 5 m above the exit stair or ramp. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.13.(3) | Protection of Exit Facilities | Except as permitted by Sentence 3.4.4.3.(1), if an exterior exit door in one fire compartment is within 3 m horizontally of an opening in another fire compartment and the exterior walls of these fire compartments intersect at an exterior angle of less than 135Â°, the opening shall be protected in conformance with the requirements of Sentence 3.2.3.13.(4). | obc2019_divb | Div B | 3.2.3.13.(3) | 3.2.3.13. Protection of Exit Facilities | Except as permitted by Sentence 3.4.4.3.(1), if an exterior exit door in one fire compartment is within 3 m horizontally of an opening in another fire compartment and the exterior walls of these fire compartments intersect at an exterior angle of less than 135Ã¯â€šÂ°, the opening shall be protected in conformance with the requirements of Sentence (4). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.13.(4) | Protection of Exit Facilities | The opening protection referred to in Sentences 3.2.3.13.(1) , 3.2.3.13.(2) and 3.2.3.13.(3) shall consist of glass block conforming to the requirements of Article 3.1.8.16., a wired glass assembly conforming to apparticle D-2.2.3.15. in Appendix D, or a closure conforming to the requirements of part 3. and Articles 3.2.3.1. and 3.2.3.14. | obc2019_divb | Div B | 3.2.3.13.(4) | 3.2.3.13. Protection of Exit Facilities | The opening protection referred to in Sentences (1) to (3) shall consist of, glass block conforming to the requirements of Article 3.1.8.14., a wired glass assembly conforming to MMAH Supplementary Standard SB-2, "Fire Performance Ratings", or a closure conforming to the requirements of Subsection 3.1.8. and Articles 3.2.3.1. and 3.2.3.14. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.14.(1) | Wall Exposed to Another Wall | Except as required by Sentences 3.2.3.14.(3) and 3.2.3.13.(1) or as permitted by Sentence 3.2.3.19.(4), if an unprotected opening in an exterior wall of a fire compartment is exposed to an unprotected opening in the exterior wall of another fire compartment, and the planes of the 2 walls are parallel or at an angle less than 135Â°, measured from the exterior of the building, the unprotected openings in the 2 fire compartments shall be separated by a distance not less than Do where Do=2D-q90 Ã—D but in no case less than 1 m, and | obc2019_divb | Div B | 3.2.3.14.(1) | 3.2.3.14. Wall Exposed to Another Wall (See Appendix A.) | Except as required by Sentences (3) and 3.2.3.13.(1) or as permitted by Sentence 3.2.3.19.(4), if an unprotected opening in an exterior wall of a fire compartment is exposed to an unprotected opening in the exterior wall of another fire compartment, and the planes of the two walls are parallel or at an angle less than 135Ã¯â€šÂ°, measured from the exterior of the building, the unprotected openings in the two fire compartments shall be separated by a distance not less than DO,where, DO = 2D Ã¢â‚¬" [(ÃŽÂ¸/90) x D] but in no case less than 1 m, and D = the greater required limiting distance for the exposing building faces of the two fire compartments, and ÃŽÂ¸ = the angle made by the intersecting planes of the exposing building faces of the two fire compartments (in the case where the exterior walls are parallel and face each other, ÃŽÂ¸ = 0Ã¯â€šÂ°). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.14.(2) | Wall Exposed to Another Wall | The exterior wall of each fire compartment referred to in Sentence 3.2.3.14.(1) within the distance, Do, shall have a fire-resistance rating not less than that required for the interior vertical fire separation between the fire compartment and the remainder of the building. | obc2019_divb | Div B | 3.2.3.14.(2) | 3.2.3.14. Wall Exposed to Another Wall (See Appendix A.) | The exterior wall of each fire compartment referred to in Sentence (1) within the distance, DO, shall have a fire-resistance rating not less than that required for the interior vertical fire separation between the fire compartment and the remainder of the building. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.14.(3) | Wall Exposed to Another Wall | Sentence 3.2.3.14.(1) does not apply to unprotected openings of fire compartments within a building that is sprinklered throughout, but shall apply to unprotected openings of fire compartments on opposite sides of a firewall, and exposure from unprotected openings of a fire compartment that is not protected by an automatic sprinkler system. | obc2019_divb | Div B | 3.2.3.14.(3) | 3.2.3.14. Wall Exposed to Another Wall (See Appendix A.) | Sentence (1) does not apply to unprotected openings of fire compartments within a building that is sprinklered, but shall apply to, unprotected openings of fire compartments on opposite sides of a firewall, and exposure from unprotected openings of a fire compartment that is not protected by an automatic sprinkler system. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.15.(1) | Wall Exposed to Adjoining Roof | Except as permitted by Sentence 3.2.3.19.(4), if a wall in a building is exposed to a fire hazard from an adjoining roof of a separate fire compartment that is not sprinklered in the same building, and the exposed wall contains windows within 3 storeys vertically and 5 m horizontally of the roof, the roof shall contain no skylights within 5 m of the exposed wall. | obc2019_divb | Div B | 3.2.3.15.(1) | 3.2.3.15. Wall Exposed to Adjoining Roof | Except as permitted by Sentence 3.2.3.19.(4), if a wall in a building is exposed to a fire hazard from an adjoining roof of a separate fire compartment that is not sprinklered in the same building, and the exposed wall contains windows within 3 storeys vertically and 5 m horizontally of the roof, the roof shall contain no skylights within 5 m of the exposed wall. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.16.(1) | Protection of Soffits | Except as permitted by Sentences (3) and (4), where there is a common attic or roof space above more than 2 suites of residential occupancy or above more than 2 patients’ sleeping rooms, and the common attic or roof space projects beyond the exterior wall of the building, the soffit, and any opening in the soffit or other surface of the projection located within 2 500 mm of a window or door opening, shall be protected by (a) noncombustible material, (i) not less than 0.38 mm thick, and (ii) having a melting point not below 650°C, (b) plywood not less than 11 mm thick, (c) strandboard or waferboard not less than 12.5 mm thick, or (d) lumber not less than 11mm thick. | obc2019_divb | Div B | 3.2.3.16.(1) | 3.2.3.16. Protection of Soffits | Except as permitted by Sentences (2) to (4), where a common attic or roof space spans more than two suites of residential occupancy or more than two patients’ or residents’ sleeping rooms in a Group B, Division 2 or 3 occupancy, and the common attic or roof space projects beyond the exterior wall of the building, the portion of any soffit or other surface enclosing the projection that is less than 2.5 m vertically above a window or door and less than 1.2 m from either side of the window or door, shall have no openings and shall be protected by, (a) noncombustible material, (i) not less than 0.38 mm thick, and (ii) having a melting point not below 650°C, (b) not less than 12.7 mm thick gypsum soffit board or gypsum wallboard installed according to CSA A82.31-M, “Gypsum Board Application”, (c) not less than 11 mm thick plywood, (d) not less than 12.5 mm thick OSB or waferboard, or (e) not less than 11 mm thick lumber. |  | Common Sentence | Yes | Fire containment
2015 | ON | NBC | Div B | 3.2.3.16.(3) | Protection of Soffits | If an eave overhang is completely separated from the remainder of the attic or roof space by the use of fire blocks, the requirements of Sentence 3.2.3.16.(1) do not apply. | obc2019_divb | Div B | 3.2.3.16.(3) | 3.2.3.16. Protection of Soffits | If an eave overhang is completely separated from the remainder of the attic or roof space by fire blocks, the requirements of Sentence (1) do not apply. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.16.(4) | Protection of Soffits | The protection required by Sentence 3.2.3.16.(1) for projections is permitted to be omitted if the fire compartments behind the window and door openings are sprinklered in accordance with Article 3.2.5.12., and all rooms, including closets and bathrooms, having openings in the wall beneath the soffit are sprinklered, notwithstanding exceptions permitted in the standards referenced in Article 3.2.5.12. for the installation of automatic sprinkler systems. | obc2019_divb | Div B | 3.2.3.16.(4) | 3.2.3.16. Protection of Soffits | The protection required by Sentence (1) for projections is permitted to be omitted if, the fire compartments behind the window and door openings are sprinklered in accordance with Article 3.2.5.13., and all rooms, including closets and bathrooms, having openings in the wall beneath the soffit are sprinklered, notwithstanding exceptions permitted in the standards referenced in Article 3.2.5.13. for the installation of automatic sprinkler systems. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.17.(1) | Canopy Protection for Vertically Separated Openings | Except as permitted by Sentences 3.2.3.17.(2) and 3.2.3.17.(3), if a storey classified as a Group E or Group F, Division 1 or 2 major occupancy is required to be separated from the storey above by a fire separation, every opening in the exterior wall of the lower storey that is located vertically below an opening in the storey above shall be separated from the storey above by a canopy projecting not less than 1 m from the face of the building at the intervening floor level, and the canopy required by Sentence 3.2.3.17.(1) shall have a fire-resistance rating not less than that required for the floor assembly but need not be more than 1 h, except as required elsewhere in this Subsection. | obc2019_divb | Div B | 3.2.3.17.(1) | 3.2.3.17. Canopy Protection for Vertically Separated Openings | Except as permitted by Sentences (2) and (3), if a storey classified as a Group E or Group F, Division 1 or 2 major occupancy is required to be separated from the storey above by a fire separation, every opening in the exterior wall of the lower storey that is located vertically below an opening in the storey above shall be separated from the storey above by a canopy projecting not less than 1 m from the face of the building at the intervening floor level, and the canopy required by Clause (a) shall have a fire-resistance rating not less than that required for the floor assembly but need not be more than 1 h, except as required elsewhere in this Subsection. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.17.(2) | Canopy Protection for Vertically Separated Openings | Except as permitted by Sentence 3.2.3.17.(3), the canopy required by Sentence 3.2.3.17.(1) is permitted to be omitted if the exterior wall of the upper storey is recessed not less than 1 m behind the exterior wall containing the opening in the lower storey. | obc2019_divb | Div B | 3.2.3.17.(2) | 3.2.3.17. Canopy Protection for Vertically Separated Openings | Except as permitted by Sentence (3), the canopy required by Sentence (1) is permitted to be omitted if the exterior wall of the upper storey is recessed not less than 1 m behind the exterior wall containing the opening in the lower storey. |  | Common Sentence | Yes | Fire containment
2015 | ON | NBC | Div B | 3.2.3.17.(3) | Canopy Protection for Vertically Separated Openings | The requirements of Sentences (1) and (2) are permitted to be waived if the building is sprinklered throughout. | obc2019_divb | Div B | 3.2.3.17.(3) | 3.2.3.17. Canopy Protection for Vertically Separated Openings | The requirements of Sentences (1) and (2) are permitted to be waived if sprinklers are installed in, (a) the lower storey referred to in Clause (1)(a), and (b) the storey immediately above the lower storey. |  | Common Sentence | Yes | Fire containment
2015 | ON | NBC | Div B | 3.2.3.18.(1) | Covered Vehicular Passageway | A covered vehicular passageway designed as a receiving or shipping area shall be separated from every building or part of a building adjoining it by a fire separation having a fire-resistance rating not less than 1.5 h. | obc2019_divb | Div B | 3.2.3.18.(1) | 3.2.3.18. Covered Vehicular Passageway | A covered vehicular passageway designed as a receiving or shipping area shall be separated from every building or part of a building adjoining it by a fire separation having a fire-resistance rating not less than 1.5 h. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.18.(2) | Covered Vehicular Passageway | A covered vehicular passageway constructed below grade shall be of noncombustible construction. | obc2019_divb | Div B | 3.2.3.18.(2) | 3.2.3.18. Covered Vehicular Passageway | A covered vehicular passageway constructed below grade shall be of noncombustible construction. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.19.(1) | Walkway between Buildings | Except as required by Sentence 3.2.3.20.(2), if buildings are connected by a walkway, each building shall be separated from the walkway by a fire separation with a fire-resistance rating not less than 45 min . | obc2019_divb | Div B | 3.2.3.19.(1) | 3.2.3.19. Walkway Between Buildings | Except as required by Sentence 3.2.3.20.(2), if buildings are connected by a walkway, each building shall be separated from the walkway by a fire separation with a fire-resistance rating not less than 45 min. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.19.(2) | Walkway between Buildings | Except as permitted by Sentence 3.2.3.19.(3), a walkway connected to a building required to be of noncombustible construction shall also be of noncombustible construction. | obc2019_divb | Div B | 3.2.3.19.(2) | 3.2.3.19. Walkway Between Buildings | Except as permitted by Sentence (3), a walkway connected to a building required to be of noncombustible construction shall also be of noncombustible construction. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.19.(3) | Walkway between Buildings | A walkway connected to a building required to be of noncombustible construction is permitted to be of heavy timber construction provided not less than 50% of the area of any enclosing perimeter walls is open to the outdoors, and the walkway is at ground level. | obc2019_divb | Div B | 3.2.3.19.(3) | 3.2.3.19. Walkway Between Buildings | A walkway connected to a building required to be of noncombustible construction is permitted to be of heavy timber construction provided, not less than 50% of the area of any enclosing perimeter walls is open to the outdoors, and the walkway is at ground level. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.19.(4) | Walkway between Buildings | A walkway of noncombustible construction used only as a pedestrian thoroughfare need not conform to the requirements of Articles 3.2.3.14.and 3.2.3.15. | obc2019_divb | Div B | 3.2.3.19.(4) | 3.2.3.19. Walkway Between Buildings | A walkway of noncombustible construction used only as a pedestrian thoroughfare need not conform to the requirements of Articles 3.2.3.14. and 3.2.3.15. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.19.(5) | Walkway between Buildings | A walkway between buildings shall be not more than 9 m wide. | obc2019_divb | Div B | 3.2.3.19.(5) | 3.2.3.19. Walkway Between Buildings | A walkway between buildings shall be not more than 9 m wide. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.2.(1) | Area of Exposing Building Face | Except as permitted by Sentences 3.2.3.2.(2)and 3.2.3.2.(3), the area of an exposing building face shall be calculated as the total area of an exterior wall facing in one direction on any side of a building measured from the finished ground level to the uppermost ceiling. | obc2019_divb | Div B | 3.2.3.2.(1) | 3.2.3.2. Area of Exposing Building Face | Except as permitted by Sentences (2), and (3), the area of an exposing building face shall be calculated as the total area of exterior wall facing in one direction on any side of a building measured from the finished ground level to the uppermost ceiling. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.2.(2) | Area of Exposing Building Face | If a building is divided by fire separations into fire compartments, the area of exposing building face is permitted to be calculated for each fire compartment provided the fire separations have a fire-resistance rating not less than 45 min. | obc2019_divb | Div B | 3.2.3.2.(2) | 3.2.3.2. Area of Exposing Building Face | If a building is divided by fire separations into fire compartments, the area of exposing building face is permitted to be calculated for each fire compartment provided the fire separations have a fire-resistance rating not less than 45 min. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.2.(3) | Area of Exposing Building Face | In a building that is sprinklered throughout and contains an interconnected floor space, the area of the exposing building face for the interconnected floor space is permitted to be determined by considering each storey as a separate fire compartment notwithstanding openings through the floor assemblies. | obc2019_divb | Div B | 3.2.3.2.(3) | 3.2.3.2. Area of Exposing Building Face | In a building that contains an interconnected floor space, the area of the exposing building face for the interconnected floor space is permitted to be determined by considering each storey as a separate fire compartment notwithstanding openings through the floor assemblies. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.3.20.(1) | Underground Walkway | An underground walkway shall not be designed or used for any purpose other than pedestrian travel unless the purpose is acceptable to the authority having jurisdiction, and sprinklers are installed in any space in the walkway containing an occupancy. | obc2019_divb | Div B | 3.2.3.20.(1) | 3.2.3.20. Underground Walkway | An underground walkway shall not be designed or used for any purpose other than pedestrian travel unless, the purpose is permitted, and sprinklers are installed in any space in the walkway containing an occupancy. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.20.(2) | Underground Walkway | Buildings connected by an underground walkway shall be separated from the walkway by a fire separation with a fire-resistance rating not less than 1 h. | obc2019_divb | Div B | 3.2.3.20.(2) | 3.2.3.20. Underground Walkway | Buildings connected by an underground walkway shall be separated from the walkway by a fire separation with a fire-resistance rating not less than 1 h. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.20.(3) | Underground Walkway | An underground walkway shall be of noncombustible construction suitable for an underground location. | obc2019_divb | Div B | 3.2.3.20.(3) | 3.2.3.20. Underground Walkway | An underground walkway shall be of noncombustible construction suitable for an underground location. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.20.(4) | Underground Walkway | In an underground walkway smoke barrier doors shall be installed at intervals of not more than 100 m, or the travel distance from the door of an adjacent room or space to the nearest exit shall be not more than one and a half times the least allowable travel distance to an exit for any of the adjacent occupancies as permitted by Sentence 3.4.2.5.(1). | obc2019_divb | Div B | 3.2.3.20.(4) | 3.2.3.20. Underground Walkway | In an underground walkway, smoke barrier doors shall be installed at intervals of not more than 100 m, or the travel distance from the door of an adjacent room or space to the nearest exit shall be not more than one and a half times the least allowable travel distance to an exit for any of the adjacent occupancies as permitted by Sentence 3.4.2.5.(1). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.20.(5) | Underground Walkway | An underground walkway between buildings shall be not more than 9 m wide. | obc2019_divb | Div B | 3.2.3.20.(5) | 3.2.3.20. Underground Walkway | An underground walkway between buildings shall be not more than 9 m wide. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.22.(1) | Installation of Service Lines Under Buildings | When a building is erected over existing buried flammable gas mains, such service lines shall be encased in gas-tight conduits in conformance with CSA CAN/CSA-Z662-15 Oil and Gas Pipeline Systems | obc2019_divb | Div B | 3.2.3.21.(1) | 3.2.3.21. Service Lines Under Buildings | A building shall not be constructed over an existing buried flammable gas main unless the gas main is encased in a gas-tight conduit in conformance with CAN/CSA-Z662, "Oil and Gas Pipeline Systems". |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.3.(1) | Wall Enclosing Attic or Roof Space | An exterior wall enclosing an attic or roof space and located above an exposing building face, shall be constructed in conformance with the requirements for the exposing building face. | obc2019_divb | Div B | 3.2.3.3.(1) | 3.2.3.3. Wall Enclosing Attic or Roof Space | An exterior wall enclosing an attic or roof space and located above an exposing building face, shall be constructed in conformance with the requirements for the exposing building face. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.5.(1) | Wall with Limiting Distance Less Than 1.2 m | Openings in a wall that has a limiting distance less than 1.2 m shall be protected by closures whose fire-protection rating is in conformance with the fire-resistance rating required for the wall. | obc2019_divb | Div B | 3.2.3.5.(1) | 3.2.3.5. Wall With Limiting Distance Less Than 1.2 m | Openings in a wall that has a limiting distance less than 1.2 m shall be protected by closures whose fire-protection rating is in conformance with the fire-resistance rating required for the wall. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.5.(2) | Wall with Limiting Distance Less Than 1.2 m | Wired glass or glass block shall not be used for a closure referred to in Sentence 3.2.3.5.(1). | obc2019_divb | Div B | 3.2.3.5.(2) | 3.2.3.5. Wall With Limiting Distance Less Than 1.2 m | Wired glass or glass block shall not be used for a closure referred to in Sentence (1). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.6.(1) | Combustible Projections | Except for a building containing one or 2 dwelling units only, combustible projections on the exterior of a wall that could expose an adjacent building to fire spread and are more than 1 m above ground level, including balconies, platforms, canopies and stairs, shall not be permitted within 1.2 m of a property line or the centre line of a public way, or 2.4 m of a combustible projection on another building on the same property. | obc2019_divb | Div B | 3.2.3.6.(1) | 3.2.3.6. Combustible Projections | Except for a building containing one or two dwelling units only, combustible projections on the exterior of a wall that could expose an adjacent building to fire spread and are more than 1 m above ground level, including balconies, platforms, canopies and stairs, shall not be permitted within, 1.2 m of a property line or the centre line of a public way, or 2.4 m of a combustible projection on another building on the same property. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.6.(2) | Combustible Projections | Except as provided in Sentence 3.2.3.6.(4), where the exposing building face has a limiting distance of not more than 0.45 m, projecting roof soffits shall not be constructed above the exposing building face. (See Note A-3.2.3.6.(2).) | obc2019_divb | Div B | 3.2.3.6.(2) | 3.2.3.6. Combustible Projections | Except as provided in Sentence (3.1), where the exposing building face has a limiting distance of not more than 0.45 m, projecting roof soffits shall not be constructed above the exposing building face. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.6.(3) | Combustible Projections | Except as provided in Sentence 3.2.3.6.(4), where the exposing building face has a limiting distance of more than 0.45 m, the face of roof soffits shall not project to less than 0.45 m from the property line. (See Note A-3.2.3.6.(2).) | obc2019_divb | Div B | 3.2.3.6.(3) | 3.2.3.6. Combustible Projections | Except as provided in Sentence (3.1), where the exposing building face has a limiting distance of more than 0.45 m, the face of roof soffits above the exposing building face shall not project to less than 0.45 m from the property line.(3.1) Subject to Sentence (4), the face of a roof soffit is permitted to project to the property line, where it faces a street, lane or public thoroughfare. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.6.(4) | Combustible Projections | The face of a roof soffit is permitted to project to the property line, where it faces a street, lane or public thoroughfare. (See Note A-9.10.14.5.(11) and 9.10.15.5.(10).) | obc2019_divb | Div B | 3.2.3.6.(3) | 3.2.3.6. Combustible Projections | Except as provided in Sentence (3.1), where the exposing building face has a limiting distance of more than 0.45 m, the face of roof soffits above the exposing building face shall not project to less than 0.45 m from the property line.(3.1) Subject to Sentence (4), the face of a roof soffit is permitted to project to the property line, where it faces a street, lane or public thoroughfare. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.6.(5) | Combustible Projections | Where roof soffits project to less than 1.2 m from the centre line of a lane or public thoroughfare, or from an imaginary line between two buildings or fire compartments on the same property, they shall have no openings, and be protected by not less than 0.38 mm thick sheet steel, unvented aluminum conforming to CGSB CAN/CGSB-93.2-M91 Prefinished Aluminum Siding, Soffits, and Fascia, for Residential Use not less than 12.7 mm thick gypsum soffit board or gypsum ceiling board installed according to CSA A82.31-M1980 Gypsum Board Application not less than 11 mm thick plywood, not less than 12.5 mm thick OSB or waferboard, or not less than 11 mm thick lumber. | obc2019_divb | Div B | 3.2.3.6.(4) | 3.2.3.6. Combustible Projections | Where roof soffits project to less than 1.2 m from the centre line of a lane or public thoroughfare or from an imaginary line between two buildings or fire compartments on the same property, they shall, have no openings, and be protected by, not less than 0.38 mm thick sheet steel, unvented aluminum conforming to CAN/CGSB-93.2-M, "Prefinished Aluminum Siding, Soffits and Fascia, for Residential Use", not less than 12.7 mm thick gypsum soffit board or gypsum ceiling board installed according to CSA A82.31 M, "Gypsum Board Application", not less than 11 mm thick plywood, not less than 12.5 mm thick OSB or waferboard, or not less than 11 mm thick lumber. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.6.(6) | Combustible Projections | For buildings of combustible construction, materials installed to provide the required protection of soffits may be covered with a combustible or noncombustible finish material. | obc2019_divb | Div B | 3.2.3.6.(5) | 3.2.3.6. Combustible Projections | For buildings of combustible construction, materials installed to provide the required protection of soffits may be covered with a combustible or noncombustible finish material. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.7.(1) | Construction of Exposing Building Face | Except as provided in Sentences (3) and (4), and Articles 3.2.3.10. and 3.2.3.11., the fire-resistance rating, construction and cladding for exposing building faces of buildings or fire compartments of Group A, B, C, D or Group F, Division 3 occupancy classification shall comply with Table 3.2.3.7. | obc2019_divb | Div B | 3.2.3.7.(6) | 3.2.3.7. Construction of Exposing Building Face | Subject to Sentence (7), cladding for buildings within the scope of Article 3.2.2.43A. or 3.2.2.50A. that exceed 4 storeys in building height or for fire compartments in such buildings where the maximum permitted area of unprotected openings is more than 10% of the exposing building face need not be noncombustible where the wall assembly complies with the requirements of Subclauses 3.1.5.5.(1)(b)(i) and (ii) when tested in accordance with CAN/ULC-S134, “Fire Test of Exterior Wall Assemblies”. |  | Common Sentence | Yes | Mid-rise Wood
2015 | ON | NBC | Div B | 3.2.3.7.(1) | Construction of Exposing Building Face | Except as provided in Sentences 3.2.3.7.(3) and 3.2.3.7.(4), and Articles 3.2.3.10. and 3.2.3.11., the fire-resistance rating, construction and cladding for exposing building faces of buildings or fire compartments of Group A, B, C, D or Group F, Division 3 occupancy classification shall comply with Table 3.2.3.7. | obc2019_divb | Div B | 3.2.3.7.(1) | 3.2.3.7. Construction of Exposing Building Face | Except as provided by Sentences (3) to (6) and Articles 3.2.3.10. and 3.2.3.11, the fire-resistance rating, construction and cladding for exposing building faces of buildings or fire compartments shall comply with Table 3.2.3.7. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.3.7.(3) | Construction of Exposing Building Face | Except as provided in Article 3.1.4.8., the requirement in Table 3.2.3.7. for noncombustible cladding for buildings or fire compartments where the maximum permitted area of unprotected openings is more than 10% of the exposing building face is permitted to be waived for exterior wall assemblies that comply with Article 3.1.5.5. | obc2019_divb | Div B | 3.2.3.7.(3) | 3.2.3.7. Construction of Exposing Building Face | Except as provided by Sentences (4) to (6), cladding for buildings or fire compartments where the maximum permitted area of unprotected openings is more than 10% of the exposing building face need not be noncombustible where the wall assembly complies with the requirements of Sentences 3.1.5.5.(1), when tested in conformance with CAN/ULC-S134, “Fire Test of Exterior Wall Assemblies". |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.3.7.(4) | Construction of Exposing Building Face | Except as provided in Article 3.1.4.8., the requirement in Table 3.2.3.7. for noncombustible cladding for buildings or fire compartments where the maximum permitted area of unprotected openings is more than 25% but not more than 50% of the exposing building face is permitted to be waived where (a) the limiting distance is greater than 5 m, (b) the building or fire compartment and all combustible attic and roof spaces are sprinklered throughout, (c) the cladding (i) conforms to Subsections 9.27.6 , 9.27.7 , 9.27.8 , 9.27.9 or 9.27.10, (ii) is installed without furring members, or on furring not more than 25 mm thick, over gypsum sheathing at least 12.7 mm thick or over masonry, and (iii) after conditioning in conformance with ASTM D 2898-10 Accelerated Weathering of Fire-Retardant-Treated Wood for Fire Testing has a flame-spread rating not greater than 25 on the exterior face when tested in accordance with Sentence 3.1.12.1.(1), (d) the cladding (i) conforms to Subsection 9.27.12, (ii) is installed with or without furring members over gypsum sheathing at least 12.7 mm thick or over masonry, (iii) has a flame-spread rating not greater than 25 when tested in accordance with Sentence 3.1.12.1.(2), and (iv) does not exceed 2 mm in thickness exclusive of fasteners, joints and local reinforcements, or (e) the exterior wall assembly complies with Article 3.1.5.5. | obc2019_divb | Div B | 3.2.3.7.(5) | 3.2.3.7. Construction of Exposing Building Face | Except as provided by Sentence (6), cladding for buildings or fire compartments where the maximum permitted area of unprotected openings is more than 25% but not more than 50% of the exposing building face need not be noncombustible where, (a) the limiting distance is greater than 5 m, (b) the building or fire compartment and all combustible attic or roof spaces are sprinklered, (c) the cladding, (i) conforms to Subsection 9.27.6., 9.27.7., 9.27.8., 9.27.9. or 9.27.10., (ii) is installed without furring members, or on furring not more than 25 mm thick, over gypsum sheathing at least 12.7 mm thick or over masonry, and (iii) after conditioning in conformance with ASTM D2898, "Accelerated Weathering of Fire-Retardant-Treated Wood for Fire Testing", has a flame-spread rating not greater than 25 on the exterior face when tested in accordance with Sentence 3.1.12.1.(1), (d) the cladding, (i) conforms to Subsection 9.27.12., (ii) is installed with or without furring members over gypsum sheathing at least 12.7 mm thick or over masonry, (iii) has a flame-spread rating not greater than 25 when tested in accordance with Sentence 3.1.12.1.(2), and (iv) does not exceed 2 mm in thickness exclusive of fasteners, joints and local reinforcements, or (e) the wall assembly complies with Article 3.1.5.5. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.3.7.(5) | Construction of Exposing Building Face | The construction requirements for the exposing building face stated in Sentences 3.2.3.7.(1) and 3.2.3.7.(2) shall be satisfied before increasing the unprotected opening area as permitted by Sentence 3.2.3.12.(1). | obc2019_divb | Div B | 3.2.3.7.(8) | 3.2.3.7. Construction of Exposing Building Face | The construction requirements for the exposing building face that are listed in Table 3.2.3.7. shall be satisfied before the area of unprotected openings may be increased as permitted by Sentence 3.2.3.12.(1). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.8.(1) | Protection of Exterior Building Face | Except as permitted by Sentence 3.2.3.8.(3) and in addition to the requirements of Sentences 3.2.3.7.(1) and 3.2.3.7.(2) and where the maximum permitted area of unprotected openings is greater than 10% of the exposing building face, foamed plastic insulation used in an exterior wall of a building more than 3 storeys in building height shall be protected on its exterior surface by (a) concrete or masonry not less than 25 mm thick, or (b) noncombustible material that complies with the criteria for testing and the conditions of acceptance stated in Sentence 3.2.3.8.(2) when tested in conformance with ULC CAN/ULC-S101-14 Fire Endurance Tests of Building Construction and Materials | obc2019_divb | Div B | 3.2.3.8.(1) | 3.2.3.8. Protection of Exterior Building Face | Except as permitted by Sentence (3) and in addition to the requirements of Sentence 3.2.3.7.(1) and where the maximum permitted area of unprotected openings is greater than 10% of the exposing building face, foamed plastic insulation used in an exterior wall of a building more than 3 storeys in building height shall be protected on its exterior surface by, (a) concrete or masonry not less than 25 mm thick, or (b) noncombustible material that complies with the criteria for testing and conditions of acceptance of Sentence (2) when tested in conformance with CAN/ULC-S101, "Fire Endurance Tests of Building Construction and Materials". |  | Common Sentence | Yes | Fire containment
2015 | ON | NBC | Div B | 3.2.3.8.(2) | Protection of Exterior Building Face | The criteria for testing and the conditions of acceptance for a wall assembly to satisfy the requirements of Sentence 3.2.3.8.(1) are that (a) the fire exposed area of the wall assembly shall be not less than 9.3 m2 and have no dimension less than 2.75 m, (b) the exposed surface shall include typical vertical and horizontal joints, (c) the test shall be continued for not less than 15 min and the standard time/temperature curve of the referenced standard shall be followed, (d) the noncombustible protective material must remain in place and no through openings should develop that are visible when viewed normal to the face of the material, and (e) the noncombustible protective material should not disintegrate in a manner that would permit fire to propagate along the surface of the test assembly. | obc2019_divb | Div B | 3.2.3.8.(2) | 3.2.3.8. Protection of Exterior Building Face | The criteria for testing and the conditions of acceptance for a wall assembly to satisfy the requirements of Clause (1)(b) are that, (a) the fire exposed area of the wall assembly shall be not less than 9.3 m2 and have no dimension less than 2.75 m, (b) the exposed surface will include typical vertical and horizontal joints, (c) the test shall be continued for not less than 15 min and the standard time/temperature curve of the referenced standard shall be followed, (d) the noncombustible protective material will remain in place and no through openings will develop that are visible when viewed normal to the face of the material, and (e) the noncombustible protective material will not disintegrate in a manner that would permit fire to propagate along the surface of the test assembly. |  | Common Sentence | Yes | Fire containment
2015 | ON | NBC | Div B | 3.2.3.8.(3) | Protection of Exterior Building Face | The requirements of Sentence 3.2.3.8.(1) are waived for wall assemblies that comply with the requirements of Article 3.1.5.5. (See Note A-3.1.4.1.(1).) | obc2019_divb | Div B | 3.2.3.8.(3) | 3.2.3.8. Protection of Exterior Building Face | The requirements of Sentence (1) are waived for wall assemblies that comply with the requirements of Article 3.1.5.5. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.9.(1) | Protection of Structural Members | Structural members, including beams, columns and arches, that are placed wholly or partly outside the exterior face of a building and are less than 3 m from the property line or the centre line of a public thoroughfare shall be protected from exterior fire exposure by fire protection having a fire-resistance rating not less than that required for their protection from interior fire exposure, as stated in Articles 3.2.2.20. to 3.2.2.90., but not less than 1 h. | obc2019_divb | Div B | 3.2.3.9.(1) | 3.2.3.9. Protection of Structural Members | Structural members, including beams, columns and arches, placed wholly or partly outside an exterior face of a building that are less than 3 m from the property line or centreline of a public thoroughfare shall be protected from exterior fire by fire protection having a fire-resistance rating not less than that required by Articles 3.2.2.20. to 3.2.2.83. for their protection from interior fires, but not less than 1 h. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.3.9.(2) | Protection of Structural Members | Structural members of heavy timber construction, including beams, columns and arches, that are placed wholly or partly outside the exterior face of a building and are 3 m or more from the property line or the centre line of a public thoroughfare need not be covered with noncombustible cladding. | obc2019_divb | Div B | 3.2.3.9.(2) | 3.2.3.9. Protection of Structural Members | Structural members of heavy timber construction, including beams, columns and arches, placed wholly or partly outside an exterior face of a building and 3 m or more from the property line or centreline of a public thoroughfare need not be covered with noncombustible cladding. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.1.(4) | Determination of Requirement for a Fire Alarm System | Except as permitted by Sentences 3.2.4.1.(5) to 3.2.4.1.(7) and Sentence 3.2.4.2.(4), a fire alarm system shall be installed in a building that is not sprinklered throughout and that contains (a) a contained use area, (b) an impeded egress zone, (c) more than 3 storeys , including the storeys below the first storey, (d) a total occupant load more than 300, other than in open air seating areas, (e) an occupant load more than 150 above or below the first storey, other than in open air seating areas, (f) a school, college, or child care facility, including a daycare facility, with an occupant load more than 40, (g) a licensed beverage establishment or a licensed restaurant, with an occupant load more than 150, (h) a low-hazard industrial occupancy with an occupant load more than 75 above or below the first storey, (i) a medium-hazard industrial occupancy with an occupant load more than 75 above or below the first storey, (j) a residential occupancy with sleeping accommodation for more than 10 persons, (k) a high-hazard industrial occupancy with an occupant load more than 25, or (l) an occupant load more than 300 below an open air seating area. | obc2019_divb | Div B | 3.2.4.1.(2) | 3.2.4.1. Determination of Requirement for a Fire Alarm System | Except as permitted by Sentences (3) to (5) and Sentence 3.2.4.2.(4), a fire alarm system shall be installed in a building that contains, (a) a contained use area, (b) an impeded egress zone, (c) more than 3 storeys, including storeys below the first storey, (d) a total occupant load more than 300, other than in open air seating areas, (e) an occupant load more than 150 above or below the first storey, other than in open air seating areas, (f) a school, college or child care facility, with an occupant load more than 40, (g) a licensed beverage establishment or a restaurant, with an occupant load more than 150, (h) a low hazard industrial occupancy with an occupant load more than 75 above or below the first storey, (h.1) a medium hazard industrial occupancy with an occupant load more than 75 above or below the first storey, (i) a residential occupancy with sleeping accommodation for more than 10 persons, (j) a high hazard industrial occupancy with an occupant load more than 25, (k) an occupant load more than 300 below an open air seating area, (l) an interconnected floor space required to conform to Articles 3.2.8.3. to 3.2.8.11, (m) a care and treatment occupancy for more than 10 persons receiving care or treatment, or (n) a care occupancy for more than 10 persons receiving care. |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.1.(5) | Determination of Requirement for a Fire Alarm System | Where each dwelling unit in an apartment building that is not sprinklered has direct access to an exterior exit facility leading to ground level, a fire alarm system is not required if not more than 4 dwelling units share a common means of egress, or the building is not more than 3 storeys in building height. | obc2019_divb | Div B | 3.2.4.1.(3) | 3.2.4.1. Determination of Requirement for a Fire Alarm System | If each dwelling unit has direct access to an exterior exit facility leading to ground level, a fire alarm system is not required in an apartment building, in which not more than four dwelling units share a common means of egress, or that is not more than 3 storeys in building height. |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.1.(6) | Determination of Requirement for a Fire Alarm System | A fire alarm system is not required in a hotel or motel 3 storeys or less in building height that is contained in a building that is not sprinklered provided each suite has direct access to an exterior exit facility leading to ground level. | obc2019_divb | Div B | 3.2.4.1.(4) | 3.2.4.1. Determination of Requirement for a Fire Alarm System | A fire alarm system is not required in a hotel 3 storeys or less in building height provided each suite has direct access to an exterior exit facility leading to ground level. |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.1.(7) | Determination of Requirement for a Fire Alarm System | A fire alarm system is not required in a storage garage conforming to Article 3.2.2.90. that is contained in a building that is not sprinklered provided there are no other occupancies in the building. | obc2019_divb | Div B | 3.2.4.1.(5) | 3.2.4.1. Determination of Requirement for a Fire Alarm System | A fire alarm system is not required in a storage garage conforming to Article 3.2.2.83. provided there are no other occupancies in the building. |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.10.(1) | Fire Detectors | Fire detectors required by this Code shall be connected to the fire alarm system. | obc2019_divb | Div B | 3.2.4.11.(1) | 3.2.4.11. Fire Detectors | Fire detectors required by this Article shall be connected to the fire alarm system. |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.10.(2) | Fire Detectors | Except as permitted by Sentence 3.2.4.10.(3), if a fire alarm system is required in a building that is not sprinklered, fire detectors shall be installed in the following spaces: (a) storage rooms not within dwelling units, (b) service rooms not within dwelling units, (c) janitor rooms, (d) rooms in which hazardous substances are to be used or stored (see Note A-3.3.1.2.(1)), (e) elevator hoistways and dumbwaiter shafts, and (f) laundry rooms in buildings of residential occupancy, but not those within dwelling units. | obc2019_divb | Div B | 3.2.4.11.(2) | 3.2.4.11. Fire Detectors | Except as provided in Article 3.2.4.16., if a fire alarm system is required, fire detectors shall be installed in each, (a) storage room not within a dwelling unit, (b) service room not within a dwelling unit, (c) janitors room, (d) room in which hazardous substances are to be used or stored, (e) elevator or dumbwaiter shaft, (f) laundry room in a building of residential occupancy, but not one within a dwelling unit, and (g) hazardous classroom and change room in an elementary or secondary school. |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.10.(3) | Fire Detectors | Fire detectors required by Sentence (2) need not be provided within floor areas that are sprinklered | obc2019_divb | Div B | 3.2.4.16.(1) | 3.2.4.16 Sprinklers in Lieu of Fire Detectors | Fire detectors required by Article 3.2.4.11. and heat detectors required by Sentence 3.2.4.12.(2) need not be provided within a floor area if the floor area is sprinklered and the sprinkler system is electrically supervised in conformance with Sentence 3.2.4.10.(3). |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.11.(1) | Smoke Detectors | If a fire alarm system is installed, smoke detectors shall be installed in (a) except as permitted in Sentence (2), each sleeping room and each corridor serving as part of a means of egress from sleeping rooms in portions of a building classified as a Group B major occupancy, (b) each room in a contained use area and corridors serving those rooms, (c) each corridor in portions of a building classified as a Group A, Division 1 major occupancy, (d) each public corridor in portions of a building classified as a Group C major occupancy, (e) each exit stair shaft other than those serving only a Group A, Division 4 major occupancy or an open storage garage, (f) the vicinity of draftstops required by Article 3.2.8.6., and (g) elevator machine rooms. (See Note A-3.2.4.11.(1).) | obc2019_divb | Div B | 3.2.8.8.(1) | 3.2.8.8. Fire Alarm and Detection System | A building containing an interconnected floor space shall be provided with, a fire alarm system and electrically supervised annunciator conforming to Subsection 3.2.4., a system of smoke detectors located, on the ceiling of each storey in the vicinity of the openings through floor assemblies described in Article 3.2.8.3., except within dwelling units, heat detectors may be installed instead of smoke detectors, and as required for the activation of the smoke control system described in Sentences 3.2.8.9.(3), (4), (6) and (7), and (See Appendix A.) facilities for transmitting a signal to the fire department in conformance with Article 3.2.4.8. |  | Common Sentence | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B | 3.2.4.11.(1) | Smoke Detectors | If a fire alarm system is installed, smoke detectors shall be installed in except as permitted in Sentence 3.2.4.11.(2), each sleeping room and each corridor serving as part of a means of egress from sleeping rooms in portions of a building classified as a Group B major occupancy, each room in a contained use area and corridors serving those rooms, each corridor in portions of a building classified as a Group A, Division 1 major occupancy, each public corridor in portions of a building classified as a Group C major occupancy, each exit stair shaft other than those serving only a Group A, Division 4 major occupancy or an open storage garage, the vicinity of draft stops required by Article 3.2.8.6., and elevator machine rooms. | obc2019_divb | Div B | 3.2.4.12.(1) | 3.2.4.12. Smoke and Heat Detectors | If a fire alarm system is required, smoke detectors shall be installed in, each sleeping room and each corridor serving as part of a means of egress from sleeping rooms in portions of a building classified as Group B major occupancy, each room in a contained use area and corridors serving those rooms, each corridor in portions of a building classified as Group A, Division 1 major occupancy, each public corridor in portions of a building classified as Group C major occupancy, each exit stair shaft, each corridor serving classrooms in elementary and secondary schools, and each elevator machine room or machinery space. |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.11.(3) | Smoke Detectors | Smoke detectors required in the sleeping rooms of a care, treatment or detention occupancy shall, upon actuation, provide an audible and visible signal to staff serving those rooms so that the room or location containing the actuated smoke detector can be easily identified. (See Note A-3.2.4.11.(3).) | obc2019_divb | Div B | 3.2.4.12.(3) | 3.2.4.12. Smoke and Heat Detectors | Smoke detectors required in sleeping rooms of care, care and treatment or detention occupancy shall upon actuation provide an audible and visible signal to staff serving those rooms so that the room or location containing the smoke detector can be easily identified. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.11.(4) | Smoke Detectors | Smoke detectors required in Sentence 3.2.4.11.(1) shall, upon actuation, recall the elevators served by the elevator machine room in which the smoke detector is installed. | obc2019_divb | Div B | 3.2.4.12.(4) | 3.2.4.12. Smoke and Heat Detectors | Smoke detectors required by Clause (1)(g) shall, upon actuation, recall the elevators served by machinery located in the machine room or machinery space in which the smoke detector is installed. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.11.(5) | Smoke Detectors | Except as permitted in Sentences 3.2.4.11.(6) and 3.2.4.11.(7), smoke detectors installed in buildings required to be equipped with a fire alarm system shall be located near the entrance to walkways described in Articles 3.2.3.19. and 3.2.3.20. or vestibules provided in conformance with Article 3.2.6.3. | obc2019_divb | Div B | 3.2.4.12.(5) | 3.2.4.12. Smoke and Heat Detectors | Except as permitted by Sentences (6) and (7), where a building is required to be equipped with a fire alarm system, a smoke detector shall be located near the entrance to, a walkway described in Articles 3.2.3.19. and 3.2.3.20., or a vestibule provided in conformance with Article 3.2.6.3. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.11.(6) | Smoke Detectors | Smoke detectors installed at the entrance to the walkways in conformance with Article 3.1.8.14. shall be deemed to meet the requirements of Sentence 3.2.4.11.(5). | obc2019_divb | Div B | 3.2.4.12.(6) | 3.2.4.12. Smoke and Heat Detectors | Smoke detectors installed at the entrance to a walkway in conformance with Article 3.1.8.12. are deemed to meet the requirements of Sentence (5). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.11.(7) | Smoke Detectors | Smoke detectors required by Sentence 3.2.4.11.(5) may be replaced with fire detectors in Group F occupancies where the smoke detectors may be subjected to false alarms due to the activities within the building. | obc2019_divb | Div B | 3.2.4.12.(7) | 3.2.4.12. Smoke and Heat Detectors | Fire detectors are permitted to be installed in lieu of the smoke detectors required by Sentence (5) in Group F occupancies where the smoke detectors may be subjected to false alarms due to the activities within the building. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.12.(1) | Prevention of Smoke Circulation | If a fire alarm system is installed, an air-handling system shall be designed to prevent the circulation of smoke upon a signal from a duct-type smoke detector if the air-handling system serves more than one storey, serves more than one suite in a storey, or serves more than one fire compartment required by Sentence 3.3.3.5.(2). | obc2019_divb | Div B | 3.2.4.13.(1) | 3.2.4.13. Prevention of Smoke Circulation | If a fire alarm system is installed, an air handling system shall be designed to prevent the circulation of smoke upon a signal from a duct-type smoke detector if the air handling system, serves more than 1 storey, serves more than one suite in a storey, serves more than one fire compartment required by Sentence 3.3.3.5.(2) or Sentence 3.3.4.11.(2), or is not provided with fire dampers as permitted by Sentence 3.1.8.8.(4). |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.13.(1) | Vacuum Cleaning System Shutdown | A central vacuum cleaning system in a building equipped with a fire alarm system shall be designed to shut down upon actuation of the fire alarm system. | obc2019_divb | Div B | 3.2.4.14.(1) | 3.2.4.14. Vacuum Cleaning System Shutdown | A central vacuum cleaning system serving more than one suite or storey in a building equipped with a fire alarm system shall be designed to shut down upon actuation of the fire alarm system. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.14.(1) | Elevator Emergency Return | Except as permitted by Sentence 3.2.4.14.(3), in a building having elevators that serve storeys above the first storey and that are equipped with an automatic emergency recall feature, smoke detectors shall be installed in the elevator lobbies on the recall level so that when these smoke detectors are actuated, the elevators will automatically return directly to an alternate floor level. | obc2019_divb | Div B | 3.2.4.15.(1) | 3.2.4.15. Elevator Emergency Return | Except as permitted by Sentence (3), in a building having elevators that serve storeys above the first storey and that are equipped with an automatic emergency recall feature, smoke detectors shall be installed in the elevator lobbies on the recall level so that when these smoke detectors are actuated, the elevators will automatically return directly to an alternate floor level. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.14.(2) | Elevator Emergency Return | Smoke detectors required by Sentence 3.2.4.14.(1) shall be designed as part of the building fire alarm system. | obc2019_divb | Div B | 3.2.4.15.(2) | 3.2.4.15. Elevator Emergency Return | Smoke detectors required by Sentence (1) shall be designed as part of the building fire alarm system. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.14.(3) | Elevator Emergency Return | The alternate floor recall feature required by Sentence 3.2.4.14.(1) is not required if the floor area containing the recall level is sprinklered throughout. | obc2019_divb | Div B | 3.2.4.15.(3) | 3.2.4.15. Elevator Emergency Return | The alternate floor recall feature required by Sentence (1) is not required if the floor area containing the recall level is sprinklered. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.15.(1) | System Monitoring | An automatic sprinkler system shall be equipped with waterflow detecting devices and, if an annunciator is required by Article 3.2.4.8., shall be installed so that each device serves not more than one storey, and an area on each storey that is not more than the system area limits as specified in NFPA 13-2013 Installation of Sprinkler Systems | obc2019_divb | Div B | 3.2.4.17.(1) | 3.2.4.17. System Monitoring | An automatic sprinkler system shall be equipped with waterflow detecting devices and, if an annunciator is required by Article 3.2.4.9., shall be installed so that each device serves, not more than 1 storey, and an area on each storey that is not more than the system area limits as specified in NFPA 13, "Installation of Sprinkler Systems". |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.15.(2) | System Monitoring | Waterflow-detecting devices required by Sentence 3.2.4.15.(1) shall be connected to the fire alarm system so that, upon its actuation, an alert signal or an alarm signal is initiated. | obc2019_divb | Div B | 3.2.4.17.(2) | 3.2.4.17. System Monitoring | If a fire alarm system is provided, waterflow indicating devices required by Sentence (1) shall be connected to the fire alarm system so that on actuation an alert signal or an alarm signal is initiated. |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.16.(1) | Manual Stations | Except as permitted by Sentences 3.2.4.16.(2) and 3.2.4.16.(3), where a fire alarm system is installed, a manual station shall be installed in every floor area near every principal entrance to the building, and every exit. | obc2019_divb | Div B | 3.2.4.18.(1) | 3.2.4.18. Manual Pull Stations | Except as permitted by Sentences (2) and (3), if a fire alarm system is installed, a manual pull station shall be installed, near the principal entrance to the building, and near every required exit. |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.16.(2) | Manual Stations | In a building that is sprinklered throughout, a manual station is not required at an exterior egress doorway from a suite that does not lead to an interior shared means of egress in a hotel or motel not more than 3 storeys in building height, provided each suite is served by an exterior exit facility leading directly to ground level. | obc2019_divb | Div B | 3.2.4.18.(2) | 3.2.4.18. Manual Pull Stations | In a building that is sprinklered, a manual pull station is not required at an exterior egress doorway from a suite that does not lead to an interior shared means of egress in a hotel not more than 3 storeys in building height, provided each suite is served by an exterior exit facility leading directly to ground level. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.16.(3) | Manual Stations | In a building that is sprinklered throughout, a manual station is not required at an exterior egress doorway from a dwelling unit that does not lead to an interior shared means of egress in a building not more than 3 storeys in building height containing only dwelling units, provided each dwelling unit is served by an exterior exit facility leading directly to ground level. | obc2019_divb | Div B | 3.2.4.18.(3) | 3.2.4.18. Manual Pull Stations | In a building that is sprinklered, a manual pull station is not required at an exterior egress doorway from a dwelling unit that does not lead to an interior shared means of egress in a building not more than 3 storeys in building height containing only dwelling units, provided each dwelling unit is served by an exterior exit facility leading directly to ground level. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.16.(4) | Manual Stations | In a building referred to in Sentences 3.2.4.16.(2) or 3.2.4.16.(3), manual stations shall be installed near doorways leading from shared interior corridors to the exterior. | obc2019_divb | Div B | 3.2.4.18.(4) | 3.2.4.18. Manual Pull Stations | In a building referred to in Sentence (2) or (3), manual pull stations shall be installed near doorways leading from shared interior corridors to the exterior. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.17.(1) | Alert and Alarm Signals | In a 2-stage fire alarm system described in Sentence 3.2.4.4.(2), the same audible signal devices are permitted to be used to sound the alert signals and the alarm signals. | obc2019_divb | Div B | 3.2.4.19.(1) | 3.2.4.19. Alert and Alarm Signals | In a two stage fire alarm system described in Sentence 3.2.4.4.(2), the same audible signal devices are permitted to be used to sound the alert signals and the alarm signals. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.17.(2) | Alert and Alarm Signals | If audible signal devices with voice reproduction capabilities are intended for paging and similar voice message use, other than during a fire emergency, they shall be installed so that alert signals and alarm signals take priority over all other signals. | obc2019_divb | Div B | 3.2.4.19.(2) | 3.2.4.19. Alert and Alarm Signals | If audible signal devices with voice reproduction capabilities are intended for paging and similar voice message use, other than during a fire emergency, they shall be installed so that alert signals and alarm signals take priority over all other signals. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.17.(3) | Alert and Alarm Signals | Audible signal devices forming part of a fire alarm or voice communication system shall not be used for playing music or background noise. (See Note A-3.2.4.18.) | obc2019_divb | Div B | 3.2.4.19.(3) | 3.2.4.19. Alert and Alarm Signals | Audible signal devices forming part of a fire alarm or voice communication system shall not be used for playing music or background noise. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.18.(1) | Audibility of Alarm Systems | Audible signal devices forming part of a fire alarm system shall be installed in a building so that (a) alarm signals are clearly audible throughout the floor area, and (b) alert signals are clearly audible in continuously staffed locations, and where there are no continuously staffed locations, throughout the floor area. | obc2019_divb | Div B | 3.2.4.20.(1) | 3.2.4.20. Audibility of Alarm Systems (See Appendix A.) | Except as permitted by Sentence 3.2.4.19.(5) and except as required by Clause 3.2.4.4.(2)(d), audible signal devices forming part of a fire alarm system shall be installed in a building so that, (a) alarm signals are clearly audible throughout the floor area, and (b) alert signals are clearly audible in continuously staffed locations and, where there are no continuously staffed locations, throughout the floor area. |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.18.(10) | Audibility of Alarm Systems | Audible signal devices shall be installed in a service space referred to in Sentence 3.2.1.1.(8) and shall be connected to the fire alarm system. | obc2019_divb | Div B | 3.2.4.20.(12) | 3.2.4.20. Audibility of Alarm Systems (See Appendix A.) | Audible signal devices shall be installed in a service space referred to in Sentence 3.2.1.1.(9) and shall be connected to the fire alarm system. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.18.(11) | Audibility of Alarm Systems | Audible signal devices within dwelling units that are wired on separate signal circuits need not include a means for silencing as required by Sentence 3.2.4.18.(7) provided the fire alarm system includes a provision for an automatic signal silence within dwelling units, where (a) the automatic signal silence cannot occur within the first 60 s of operation or within the zone of initiation, (b) a subsequent alarm elsewhere in the building will reactuate the silenced audible signal devices within dwelling units, (c) after a period of not more than 10 min, the silenced audible signal devices will be restored to continuous audible signal if the alarm is not acknowledged, and (d) the voice communication systems referred to in Articles 3.2.4.22. and 3.2.4.23. have a provision to override the automatic signal silence to allow the transmission of voice messages through silenced audible signal device circuits that serve the dwelling units. | obc2019_divb | Div B | 3.2.4.20.(13) | 3.2.4.20. Audibility of Alarm Systems (See Appendix A.) | Audible signal devices, within dwelling units that are wired on separate signal circuits, need not include a means for silencing as required by Sentence (9) provided the fire alarm system includes a provision for the automatic signal silence within dwelling units, where, (a) the automatic signal silence cannot occur within the first 60 s of operation or within the zone of initiation, (b) a subsequent alarm elsewhere in the building will reactuate the silenced audible signal devices within dwelling units, (c) after a period of not more than 10 min, the silenced audible signal devices will be restored to continuous audible signal if the alarm is not acknowledged, and (d) the voice communication system referred to in Article 3.2.4.23. or 3.2.4.24. has a provision to override the automatic signal silence to allow the transmission of voice messages through silenced audible signal device circuits that serve the dwelling units. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.18.(12) | Audibility of Alarm Systems | If a 2-stage fire alarm system has been installed with an automatic signal silence as described in Sentence 3.2.4.18.(11), the system shall be designed so that any silenced audible signal devices serving dwelling units are reactuated whenever an alarm signal is required to be transmitted as part of the second stage. (See Note A-3.2.4.18.(7).) | obc2019_divb | Div B | 3.2.4.20.(14) | 3.2.4.20. Audibility of Alarm Systems (See Appendix A.) | If a two stage fire alarm system has been installed with an automatic signal silence as described in Sentence (13), the system shall be designed so that any silenced audible signal devices serving dwelling units are reactuated whenever an alarm signal is required to be transmitted as part of the second stage. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.18.(2) | Audibility of Alarm Systems | The sound pattern of an alarm signal shall conform to the temporal pattern defined in Clause 4.2 of ISO 8201:1987(E) Acoustics â€“ Audible emergency evacuation signal (See Note A-3.2.4.18.(2).) | obc2019_divb | Div B | 3.2.4.20.(2) | 3.2.4.20. Audibility of Alarm Systems (See Appendix A.) | The sound pattern of an alarm signal shall conform to the temporal pattern defined in Clause 4.2 of International Standard ISO 8201, "Acoustics Ã¢â‚¬" Audible Emergency Evacuation Signal". (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.18.(3) | Audibility of Alarm Systems | The sound patterns of alert signals shall be significantly different from the temporal patterns of alarm signals. (See Note A-3.2.4.18.(3).) | obc2019_divb | Div B | 3.2.4.20.(3) | 3.2.4.20. Audibility of Alarm Systems (See Appendix A.) | The sound patterns of alert signals shall be significantly different from the temporal patterns of alarm signals. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.18.(4) | Audibility of Alarm Systems | The fire alarm signal sound pressure level shall be not more than 110 dBA in any normally occupied area. (See Note A-3.2.4.18.(4).) | obc2019_divb | Div B | 3.2.4.20.(4) | 3.2.4.20. Audibility of Alarm Systems (See Appendix A.) | In all normally occupied spaces, the fire alarm signal sound pressure level, shall be not more than 100 dBA when measured at a distance of 3 m from the device, or is permitted to be more than 100 dBA provided the sound pressure level measured 2 000 mm above floor level is not more than 100 dBA. |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.18.(5) | Audibility of Alarm Systems | The sound pressure level in a sleeping room from a fire alarm audible signal device shall be not less than 75 dBA in a building of residential or care occupancy when any intervening doors between the device and the sleeping room are closed. (See Note A-3.2.4.18.(5).) | obc2019_divb | Div B | 3.2.4.20.(5) | 3.2.4.20. Audibility of Alarm Systems (See Appendix A.) | The sound pressure level in a sleeping room from a fire alarm audible signal device shall be not less than 75 dBA in a building of residential occupancy when any intervening doors between the device and the sleeping room are closed. (See Appendix A.) |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.18.(6) | Audibility of Alarm Systems | Except as required by Sentence 3.2.4.18.(5), the sound pressure level from a fire alarm systemâ€™s audible signal device within a floor area shall be not less than 10 dBA above the ambient noise level without being less than 65 dBA. | obc2019_divb | Div B | 3.2.4.20.(6) | 3.2.4.20. Audibility of Alarm Systems (See Appendix A.) | Except as required by Sentence (5), the sound pressure level from a fire alarm audible signal device in a floor area shall be not less than 10 dBA above the ambient noise level, but with a minimum value not less than 65 dBA. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.18.(7) | Audibility of Alarm Systems | Except as permitted by Sentence 3.2.4.18.(11), audible signal devices located within a dwelling unit shall include a means for them to be manually silenced for a period of not more than 10 min, after which time the devices shall restore themselves to normal operation. (See Note A-3.2.4.18.(7).) | obc2019_divb | Div B | 3.2.4.20.(9) | 3.2.4.20. Audibility of Alarm Systems (See Appendix A.) | Except as permitted by Sentence (13), an audible signal device located within a dwelling unit shall incorporate a means that enables the device to be silenced for a period of not more than 10 min, after which the device shall restore to normal operation. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.18.(9) | Audibility of Alarm Systems | In a building or part thereof classified as a residential or care occupancy, separate circuits shall be provided for audible signal devices on each floor area, and audible signal devices within dwelling units or suites of residential or care occupancy shall be wired on separate signal circuits from those not within dwelling units or suites of residential or care occupancy. | obc2019_divb | Div B | 3.2.4.20.(11) | 3.2.4.20. Audibility of Alarm Systems (See Appendix A.) | In a building or part of it classified as a residential occupancy, separate circuits shall be provided for audible signal devices on each floor area, and audible signal devices within dwelling units or suites of residential occupancy shall be wired on separate signal circuits from those not within suites of residential occupancy or dwelling units. |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.19.(1) | Visual Signals | Visual signal devices shall be installed in addition to alarm signals (a) in buildings or portions thereof intended for use primarily by persons with a hearing impairment, (b) in assembly occupancies in which music and other sounds associated with performances could exceed 100 dBA, (c) in any floor area in which the ambient noise level is more than 87 dBA, and (d) in any floor area in which the occupants (i) use ear protection devices, (ii) are located in an audiometric booth, or (iii) are located in sound-insulating enclosures. | obc2019_divb | Div B | 3.2.4.19.(4) | 3.2.4.19. Alert and Alarm Signals | Except as permitted by Sentence (6), visual signal devices shall be installed in addition to audible signal devices, (a) in a building or portion of a building intended for use primarily by persons with hearing impairment, (b) in a public corridor serving a Group A, B, C, D or E occupancy, (c) in a corridor used by the public and in a floor area or part of a floor area where the public may congregate in a Group A occupancy, (d) in not less than 10% of the suites of a hotel or motel, (e) in a washroom for public use described in Sentence 3.8.2.3.(2), (3), (4) or (6), and (f) in the living space in a suite of residential occupancy in a Group C major occupancy apartment building. |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.19.(1) | Visual Signals | Visual signal devices shall be installed in addition to alarm signals (a) in buildings or portions thereof intended for use primarily by persons with a hearing impairment, (b) in assembly occupancies in which music and other sounds associated with performances could exceed 100 dBA, (c) in any floor area in which the ambient noise level is more than 87 dBA, and (d) in any floor area in which the occupants (i) use ear protection devices, (ii) are located in an audiometric booth, or (iii) are located in sound-insulating enclosures. | obc2019_divb | Div B | 3.2.4.20.(7) | 3.2.4.20. Audibility of Alarm Systems (See Appendix A.) | Fire alarm audible signal devices shall be supplemented by visual signal devices in any floor area in which, the ambient noise level is more than 87 dBA, or the occupants of the floor area, use ear protective devices, are located within an audiometric booth, or are located within sound insulated enclosures. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.19.(1) | Visual Signals | Visual signal devices shall be installed in addition to alarm signals (a) in buildings or portions thereof intended for use primarily by persons with a hearing impairment, (b) in assembly occupancies in which music and other sounds associated with performances could exceed 100 dBA, (c) in any floor area in which the ambient noise level is more than 87 dBA, and (d) in any floor area in which the occupants (i) use ear protection devices, (ii) are located in an audiometric booth, or (iii) are located in sound-insulating enclosures. | obc2019_divb | Div B | 3.2.4.20.(8) | 3.2.4.20. Audibility of Alarm Systems (See Appendix A.) | Sentence (7) shall also apply in an assembly occupancy in which music and other sounds associated with performances could exceed 100 dBA. |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.19.(2) | Visual Signals | Visual signal devices required by Sentence 3.2.4.19.(1) shall be installed so that the signal from at least one device is visible throughout the floor area or portion thereof in which they are installed. (See Note A-3.2.4.19.(2).) | obc2019_divb | Div B | 3.2.4.21.(1) | 3.2.4.21. Visual Signals | Visual signal devices required by Sentences 3.2.4.19.(4) and 3.2.4.20.(7) and (8) shall be installed so that the signal from at least one device is visible throughout the floor area or portion of it in which they are installed. (See Appendix A.) |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.2.(1) | Continuity of Fire Alarm System | Except as permitted by Sentence 3.2.4.2.(6), if there are openings through a firewall, other than those for piping, tubing, wiring and totally enclosed noncombustible raceways, the requirements in this Subsection shall apply to the floor areas on both sides of the firewall as if they were in the same building. | obc2019_divb | Div B | 3.2.4.2.(1) | 3.2.4.2. Continuity of Fire Alarm System | Except as permitted by Sentence (6), if there are openings through a firewall, other than those for piping, tubing, wiring and totally enclosed noncombustible raceways, the requirements in this Subsection shall apply to the floor areas on both sides of the firewall as if they were in the same building. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.2.(2) | Continuity of Fire Alarm System | Except as permitted by Sentence 3.2.4.2.(4), if a building contains more than one major occupancy and a fire alarm system is required, a single system shall serve all occupancies. | obc2019_divb | Div B | 3.2.4.2.(2) | 3.2.4.2. Continuity of Fire Alarm System | Except as permitted by Sentence (4), if a building contains more than one major occupancy and a fire alarm system is required, a single system shall serve all occupancies. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.2.(3) | Continuity of Fire Alarm System | Except as permitted by Sentence 3.2.4.2.(4), if a fire alarm system is required in any portion of a building, it shall be installed throughout the building. | obc2019_divb | Div B | 3.2.4.2.(3) | 3.2.4.2. Continuity of Fire Alarm System | Except as permitted by Sentence (4), if a fire alarm system is required in any portion of a building, it shall be installed throughout the building. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.2.(4) | Continuity of Fire Alarm System | Except as required by Sentence 3.2.4.2.(5), the requirements in this Subsection are permitted to be applied to each portion of a building not more than 3 storeys in building height, in which a vertical fire separation having a fire-resistance rating not less than 1 h separates the portion from the remainder of the building as if it were a separate building, provided there are no openings through the fire separation, other than those for piping, tubing, wiring and totally enclosed noncombustible raceways. | obc2019_divb | Div B | 3.2.4.2.(4) | 3.2.4.2. Continuity of Fire Alarm System | Except as required by Sentence (5), the requirements in this Subsection are permitted to be applied to each portion of a building not more than 3 storeys in building height, in which a vertical fire separation having a fire-resistance rating not less than 1 h separates the portion from the remainder of the building as if it were a separate building, provided there are no openings through the fire separation, other than those for piping, tubing, wiring and totally enclosed noncombustible raceways. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.2.(5) | Continuity of Fire Alarm System | The permission in Sentence 3.2.4.2.(4) to consider separated portions of a building as separate buildings does not apply to service rooms and storage rooms. | obc2019_divb | Div B | 3.2.4.2.(5) | 3.2.4.2. Continuity of Fire Alarm System | The permission in Sentence (4) to consider separated portions of a building as separate buildings does not apply to service rooms and storage rooms. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.2.(6) | Continuity of Fire Alarm System | Buildings interconnected by walkways permitted in Articles 3.2.3.19.and 3.2.3.20. or by vestibules provided in conformance with Article 3.2.6.3. shall be treated as separate buildings for the purpose of fire alarm installation required by this Subsection. | obc2019_divb | Div B | 3.2.4.2.(6) | 3.2.4.2. Continuity of Fire Alarm System | Buildings interconnected by walkways permitted in Articles 3.2.3.19. and 3.2.3.20. or by vestibules provided in conformance with Article 3.2.6.3. shall be treated as separate buildings for the purpose of fire alarm installation required by this Subsection. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.20.(1) | Smoke Alarms | Except as provided in Article 3.2.4.21., smoke alarms shall be installed in accordance with this Article. | obc2019_divb | Div B | 3.2.4.22.(1) | 3.2.4.22. Smoke Alarms | (0.1) Except as provided in Article 3.2.4.22A., smoke alarms shall be installed in accordance with this Article. Except as permitted by Sentence (6), smoke alarms conforming to CAN/ULC-S531, "Smoke Alarms", shall be installed in each dwelling unit and, except for care, care and treatment or detention occupancies required to have a fire alarm system, in each sleeping room not within a dwelling unit. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.20.(10) | Smoke Alarms | If more than one smoke alarm is required in a dwelling unit, the smoke alarms shall be wired so that the actuation of one smoke alarm will cause all smoke alarms within the dwelling unit to sound. | obc2019_divb | Div B | 3.2.4.22.(8) | 3.2.4.22. Smoke Alarms | If more than one smoke alarm is required in a dwelling unit, the smoke alarms shall be wired so that the actuation of one smoke alarm will cause all smoke alarms within the dwelling unit to sound. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.20.(11) | Smoke Alarms | A smoke alarm required by Sentence 3.2.4.20.(2) shall be installed in conformance with ULC CAN/ULC-S553-14 Installation of Smoke Alarms | obc2019_divb | Div B | 3.2.4.22.(9) | 3.2.4.22. Smoke Alarms | A smoke alarm required by Sentence (1) shall be installed in conformance with CAN/ULC-S553, "Installation of Smoke Alarms". |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.20.(12) | Smoke Alarms | Except as permitted in Sentence 3.2.4.20.(13), a manually operated silencing device shall be incorporated within the circuitry of a smoke alarm installed in a dwelling unit so that it will silence the signal emitted by the smoke alarm for a period of not more than 10 min, after which the smoke alarm will reset and again sound the alarm if the level of smoke in the vicinity is sufficient to reactuate the smoke alarm. | obc2019_divb | Div B | 3.2.4.22.(10) | 3.2.4.22. Smoke Alarms | Except as permitted by Sentence (11), a manually operated silencing device shall be incorporated within the circuitry of a smoke alarm installed in a dwelling unit so that it will silence the signal emitted by the smoke alarm for a period of not more than 10 min, after which the smoke alarm will reset and again sound the alarm if the level of smoke in the vicinity is sufficient to reactuate the smoke alarm. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.20.(13) | Smoke Alarms | Suites of residential occupancy equipped with smoke detectors installed to ULC CAN/ULC-S524-14 Installation of Fire Alarm Systems as part of the fire alarm system in lieu of smoke alarms as permitted by Sentence 3.2.4.20.(8), need not incorporate the manually operated device required in Sentence 3.2.4.20.(12). (See Note A-3.2.4.20.(8).) | obc2019_divb | Div B | 3.2.4.22.(11) | 3.2.4.22. Smoke Alarms | Suites of residential occupancy equipped with smoke detectors installed in conformance with CAN/ULC-S524, "Installation of Fire Alarm Systems", as part of the fire alarm system in lieu of smoke alarms as permitted by Sentence (6), need not incorporate the manually operated silencing device required by Sentence (10). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.20.(14) | Smoke Alarms | The sound patterns of smoke alarms shall meet the temporal patterns of alarm signals (see Note A-3.2.4.18.(2)), or be a combination temporal pattern and voice relay. | obc2019_divb | Div B | 3.2.4.22.(12) | 3.2.4.22. Smoke Alarms | The sound patterns of smoke alarms shall, meet the temporal patterns of alarm signals, or be a combination of temporal pattern and voice relay. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.20.(2) | Smoke Alarms | Except as required by Sentence 3.2.4.20.(5) and permitted by Sentence 3.2.4.20.(8), smoke alarms conforming to ULC CAN/ULC-S531-14 Smoke Alarms shall be installed in each dwelling unit and, except for care, treatment or detention occupancies required to have a fire alarm system, in each sleeping room not within a dwelling unit or suite of care occupancy. | obc2019_divb | Div B | 3.2.4.22.(1) | 3.2.4.22. Smoke Alarms | (0.1) Except as provided in Article 3.2.4.22A., smoke alarms shall be installed in accordance with this Article. Except as permitted by Sentence (6), smoke alarms conforming to CAN/ULC-S531, "Smoke Alarms", shall be installed in each dwelling unit and, except for care, care and treatment or detention occupancies required to have a fire alarm system, in each sleeping room not within a dwelling unit. |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.20.(3) | Smoke Alarms | At least one smoke alarm shall be installed on each storey of a dwelling unit or suite of care occupancy. | obc2019_divb | Div B | 3.2.4.22.(2) | 3.2.4.22. Smoke Alarms | At least one smoke alarm shall be installed on each storey and mezzanine of a dwelling unit. |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.20.(4) | Smoke Alarms | On any storey of a dwelling unit containing sleeping rooms, a smoke alarm shall be installed (a) in each sleeping room, and (b) in a location between the sleeping rooms and the remainder of the storey, and if the sleeping rooms are served by a hallway, the smoke alarm shall be located in the hallway. | obc2019_divb | Div B | 3.2.4.22.(3) | 3.2.4.22. Smoke Alarms | On any storey of a dwelling unit containing sleeping rooms, a smoke alarm shall be installed in, (a) each sleeping room, and (b) a location between the sleeping rooms and the remainder of the storey, and if the sleeping rooms are served by a hallway, the smoke alarm shall be located in the hallway. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.20.(6) | Smoke Alarms | A smoke alarm shall be installed on or near the ceiling. | obc2019_divb | Div B | 3.2.4.22.(4) | 3.2.4.22. Smoke Alarms | A smoke alarm shall be installed on or near the ceiling. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.20.(7) | Smoke Alarms | Except as permitted in Sentence 3.2.4.20.(8), smoke alarms referred in Sentence 3.2.4.20.(2) shall (a) be installed with permanent connections to an electrical circuit (see Note A-3.2.4.20.(7)(a)), (b) have no disconnect switch between the overcurrent device and the smoke alarm, and (c) in case the regular power supply to the smoke alarm is interrupted, be provided with a battery as an alternative power source that can continue to provide power to the smoke alarm for a period of no less than 7 days in the normal condition, followed by 4 minutes of alarm. | obc2019_divb | Div B | 3.2.4.22.(5) | 3.2.4.22. Smoke Alarms | Except as permitted by Sentence (6), smoke alarms required by Sentence (1) shall, (a) be installed with permanent connections to an electrical circuit, (b) have no disconnect switch between the overcurrent device and the smoke alarm, and (c) in case the regular power supply to the smoke alarm is interrupted, be provided with a battery as an alternative power source that can continue to provide power to the smoke alarm for a period of not less than seven days in the normal condition, followed by 4 min of alarm. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.20.(8) | Smoke Alarms | Suites of residential occupancy are permitted to be equipped with smoke detectors in lieu of smoke alarms, provided the smoke detectors (a) are capable of independently sounding audible signals within the individual suites, (b) except as permitted in Sentence 3.2.4.20.(9), are installed in conformance with ULC CAN/ULC-S524-14 Installation of Fire Alarm Systems and (c) form part of the fire alarm system. | obc2019_divb | Div B | 3.2.4.22.(6) | 3.2.4.22. Smoke Alarms | Suites of residential occupancy are permitted to be equipped with smoke detectors in lieu of smoke alarms, provided the smoke detectors, (a) are capable of independently sounding audible signals within the individual suites, (b) except as provided by Sentence (7), are installed in conformance with CAN/ULC-S524, "Installation of Fire Alarm Systems", and verified in conformance with CAN/ULC-S537, "Verification of Fire Alarm Systems", and (c) form part of the fire alarm system. |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.20.(9) | Smoke Alarms | Smoke detectors permitted to be installed in lieu of smoke alarms as stated in Sentence (8) are permitted to sound localized alarms within individual suites, and need not sound an alarm throughout the rest of the building. | obc2019_divb | Div B | 3.2.4.22.(7) | 3.2.4.22. Smoke Alarms | Smoke detectors permitted to be installed in lieu of smoke alarms as provided in Sentence (6) are not required under Clause (6)(b) to sound an alarm throughout the rest of the building, provided they sound localized alarms within individual suites and otherwise meet the requirements of Clause (6)(b). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.21.(1) | Residential Fire Warning Systems | Except where a fire alarm system is installed or required in a building, smoke detectors forming part of a residential fire warning system installed in conformance with ULC CAN/ULC-S540-13 Residential Fire and Life Safety Warning Systems: Installation, Inspection, Testing and Maintenance are permitted to be installed in lieu of all smoke alarms required by Article 3.2.4.20., provided the system (a) is capable of sounding audible signals in accordance with Articles 9.10.19.2. and Article 9.10.19.5., (b) is powered in accordance with Article 9.10.19.4., and (c) is provided with a silencing device in accordance with Article 9.10.19.6. | obc2019_divb | Div B | 3.2.4.22.(1) | 3.2.4.22A. Residential Fire Warning Systems | Except where a fire alarm system is installed or required in a building, smoke detectors forming part of a residential fire warning system installed in conformance with CAN/ULC-S540, "Residential Fire and Life Safety Warning Systems: Installation, Inspection, Testing and Maintenance", are permitted to be installed in lieu of all smoke alarms required by Article 3.2.4.22., provided that the system is, (a) capable of sounding audible signals in accordance with Sentences 3.2.4.22.(8) and (12), (b) provided with a visual signalling component in accordance with Sentences 3.2.4.22.(13) to (15), (c) powered in accordance with Sentences 3.2.4.22.(5), and (d) provided with a silencing device in accordance with Sentences 3.2.4.22.(10) and (11). |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.22.(1) | Voice Communication Systems for High Buildings | A voice communication system required by Subsection 3.2.6. shall (a) consist of a two-way means of communication with the central alarm and control facility and to the mechanical control centre from each floor area, and (b) be capable of broadcasting prerecorded, synthesized, or live messages from the central alarm and control facility that are audible and intelligible in all parts of the building, except that this requirement does not apply to elevator cars (see Note A-3.2.4.22.(1)(b)). | obc2019_divb | Div B | 3.2.4.23.(1) | 3.2.4.23. Two-Way Voice Communication Systems | A voice communication system required by Subsection 3.2.6., Clause 3.3.2.4.(14)(f) or Sentence 3.3.4.11.(12) shall, (a) consist of a two-way means of communication with the central alarm and control facility and with the mechanical control centre from each floor area, and (b) be capable of broadcasting pre-recorded, synthesized or live messages from the central alarm and control facility that are audible and intelligible in all parts of the building, except in elevator cars. |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.22.(2) | Voice Communication Systems for High Buildings | The voice communication system referred to in Sentence 3.2.4.22.(1) shall include a means to silence the alarm signal in a single stage fire alarm system while voice instructions are being transmitted, but only after the alarm signal has initially sounded for not less than 30 s. | obc2019_divb | Div B | 3.2.4.23.(2) | 3.2.4.23. Two-Way Voice Communication Systems | The voice communication system referred to in Sentence (1) shall include a means to silence the alarm signal in a single-stage fire alarm system while voice messages are being transmitted, but only after the alarm signal has initially sounded for not less than 30 s. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.22.(3) | Voice Communication Systems for High Buildings | The voice communication system referred to in Sentence 3.2.4.22.(1) shall include a means to silence the alert signal and the alarm signal in a 2-stage fire alarm system while voice instructions are being transmitted, but only after the alert signal has initially sounded for not less than (a) 10 s in hospitals that have supervisory personnel on duty for twenty-four hours each day, or (b) 30 s for all other occupancies. | obc2019_divb | Div B | 3.2.4.23.(3) | 3.2.4.23. Two-Way Voice Communication Systems | The voice communication system referred to in Sentence (1) shall include a means to silence the alert signal and the alarm signal in a two-stage fire alarm system while voice messages are being transmitted, but only after the alert signal has initially sounded for not less than, (a) 10 s in hospitals that have supervisory personnel on duty for twenty-four hours each day, or (b) 30 s for all other occupancies. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.22.(4) | Voice Communication Systems for High Buildings | The voice communication system referred to in Clause 3.2.4.22.(1)(b) shall be designed so that the alarm signal in a 2-stage fire alarm system can be selectively transmitted to any zone or zones while maintaining an alert signal or selectively transmitting voice instructions to any other zone or zones in the building. | obc2019_divb | Div B | 3.2.4.23.(4) | 3.2.4.23. Two-Way Voice Communication Systems | The voice communication system referred to in Sentence (1) shall be designed so that the alarm signal in a two-stage fire alarm system can be selectively transmitted to any zone or zones while maintaining an alert signal or selectively transmitting voice instructions to any other zone or zones in the building. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.22.(5) | Voice Communication Systems for High Buildings | Visual signal devices required by Sentence 3.2.4.19.(1) shall continue to emit a visible signal while voice instructions are being transmitted. | obc2019_divb | Div B | 3.2.4.23.(5) | 3.2.4.23. Two-Way Voice Communication Systems | The voice communication system referred to in Sentence (1) shall be designed so that visual signal devices are not interrupted while voice instructions are being transmitted. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.22.(6) | Voice Communication Systems for High Buildings | The 2-way communication system referred to in Clause 3.2.4.22.(1)(a) shall be installed so that emergency telephones are located in each floor area near exit stair shafts. | obc2019_divb | Div B | 3.2.4.23.(6) | 3.2.4.23. Two-Way Voice Communication Systems | The voice communication system referred to in Sentence (1) shall be installed so that emergency communication devices are located in each floor area near exit stair shafts. |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.22.(7) | Voice Communication Systems for High Buildings | Where the facility is not equipped with staff trained to provide instructions over the loudspeakers, a pre-recorded message shall be provided. | obc2019_divb | Div B | 3.2.4.23.(7) | 3.2.4.23. Two-Way Voice Communication Systems | A voice communication system referred to in Sentence (1) that is installed in a building that is not intended to be staffed, at times when the building will be occupied, with persons trained to provide instructions over the system shall include a pre-recorded message. |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.23.(1) | One-Way Voice Communication Systems | Except for Group B, Division 1 and Group F, Division 1 major occupancies, where a fire alarm system is required under part 3., a one-way voice communication system shall be installed in buildings where a 2-stage fire alarm system is installed and whose occupant load exceeds 1 000. | obc2019_divb | Div B | 3.2.4.24.(1) | 3.2.4.24. One-Way Voice Communication Systems | Except for Group B, Division 1 and Group F, Division 1 major occupancies, a one-way voice communication system shall be installed in a building where, a fire alarm system is required under Subsection 3.2.4., a two-stage fire alarm system is installed, and the occupant load of the building exceeds 1 000. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.23.(2) | One-Way Voice Communication Systems | The one-way voice communication system required by Sentence 3.2.4.23.(1) shall consist of loudspeakers that are operated from the central alarm and control facility or, in the absence of such a facility, from a designated area, and except in elevator cars, designed and located so that transmitted messages are audible and intelligible in all parts of the building. | obc2019_divb | Div B | 3.2.4.24.(2) | 3.2.4.24. One-Way Voice Communication Systems | The voice communication system required by Sentence (1) shall consist of loudspeakers that are, operated from the central alarm and control facility or, in the absence of a central alarm and control facility, from a designated area, and designed and located so that transmitted messages are audible and intelligible in all parts of the building, except in elevator cars. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.23.(3) | One-Way Voice Communication Systems | Where the facility is not equipped with staff trained to provide instructions over the loudspeakers, a pre-recorded message shall be provided. | obc2019_divb | Div B | 3.2.4.24.(3) | 3.2.4.24. One-Way Voice Communication Systems | A voice communication system required by Sentence (1) that is installed in a building that is not intended to be staffed, at times when the building will be occupied, with persons trained to provide instructions over loudspeakers described in Sentence (2) shall include a pre-recorded message. |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.23.(4) | One-Way Voice Communication Systems | The one-way voice communication system required by Sentence 3.2.4.23.(1) shall meet the silencing and transmission requirements of Sentences 3.2.4.22.(2) to 3.2.4.22.(4) and 3.2.4.22.(6). | obc2019_divb | Div B | 3.2.4.24.(4) | 3.2.4.24. One-Way Voice Communication Systems | The voice communication system required by Sentence (1) shall meet the silencing and transmission requirements of Sentences 3.2.4.23.(2) to (5). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.3.(1) | Types of Fire Alarm Systems | A fire alarm system shall be (a) a single-stage system in a Group F, Division 1 occupancy, (b) except as permitted in Sentence 3.2.4.3.(1), a 2-stage system in a Group B occupancy, (c) a single- or 2-stage system in a Group B, Division 3 occupancy where the building is 3 storeys or less in building height, and (d) a single- or 2-stage system in all other cases. | obc2019_divb | Div B | 3.2.4.3.(1) | 3.2.4.3. Types of Fire Alarm Systems | A fire alarm system shall be, (a) a single stage system in a Group F, Division 1 occupancy, (b) a two stage system in a Group B occupancy other than those described in Clause (c), (c) a single or two stage system in a building 3 storeys or less in building height that contains a Group B, Division 3 occupancy, (d) a single stage system in elementary and secondary schools, except for a special needs facility, and (e) a single or two stage system in all other cases. |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.4.(1) | Description of Fire Alarm Systems | A single stage fire alarm system shall, upon the operation of any manual station, waterflow detecting device, or fire detector, cause an alarm signal to sound on all audible signal devices in the system. (See Note A-3.2.4.4.(1).) | obc2019_divb | Div B | 3.2.4.4.(1) | 3.2.4.4. Description of Fire Alarm Systems | A single stage fire alarm system shall, upon the operation of any manual pull station or fire detector, cause an alarm signal to sound on all audible signal devices in the system. (See Appendix A.) |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.4.(2) | Description of Fire Alarm Systems | A 2-stage fire alarm system shall (a) cause an alert signal to sound upon the operation of any manual station, waterflow detecting device, or fire detector, (b) automatically cause an alarm signal to sound if the alert signal is not acknowledged within 5 min of its initiation, and (c) have manual stations, each of which is equipped so that the use of a key or other similar device causes an alarm signal to sound that continues to sound upon removal of the key or similar device from the manual station (see Note A-3.2.4.4.(2)(c)). | obc2019_divb | Div B | 3.2.4.4.(2) | 3.2.4.4. Description of Fire Alarm Systems | A two stage fire alarm system shall, (a) cause an alert signal to sound upon the operation of any manual pull station or fire detector, (b) except for a Group B, Division 2 occupancy, automatically cause an alarm signal to sound if the alert signal is not acknowledged within 5 min of its initiation, (c) have each manual pull station equipped so that the use of a key or other similar device causes an alarm signal to sound and continue to sound upon the removal of the key or similar device from the manual pull station, and (See Appendix A.) (d) in a building containing a hotel, (i) cause an alarm signal to sound in the initiating fire zone in the hotel, and (ii) cause an alert signal to sound throughout the hotel and such parts of the building as is necessary to alert hotel staff. |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.4.(3) | Description of Fire Alarm Systems | A 2-stage fire alarm system is permitted to be zone coded so that, upon the operation of any manual station, waterflow detecting device, or fire detector, (a) a coded alert signal is sounded indicating the zone of alarm initiation, (b) the coded alert signal is repeated in its entirety not less than 4 times, and (c) a continuous alert signal is sounded upon completion of the coded signals referred to in Clause 3.2.4.4.(3)(b) and Sentence 3.2.4.4.(4). | obc2019_divb | Div B | 3.2.4.4.(3) | 3.2.4.4. Description of Fire Alarm Systems | A two stage fire alarm system is permitted to be zone coded so that, upon the operation of any manual pull station or fire detector, (a) a coded alert signal is sounded indicating the zone of alarm initiation, (b) the coded alert signal is repeated in its entirety no fewer than four times, and (c) a continuous alert signal is sounded upon completion of the coded signals referred to in Clause (b) and Sentence (4). |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.4.(4) | Description of Fire Alarm Systems | If a second manual station, waterflow detecting device, or fire detector is operated in a fire alarm system with zone coding as permitted by Sentence 3.2.4.4.(3), in a zone other than that for which the first alert signal was sounded, the coded alert signal for the first zone shall be completed before the coded alert signal for the second zone is repeated not less than 4 times. | obc2019_divb | Div B | 3.2.4.4.(4) | 3.2.4.4. Description of Fire Alarm Systems | If a second manual pull station or fire detector is operated in a fire alarm system with zone coding as permitted by Sentence (3), in a zone other than that for which the first alert signal was sounded, the coded alert signal for the first zone shall be completed before the coded alert signal for the second zone is repeated no fewer than four times. |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.5.(1) | Installation and Verification of Fire Alarm Systems | Fire alarm systems, including the voice communication capability where provided, shall be installed in conformance with ULC CAN/ULC-S524-14 Installation of Fire Alarm Systems | obc2019_divb | Div B | 3.2.4.5.(1) | 3.2.4.5. Installation and Verification of Fire Alarm Systems | Fire alarm systems, including those with voice communication capability, shall be installed in conformance with CAN/ULC-S524, "Installation of Fire Alarm Systems". |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.5.(2) | Installation and Verification of Fire Alarm Systems | Fire alarm systems shall be verified in conformance with ULC CAN/ULC-S537-13 Verification of Fire Alarm Systems to ensure they are operating satisfactorily. | obc2019_divb | Div B | 3.2.4.5.(2) | 3.2.4.5. Installation and Verification of Fire Alarm Systems | A fire alarm system shall be verified in conformance with CAN/ULC-S537, "Verification of Fire Alarm Systems", to ensure satisfactory operation. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.6.(1) | Silencing of Alarm Signals | A fire alarm system shall be designed so that when an alarm signal is actuated, it cannot be silenced automatically before a period of time has elapsed that is not less than 5 min for a building not required to be equipped with an annunciator, and 20 min for any other building. | obc2019_divb | Div B | 3.2.4.7.(1) | 3.2.4.7. Silencing of Alarm Signals | Except as permitted by Sentence (3), a fire alarm system shall be designed so that when an alarm signal is actuated it cannot be silenced automatically before a period of time has elapsed that is not less than, 5 min for a building not required to be equipped with an annunciator, and 20 min for any other building. |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.6.(2) | Silencing of Alarm Signals | Except as permitted by Sentence 3.2.4.18.(7) and Sentences 3.2.4.22.(2) and 3.2.4.22.(3), a fire alarm system shall not incorporate manual silencing switches other than those installed inside the fire alarm control unit. (See Note A-3.2.4.6.(2).) | obc2019_divb | Div B | 3.2.4.7.(2) | 3.2.4.7. Silencing of Alarm Signals | Except as permitted by Sentences 3.2.4.20.(9) and 3.2.4.23.(2) and (3), a fire alarm system shall not incorporate manual silencing switches other than those installed inside the fire alarm control unit. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.7.(1) | Signals to Fire Department | A single stage fire alarm system installed in a building of assembly occupancy that has an occupant load more than 300 shall be designed to notify the fire department, in conformance with Sentence (4), that an alarm signal has been initiated. | obc2019_divb | Div B | 3.2.4.8.(1) | 3.2.4.8. Signals to Fire Department | If a fire alarm system is required to be installed and a single stage system is provided, the system shall be designed to notify the fire department in conformance with Sentence (4) that an alarm signal has been initiated in, (a) a Group A occupancy having an occupant load more than 300, (b) a Group B occupancy, (c) a Group F, Division 1 occupancy, (d) a building regulated by the provisions of Subsection 3.2.6., (e) a building containing interconnected floor space required to conform to Articles 3.2.8.3. to 3.2.8.11., or (f) a retirement home. |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.7.(2) | Signals to Fire Department | A fire alarm system that includes waterflow-indicating devices shall be designed to notify the fire department in conformance with Sentence 3.2.4.7.(4) when an alarm is initiated. | obc2019_divb | Div B | 3.2.4.8.(2) | 3.2.4.8. Signals to Fire Department | A fire alarm system that includes waterflow indicating devices shall be designed to notify the fire department, in conformance with Sentence (4), that an alarm has been initiated. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.7.(3) | Signals to Fire Department | A 2-stage fire alarm system shall be designed to notify the fire department, in conformance with Sentence 3.2.4.7.(4), that an alert signal has been initiated. | obc2019_divb | Div B | 3.2.4.8.(3) | 3.2.4.8. Signals to Fire Department | If a fire alarm system is required to be installed and a two stage system is provided, the system shall be designed to notify the fire department, in conformance with Sentence (4), that an alert signal has been initiated. |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.7.(4) | Signals to Fire Department | Notification of the fire department, as required by Sentences 3.2.4.7.(1) , 3.2.4.7.(2) and 3.2.4.7.(3), shall be provided in conformance with ULC CAN/ULC-S561-13 Installation and Services for Fire Signal Receiving Centres and Systems (See Note A-3.2.4.7.(4).) | obc2019_divb | Div B | 3.2.4.8.(4) | 3.2.4.8. Signals to Fire Department | Notification of the fire department required by Sentences (1) to (3) shall be by way of, (a) signals to a central station conforming to CAN/ULC-S561, "Installation and Services for Fire Signal Receiving Centres and Systems", or (b) the municipal fire alarm system. |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.7.(5) | Signals to Fire Department | Where a single stage fire alarm system is installed in a building that is not sprinklered throughout and Sentence 3.2.4.7.(1) does not apply, a legible notice that is not easily removed shall be affixed to the wall near each manual station stating that the fire department is to be notified in the event of a fire emergency, and the emergency telephone number for the municipality or for the fire department (see Note A-3.2.4.7.(5)(b)). | obc2019_divb | Div B | 3.2.4.8.(5) | 3.2.4.8. Signals to Fire Department | Where a single stage fire alarm system is installed in a building that is not sprinklered, and Sentence (1) does not apply, a legible notice, that is not easily removed, shall be affixed to the wall near each manual pull station stating, that the fire department is to be notified in the event of a fire emergency, and the emergency telephone number for the municipality or the telephone number of the fire department. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.8.(1) | Annunciator and Zone Indication | Except as permitted by Sentences 3.2.4.8.(3) to 3.2.4.8.(5), an annunciator shall be installed in close proximity to a building entrance that faces a street or an access route for fire department vehicles that complies with Sentence 3.2.5.5.(1). | obc2019_divb | Div B | 3.2.4.9.(1) | 3.2.4.9. Annunciator and Zone Indication | Except as permitted by Sentences (3) to (5), an annunciator shall be installed in close proximity to a building entrance that faces a street or an access route for fire department vehicles that complies with Sentence 3.2.5.5.(1). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.8.(2) | Annunciator and Zone Indication | Except as permitted by Sentence 3.2.4.8.(6), the annunciator required by Sentence 3.2.4.8.(1) shall have separate zone indication of the actuation of the alarm initiating devices in each (a) floor area so that the area of coverage for each zone in a building that is not sprinklered is not more than 2?000 m2 , (b) floor area so that the area of coverage for each zone is neither (i) more than one storey, nor (ii) more than the system area limits specified in NFPA 13-2013 Installation of Sprinkler Systems (c) shaft required to be equipped with smoke detectors, (d) air-handling system required to be equipped with smoke detectors, (e) fire extinguishing system required by NFPA 96-2014 Ventilation Control and Fire Protection of Commercial Cooking Operations (f) contained use area, (g) impeded egress zone, and (h) fire compartment required by Sentence 3.3.3.5.(2). | obc2019_divb | Div B | 3.2.4.9.(2) | 3.2.4.9. Annunciator and Zone Indication | Except as permitted by Sentence (6), the annunciator required by Sentence (1) shall have separate zone indication of the actuation of the alarm initiating devices in each, (a) floor area so that in a building that is not sprinklered, the area of coverage for each zone is neither more than, (i) 1 storey, nor (ii) 2000 m2, (b) floor area so that in a building that is sprinklered, the area of coverage for each zone is neither more than, (i) 1 storey, nor (ii) the system area limits as specified in NFPA 13, "Installation of Sprinkler Systems", (c) shaft required to be equipped with fire detectors, (d) air handling system required to be equipped with smoke detectors, (e) fire extinguishing system required by NFPA 96, "Ventilation Control and Fire Protection of Commercial Cooking Operations", (f) contained use area, (g) impeded egress zone, (h) fire compartment required by Sentence 3.3.3.5.(2) or Sentence 3.3.4.11.(2), and (i) fire compartment required to be separated by vertical fire separations having a fire-resistance rating not less than 2 h, other than dwelling units described in Subsection 3.3.4. |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.8.(3) | Annunciator and Zone Indication | An annunciator need not be provided for a fire alarm system if not more than one zone indicator is required by Sentence 3.2.4.8.(2). | obc2019_divb | Div B | 3.2.4.9.(3) | 3.2.4.9. Annunciator and Zone Indication | An annunciator need not be provided for a fire alarm system if not more than one zone indicator is required in Sentence (2). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.8.(4) | Annunciator and Zone Indication | If an annunciator is not installed as part of a fire alarm system in conformance with Sentence 3.2.4.8.(1), a visual and audible trouble signal device shall be provided inside the main entrance of the building. | obc2019_divb | Div B | 3.2.4.9.(4) | 3.2.4.9. Annunciator and Zone Indication | If an annunciator is not installed as part of a fire alarm system in conformance with Sentence (1), a visual and audible trouble signal device shall be provided inside the main entrance of the building. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.8.(5) | Annunciator and Zone Indication | The requirements of Sentence 3.2.4.8.(1) are waived in a building in which an automatic sprinkler system is not installed, that has an aggregate area for all storeys of not more than 2?000 m2 , and that is not more than 3 storeys in building height. | obc2019_divb | Div B | 3.2.4.9.(5) | 3.2.4.9. Annunciator and Zone Indication | The requirements in Sentence (1) are waived in a building, reserved that has an aggregate area for all storeys of not more than 2 000 m2, and that is not more than 3 storeys in building height. |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.8.(6) | Annunciator and Zone Indication | The area limits of Sentence 3.2.4.8.(2) are waived for an interior undivided open space used as an arena, a rink, or a swimming pool provided that other spaces in the building that are separated from the open space are individually zoned in accordance with the requirements of Sentence 3.2.4.8.(2). | obc2019_divb | Div B | 3.2.4.9.(6) | 3.2.4.9. Annunciator and Zone Indication | The area limits of Clause (2)(a) are waived for an interior undivided open space used as an arena, a rink or a swimming pool provided that other spaces in the building that are separated from the open space are individually zoned in accordance with the requirements of Sentence (2). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.8.(7) | Annunciator and Zone Indication | A fire alarm control unit installed in close proximity to a building entrance that faces a street or an access route for fire department vehicles that complies with Sentence 3.2.5.5.(1) is deemed to satisfy the requirement for an annunciator, provided all indicators required for an annunciator or trouble signal device are included on the control unit. | obc2019_divb | Div B | 3.2.4.9.(7) | 3.2.4.9. Annunciator and Zone Indication | A fire alarm control unit installed in close proximity to a building entrance that faces a street or an access route for fire department vehicles that complies with Sentence 3.2.5.5.(1), is deemed to satisfy the requirement for an annunciator provided all indicators required for an annunciator or trouble signal device are included on the control unit. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.9.(1) | Electrical Supervision | Electrical supervision shall be provided for a fire alarm system. | obc2019_divb | Div B | 3.2.4.10.(1) | 3.2.4.10. Electrical Supervision | Electrical supervision shall be provided for a fire alarm system. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.9.(2) | Electrical Supervision | If a fire alarm system in a building is required to have an annunciator by Sentence 3.2.4.8.(1), except for hose valves, all valves controlling water supplies in a standpipe system shall be equipped with an electrically supervised switch for transmitting a trouble signal to the annunciator in the event of movement of the valve handle. | obc2019_divb | Div B | 3.2.4.10.(2) | 3.2.4.10. Electrical Supervision | If a fire alarm system in a building is required by Sentence 3.2.4.9.(1) to have an annunciator, each valve controlling water supplies in a standpipe system, except for hose valves, shall be equipped with an electrically supervised switch for transmitting a trouble signal to the annunciator in the event of movement of the valve handle. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.4.9.(3) | Electrical Supervision | An automatic sprinkler system shall be electrically supervised to indicate a supervisory signal on the building fire alarm system annunciator for each of the following: (a) movement of a valve handle that controls the supply of water to sprinklers, (b) loss of excess water pressure required to prevent false alarms in a wet pipe system, (c) loss of air pressure in a dry pipe system, (d) loss of air pressure in a pressure tank, (e) a significant change in water level in any water storage container used for firefighting purposes, (f) loss of power to any automatically starting fire pump (see Note A-3.2.4.9.(3)(f) ), and (g) a temperature approaching the freezing point in any dry pipe valve enclosure or water storage container used for firefighting purposes. | obc2019_divb | Div B | 3.2.4.10.(3) | 3.2.4.10. Electrical Supervision | If a fire alarm system is installed in a building, an automatic sprinkler system shall be electrically supervised to indicate a supervisory signal on the building fire alarm system annunciator for each of the following, (a) movement of a valve handle that controls the supply of water to sprinklers, (b) loss of excess water pressure required to prevent false alarms in a wet pipe system, (c) loss of air pressure in a dry pipe system, (d) loss of air pressure in a pressure tank, (e) a significant change in water level in any water storage container used for firefighting purposes, (f) loss of power to any automatically starting fire pump, and (g) a temperature approaching the freezing point in any dry pipe valve enclosure or water storage container used for firefighting purposes. |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.9.(4) | Electrical Supervision | A fire pump shall be electrically supervised as stipulated in NFPA 20-2016 Installation of Stationary Pumps for Fire Protection | obc2019_divb | Div B | 3.2.4.10.(4) | 3.2.4.10. Electrical Supervision | If a fire alarm system is installed in a building, a fire pump shall be electrically supervised in accordance with NFPA 20, "Installation of Stationary Pumps for Fire Protection". |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.9.(5) | Electrical Supervision | Indication of a supervisory signal in accordance with Sentence 3.2.4.9.(3) shall be transmitted to the fire department in conformance with Sentence 3.2.4.7.(4). | obc2019_divb | Div B | 3.2.4.10.(6) | 3.2.4.10. Electrical Supervision | In a building regulated by the provisions of Subsection 3.2.6., the indication of a supervisory signal in accordance with Sentence (3) shall be transmitted to a proprietary control centre or to an independent central station. |  | Common Sentence | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.5.1.(1) | Access to Above-Grade Storeys | Except for storeys below the first storey, direct access for firefighting shall be provided from the outdoors to every storey that is not sprinklered throughout and whose floor level is less than 25 m above grade, by at least one unobstructed window or access panel for each 15 m of wall in each wall required to face a street by part 3. | obc2019_divb | Div B | 3.2.5.1.(1) | 3.2.5.1. Access to Above Grade Storeys | Except for storeys below the first storey, direct access for firefighting shall be provided from the outdoors to every storey that is not sprinklered and whose floor level is less than 25 m above grade, by at least one unobstructed window or access panel for each 15 m of wall in each wall required to face a street by Subsection 3.2.2. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.5.1.(2) | Access to Above-Grade Storeys | An opening for access required by Sentence 3.2.5.1.(1) shall have a sill no higher than 900 mm above the inside floor, and be not less than 1?100 mm high by not less than 550 mm wide for a building not designed for the storage or use of dangerous goods, or 750 mm wide for a building designed for the storage or use of dangerous goods. | obc2019_divb | Div B | 3.2.5.1.(2) | 3.2.5.1. Access to Above Grade Storeys | An opening for access required by Sentence (1) shall, have a sill no higher than 1 070 mm above the inside floor, and be not less than 1 100 mm high by not less than, 550 mm wide for a building not designed for the storage or use of dangerous goods, or 750 mm wide for a building designed for the storage or use of dangerous goods. |  | Common Sentence | Yes | Emergency Response
2015 | ON | NBC | Div B | 3.2.5.1.(3) | Access to Above-Grade Storeys | Access panels above the first storey shall be readily openable from both inside and outside, or the opening shall be glazed with plain glass. | obc2019_divb | Div B | 3.2.5.1.(3) | 3.2.5.1. Access to Above Grade Storeys | Access panels above the first storey shall be readily openable from both inside and outside, or the opening shall be glazed with plain glass. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.5.11.(4) | Hose Stations | A hose station located on one side of a horizontal exit shall be considered to serve only the floor area on that side of the horizontal exit. | obc2019_divb | Div B | 3.2.9.4.(8) | 3.2.9.4. Hose Stations | A hose station located on one side of a horizontal exit shall be considered to serve only the floor area on that side of the horizontal exit. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.5.11.(5) | Hose Stations | A hose cabinet shall be located so that its door, when fully opened, will not obstruct the required width of a means of egress. | obc2019_divb | Div B | 3.2.9.4.(9) | 3.2.9.4. Hose Stations | A hose cabinet shall be located so that its door, when fully opened, will not obstruct the required width of a means of egress. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.5.12.(1) | Automatic Sprinkler Systems | Except as permitted by Sentences 3.2.5.12.(2) , 3.2.5.12.(3) and 3.2.5.12.(4), an automatic sprinkler system shall be designed, constructed, installed and tested in conformance with NFPA 13-2013 Installation of Sprinkler Systems (See Note A-3.2.5.12.(1).) | obc2019_divb | Div B | 3.2.5.13.(1) | 3.2.5.13. Automatic Sprinkler Systems | Except as provided by Sentences (2) to (4), an automatic sprinkler system shall be designed, constructed, installed and tested in conformance with NFPA 13, "Installation of Sprinkler Systems". (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.5.12.(2) | Automatic Sprinkler Systems | Instead of the requirements of Sentence (1), NFPA 13R, “Installation of Sprinkler Systems in Low-Rise Residential Occupancies,” is permitted to be used for the design, construction and installation of an automatic sprinkler system installed (a) in a building of residential occupancy throughout that (i) is not more than 4 storeys in building height and conforms to Articles 3.2.2.47., 3.2.2.48., 3.2.2.50., 3.2.2.51. or 3.2.2.54., or (ii) is not more than 3 storeys in building height and conforms to Article 9.10.1.3., or (b) in a building of care occupancy with not more than 10 occupants that is not more than 3 storeys in building height and conforms to one of Articles 3.2.2.42. to 3.2.2.46. (See Note A-3.2.5.12.(2).) | obc2019_divb | Div B | 3.2.5.13.(2) | 3.2.5.13. Automatic Sprinkler Systems | NFPA 13R, "Installation of Sprinkler Systems in Low-Rise Residential Occupancies", is permitted to be used for the design, construction, installation and testing of an automatic sprinkler system installed in a building, (a) of residential occupancy that does not contain a retirement home and that is not more than 4 storeys in building height, (b) of Group B, Division 3 occupancy that contains sleeping accommodation for not more than 10 persons and not more than six occupants require assistance in evacuation in case of an emergency, (c) that contains a retirement home constructed in accordance with Article 3.2.2.48D., or (d) that contains a retirement home constructed in accordance with Article 3.2.2.48E., where the fire separation required by Sentence 3.3.4.11.(2) on the storey immediately below the roof assembly is continuous to the underside of the roof deck. |  | Common Sentence | Yes | Retirement Homes
2015 | ON | NBC | Div B | 3.2.5.12.(3) | Automatic Sprinkler Systems | Instead of the requirements of Sentence 3.2.5.12.(1), NFPA 13D-2016 Installation of Sprinkler Systems in One- and Two-Family Dwellings and Manufactured Homes is permitted to be used for the design, construction and installation of an automatic sprinkler system installed (a) in a building of residential occupancy throughout that contains not more than 2 dwelling units, or (b) in a building of care occupancy, provided (i) it contains not more than 2 suites of care occupancy, (ii) it has not more than 5 residents throughout, and (iii) a 30-minute water supply demand can be met. | obc2019_divb | Div B | 3.2.5.13.(3) | 3.2.5.13. Automatic Sprinkler Systems | Except as required by Sentence (9), NFPA 13D, "Installation of Sprinkler Systems in One- and Two-Family Dwellings and Manufactured Homes", is permitted to be used for the design, construction, installation and testing of an automatic sprinkler system installed in a building of residential occupancy that contains not more than two dwelling units. |  | Common Sentence | Yes | Fire Suppression
2015 | ON | NBC | Div B | 3.2.5.12.(4) | Automatic Sprinkler Systems | If a building contains fewer than 9 sprinklers, the water supply for these sprinklers is permitted to be supplied from the domestic water system for the building provided the required flow for the sprinklers can be met by the domestic system. | obc2019_divb | Div B | 3.2.5.13.(4) | 3.2.5.13. Automatic Sprinkler Systems | If a building contains fewer than nine sprinklers, the water supply for these sprinklers is permitted to be supplied from the domestic water system for the building provided the required flow for the sprinklers can be met by the domestic system. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.5.12.(5) | Automatic Sprinkler Systems | If a water supply serves both an automatic sprinkler system and a system serving other equipment, control valves shall be provided so that either system can be shut off independently. | obc2019_divb | Div B | 3.2.5.13.(5) | 3.2.5.13. Automatic Sprinkler Systems | If a water supply serves both an automatic sprinkler system and a system serving other equipment, control valves shall be provided so that either system can be shut off independently. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.5.12.(6) | Automatic Sprinkler Systems | Notwithstanding the requirements of the standards referenced in Sentences 3.2.5.12.(1) and 3.2.5.12.(2) regarding the installation of automatic sprinkler systems, sprinklers shall not be omitted in any room or closet in the storey immediately below a roof assembly. (See Note A-3.2.5.12.(6).) | obc2019_divb | Div B | 3.2.5.13.(6) | 3.2.5.13. Automatic Sprinkler Systems | Despite the requirements of the standards referenced in Sentences (1) and (2) for the installation of automatic sprinkler systems, sprinklers shall not be omitted in any room or closet in the storey immediately below a roof assembly if the fire-resistance rating of the roof assembly is waived as permitted by Article 3.2.2.17. (See Appendix A.) |  | Common Sentence | Yes | Fire Suppression
2015 | ON | NBC | Div B | 3.2.5.12.(7) | Automatic Sprinkler Systems | Notwithstanding the requirements of the standards referenced in Sentences 3.2.5.12.(1) and 3.2.5.12.(2) regarding the installation of automatic sprinkler systems, in buildings conforming to Article 3.2.2.50. or 3.2.2.58., sprinklers shall be provided for balconies and decks exceeding 610 mm in depth measured perpendicular to the exterior wall. (See Note A-3.2.5.12.(7).) | obc2019_divb | Div B | 3.2.5.13.(7) | 3.2.5.13. Automatic Sprinkler Systems | Despite the requirements of the standards referenced in Sentences (1) and (2) for the installation of automatic sprinkler systems, sprinklers shall be provided for all balconies and decks forming part of a building within the scope of Article 3.2.2.43A. or 3.2.2.50A., other than, (a) balconies or decks that are not more than 610 mm in depth measured perpendicular to the exterior wall of the building, or decks on the uppermost roof of the building. (See Appendix A.) |  | Common Sentence | Yes | Fire Suppression
2015 | ON | NBC | Div B | 3.2.5.12.(8) | Automatic Sprinkler Systems | Sprinklers in elevator machine rooms shall have a temperature rating not less than that required for an intermediate temperature classification and shall be protected against physical damage. (See Note A-3.2.5.12.(8).) | obc2019_divb | Div B | 3.2.5.13.(8) | 3.2.5.13. Automatic Sprinkler Systems | Sprinklers in elevator machine rooms shall have a temperature rating not less than that required for an intermediate temperature classification and shall be protected against physical damage. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.5.13.(1) | Combustible Sprinkler Piping | Combustible sprinkler piping shall be used only for sprinkler systems in residential occupancies and other light-hazard occupancies. (See Note A-3.2.5.13.(1).) | obc2019_divb | Div B | 3.2.5.14.(1) | 3.2.5.14. Combustible Sprinkler Piping | Combustible sprinkler piping shall be used only for sprinkler systems in residential occupancies and other light hazard occupancies. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.5.13.(2) | Combustible Sprinkler Piping | Combustible sprinkler piping shall meet the requirements of ULC ULC/ORD-C199P-2002 Combustible Piping for Sprinkler Systems | obc2019_divb | Div B | 3.2.5.14.(2) | 3.2.5.14. Combustible Sprinkler Piping | Combustible sprinkler piping shall meet the requirements of ULC/ORD-C199P, "Combustible Piping for Sprinkler Systems". |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.5.13.(3) | Combustible Sprinkler Piping | Except as permitted by Sentence 3.2.5.13.(5), combustible sprinkler piping shall be separated from the area served by the sprinkler system, and from any other fire compartment, by ceilings, walls, or soffits consisting of, as a minimum, lath and plaster, gypsum board not less than 9.5 mm thick, plywood not less than 13 mm thick, or a suspended membrane ceiling with steel suspension grids, and lay-in panels or tiles having a mass not less than 1.7 kg/m2 . | obc2019_divb | Div B | 3.2.5.14.(3) | 3.2.5.14. Combustible Sprinkler Piping | Except as permitted by Sentence (5), combustible sprinkler piping shall be separated from the area served by the sprinkler system, and from any other fire compartment, by ceilings, walls, or soffits consisting of, as a minimum, lath and plaster, gypsum board not less than 9.5 mm thick, plywood not less than 13 mm thick, or a suspended membrane ceiling with, steel suspension grids, and lay-in panels or tiles having a mass not less than 1.7 kg/m2. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.5.13.(4) | Combustible Sprinkler Piping | Except as permitted by Sentence 3.2.5.13.(5), combustible sprinkler piping may be located above a ceiling provided that the distance between the edge of any ceiling opening that is not protected in conformance with Sentence 3.2.5.13.(3) and the nearest sprinkler is not more than 300 mm. | obc2019_divb | Div B | 3.2.5.14.(4) | 3.2.5.14. Combustible Sprinkler Piping | Except as permitted by Sentence (5), combustible sprinkler piping may be located above a ceiling, provided that the distance between the edge of any ceiling opening that is not protected in conformance with Sentence (3) and the nearest sprinkler is not more than 300 mm. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.5.13.(5) | Combustible Sprinkler Piping | Where combustible sprinkler piping has been tested in conformance with ULC ULC/ORD-C199P-2002 Combustible Piping for Sprinkler Systems and has been shown to meet the requirements therein without additional protection, conformance to Sentences 3.2.5.13.(3) and 3.2.5.13.(4) is not required. | obc2019_divb | Div B | 3.2.5.14.(5) | 3.2.5.14. Combustible Sprinkler Piping | The protection required by Sentences (3) and (4) is permitted to be waived where combustible sprinkler piping has been tested in conformance with ULC/ORD-C199P, "Combustible Piping for Sprinkler Systems", and has been shown to meet the requirements in that document without additional protection. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.5.14.(1) | Sprinklered Service Space | An automatic sprinkler system shall be installed in a service space referred to in Sentence 3.2.1.1.(8) if flooring for access within the service space is other than catwalks. | obc2019_divb | Div B | 3.2.5.15.(1) | 3.2.5.15. Sprinklered Service Space | An automatic sprinkler system shall be installed in a service space referred to in Sentence 3.2.1.1.(9) if flooring for access within the service space is other than catwalks. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.5.14.(2) | Sprinklered Service Space | The sprinkler system required by Sentence 3.2.5.14.(1) shall be equipped with waterflow detecting devices, with each device serving not more than one storey. | obc2019_divb | Div B | 3.2.5.15.(2) | 3.2.5.15. Sprinklered Service Space | The sprinkler system required by Sentence (1) shall be equipped with waterflow detecting devices, with each device serving not more than 1 storey. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.5.14.(3) | Sprinklered Service Space | The waterflow detecting devices required by Sentence 3.2.5.14.(2) shall be connected to the fire alarm system, to initiate an alert signal in a 2-stage system or an alarm signal in a single stage system, and indicate separately on the fire alarm system annunciator the actuation of each device. | obc2019_divb | Div B | 3.2.5.15.(3) | 3.2.5.15. Sprinklered Service Space | The waterflow detecting devices required by Sentence (2) shall be connected to the fire alarm system to, initiate an alert signal in a two stage system or an alarm signal in a single stage system, and indicate separately on the fire alarm system annunciator the actuation of each device. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.5.15.(1) | Fire Department Connections | The fire department connection for a standpipe system shall be located so that the distance from the fire department connection to a hydrant is not more than 45 m and is unobstructed. | obc2019_divb | Div B | 3.2.5.16.(1) | 3.2.5.16. Fire Department Connections | The fire department connection for a standpipe system shall be located so that the distance from the fire department connection to a hydrant is not more than 45 m and is unobstructed. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.5.15.(2) | Fire Department Connections | The fire department connection for an automatic sprinkler system shall be located so that the distance from the fire department connection to a hydrant is not more than 45 m and is unobstructed. | obc2019_divb | Div B | 3.2.5.16.(2) | 3.2.5.16. Fire Department Connections | The fire department connection for an automatic sprinkler system shall be located so that the distance from the fire department connection to a hydrant is not more than 45 m and is unobstructed. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.5.16.(1) | Portable Fire Extinguishers | Portable extinguishers shall be provided and installed in accordance with (a) provincial or territorial regulations or municipal bylaws, or (b) the NFC, in the absence of the regulations or by laws referred to in Clause (a). | obc2019_divb | Div B | 3.2.5.17.(1) | 3.2.5.16. Portable Fire Extinguishers | Portable fire extinguishers shall be installed in all buildings, except within dwelling units, in conformance with the provisions of Part 6 of Division B of the Fire Code made under the Fire Protection and Prevention Act, 1997. |  | Common Sentence | Yes | Fire Suppression
2015 | ON | NBC | Div B | 3.2.5.16.(2) | Portable Fire Extinguishers | In a Group B, Division 1 major occupancy, portable fire extinguishers are permitted to be located in secure areas, or in lockable cabinets provided identical keys for all cabinets are located at all supervisory or security stations, or electrical remote release devices are provided and are connected to an emergency power supply. | obc2019_divb | Div B | 3.2.5.17.(2) | 3.2.5.17. Portable Fire Extinguishers | In a Group B, Division 1 major occupancy, portable fire extinguishers are permitted to be located in secure areas, or in lockable cabinets provided, identical keys for all cabinets are located at all supervisory or security stations, or electrical remote release devices are provided and are connected to an emergency power supply. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.5.17.(1) | Protection from Freezing | Equipment forming part of a fire protection system shall be protected from freezing if it could be adversely affected by freezing temperatures, and it is located in an unheated area. | obc2019_divb | Div B | 3.2.5.18.(1) | 3.2.5.18. Protection from Freezing | Equipment forming part of a fire protection system shall be protected from freezing if, it could be adversely affected by freezing temperatures, and it is located in an unheated area. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.5.18.(1) | Fire Pumps | If a fire pump is installed, it shall be installed in accordance with the requirements of NFPA 20-2016 Installation of Stationary Pumps for Fire Protection (See Note A-3.2.5.18.(1).) | obc2019_divb | Div B | 3.2.5.19.(1) | 3.2.5.19. Fire Pumps | A fire pump having a rated net head pressure greater than 280 kPa shall be installed in accordance with the requirements of NFPA 20, "Installation of Stationary Pumps for Fire Protection". (See Appendix A.) |  | Common Sentence | Yes | Fire Suppression
2015 | ON | NBC | Div B | 3.2.5.2.(1) | Access to Basements | Direct access from at least one street shall be provided from the outdoors in a building that is not sprinklered to each basement having a horizontal dimension more than 25 m. | obc2019_divb | Div B | 3.2.5.2.(1) | 3.2.5.2. Access to Basements | Direct access from at least one street shall be provided from the outdoors to each basement, that is not sprinklered, and that has horizontal dimension more than 25 m. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.5.2.(2) | Access to Basements | The access required by Sentence 3.2.5.2.(1) is permitted to be provided by doors, windows or other means that provide an opening not less than 1?100 mm high and 550 mm wide, with a sill no higher than 900 mm above the inside floor, or an interior stairway immediately accessible from the outdoors. | obc2019_divb | Div B | 3.2.5.2.(2) | 3.2.5.2. Access to Basements | The access required by Sentence (1) is permitted to be provided by, doors, windows or other means that provide an opening not less than 1 100 mm high and 550 mm wide, with a sill no higher than 900 mm above the inside floor, or an interior stairway immediately accessible from the outdoors |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.5.3.(1) | Roof Access | On a building more than 3 storeys in building height where the slope of the roof is less than 1 in 4, all main roof areas shall be provided with direct access from the floor areas immediately below, either by a stairway, or a hatch not less than 550 mm by 900 mm with a fixed ladder. | obc2019_divb | Div B | 3.2.5.3.(1) | 3.2.5.3. Roof Access | On a building more than 3 storeys in building height where the slope of the roof is less than 1 in 4, all main roof areas shall be provided with direct access from the floor areas immediately below, either by, a stairway, or a hatch not less than 550 mm by 900 mm with a fixed ladder. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.5.4.(1) | Access Routes | A building which is more than 3 storeys in building height or more than 600 m2 in building area shall be provided with access routes for fire department vehicles (a) to the building face having a principal entrance, and (b) to each building face having access openings for firefighting as required by Articles 3.2.5.1. and 3.2.5.2. | obc2019_divb | Div B | 3.2.5.4.(1) | 3.2.5.4. Access Routes | A building that is more than 3 storeys in building height or more than 600 m2 in building area shall be provided with access routes for fire department vehicles, (a) to the building face having a principal entrance, and (b) to each building face having access openings for firefighting as required by Articles 3.2.5.1. and 3.2.5.2. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.5.5.(1) | Location of Access Routes | Access routes required by Article 3.2.5.4. shall be located so that the principal entrance and every access opening required by Articles 3.2.5.1.and 3.2.5.2. are located not less than 3 m and not more than 15 m from the closest portion of the access route required for fire department use, measured horizontally from the face of the building. | obc2019_divb | Div B | 3.2.5.5.(1) | 3.2.5.5. Location of Access Routes | Access routes required by Article 3.2.5.4. shall be located so that the principal entrance and every access opening required by Articles 3.2.5.1. and 3.2.5.2. are located not less than 3 m and not more than 15 m from the closest portion of the access route required for fire department use, measured horizontally from the face of the building. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.5.5.(2) | Location of Access Routes | Access routes shall be provided to a building so that for a building provided with a fire department connection, a fire department pumper vehicle can be located adjacent to the hydrants referred to in Article 3.2.5.15., for a building not provided with a fire department connection, a fire department pumper vehicle can be located so that the length of the access route from a hydrant to the vehicle plus the unobstructed path of travel for the firefighter from the vehicle to the building is not more than 90 m, and the unobstructed path of travel for the firefighter from the vehicle to the building is not more than 45 m. | obc2019_divb | Div B | 3.2.5.5.(2) | 3.2.5.5. Location of Access Routes | Access routes shall be provided to a building so that, for a building provided with a fire department connection, a fire department pumper vehicle can be located adjacent to the hydrants referred to in Article 3.2.5.16., for a building not provided with a fire department connection, a fire department pumper vehicle can be located so that the length of the access route from a hydrant to the vehicle plus the unobstructed path of travel for the firefighter from the vehicle to the building is not more than 90 m, and the unobstructed path of travel for the firefighter from the vehicle to the building is not more than 45 m. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.5.5.(3) | Location of Access Routes | The unobstructed path of travel for the firefighter required by Sentence 3.2.5.5.(2) from the vehicle to the building shall be measured from the vehicle to the fire department connection provided for the building, except that if no fire department connection is provided, the path of travel shall be measured to the principal entrance of the building. | obc2019_divb | Div B | 3.2.5.5.(3) | 3.2.5.5. Location of Access Routes | The unobstructed path of travel for the firefighter required by Sentence (2) from the vehicle to the building shall be measured from the vehicle to the fire department connection provided for the building, except that if no fire department connection is provided, the path of travel shall be measured to the principal entrance of the building. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.5.5.(4) | Location of Access Routes | If a portion of a building is completely cut off from the remainder of the building so that there is no access to the remainder of the building, the access routes required by Sentence 3.2.5.5.(2) shall be located so that the unobstructed path of travel from the vehicle to one entrance of each portion of the building is not more than 45 m. | obc2019_divb | Div B | 3.2.5.5.(4) | 3.2.5.5. Location of Access Routes | If a portion of a building is completely cut off from the remainder of the building so that there is no access to the remainder of the building, the access routes required by Sentence (2) shall be located so that the unobstructed path of travel from the vehicle to one entrance of each portion of the building is not more than 45 m. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.5.6.(1) | Access Route Design | A portion of a roadway or yard provided as a required access route for fire department use shall have a clear width not less than 6 m, unless it can be shown that lesser widths are satisfactory, have a centre-line radius not less than 12 m, have an overhead clearance not less than 5 m, have a change of gradient not more than 1 in 12.5 over a minimum distance of 15 m, be designed to support the expected loads imposed by firefighting equipment and be surfaced with concrete, asphalt or other material designed to permit accessibility under all climatic conditions, have turnaround facilities for any dead-end portion of the access route more than 90 m long, and be connected with a public thoroughfare. | obc2019_divb | Div B | 3.2.5.6.(1) | 3.2.5.6. Access Route Design | A portion of a roadway or yard provided as a required access route for fire department use shall, have a clear width not less than 6 m, unless it can be shown that lesser widths are satisfactory, have a centreline radius not less than 12 m, have an overhead clearance not less than 5 m, have a change of gradient not more than 1 in 12.5 over a minimum distance of 15 m, be designed to support the expected loads imposed by firefighting equipment and be surfaced with concrete, asphalt or other material designed to permit accessibility under all climatic conditions, have turnaround facilities for any dead-end portion of the access route more than 90 m long, and be connected with a public thoroughfare. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.5.6.(2) | Access Route Design | For buildings conforming to Article 3.2.2.50. or 3.2.2.58., no portion of the access route described in Sentence 3.2.2.10.(3) shall be more than 20 m below the uppermost floor level. | obc2019_divb | Div B | 3.2.5.6.(2) | 3.2.5.6. Access Route Design | A building within the scope of Article 3.2.2.43A. or 3.2.2.50A. shall have no portion of the required access route more than 20 m below the floor level of the uppermost storey or mezzanine that is not a rooftop enclosure, provided for elevator machinery, a stairway or a service room used for no purpose other than for service to the building. |  | Common Sentence | Yes | Mid-rise Wood
2015 | ON | NBC | Div B | 3.2.5.7.(1) | 3.2.5.7. Water Supply (See Appendix A.) | Every building shall be provided with an adequate water supply for firefighting. (See Note A-3.2.5.7.(1).) | obc2019_divb | Div B | 3.2.5.7.(1) | 3.2.5.7. Water Supply (See Appendix A.) | An adequate water supply for firefighting shall be provided for every building. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.5.8.(1) | Standpipe Systems | Except as permitted by Sentence 3.2.5.9.(4), a standpipe system shall be installed in a building that is more than 3 storeys in building height, more than 14 m high measured between grade and the ceiling of the top storey, or not more than 14 m high measured between grade and the ceiling of the top storey but has a building area exceeding the area shown in Table 3.2.5.8. for the applicable building height unless the building is sprinklered throughout. | obc2019_divb | Div B | 3.2.9.1.(1) | 3.2.9.1. Where Required | Except as provided in Sentences (4) to (7), a standpipe system shall be installed in every building that, is more than 3 storeys in building height, is more than 14 m high measured between grade and the ceiling of the top storey, or is not more than 14 m high measured between grade and the ceiling of the top storey but has a building area exceeding the area shown in Table 3.2.9.1. for the applicable building height if the building is not sprinklered. |  | Common Sentence | Yes | Fire Suppression
2015 | ON | NBC | Div B | 3.2.5.9.(1) | Standpipe System Design | Except as provided in Sentences 3.2.5.9.(2) to 3.2.5.9.(6), Articles 3.2.5.10. and 3.2.5.11., and Sentence 3.2.4.9.(2), the design, construction, installation and testing of a standpipe system shall conform to NFPA 14-2013 Installation of Standpipe and Hose Systems | obc2019_divb | Div B | 3.2.9.2.(1) | 3.2.9.2. Standpipe System Design | Except as otherwise provided in this Subsection, if a standpipe system is required, the design, construction, installation and testing of the system shall be in conformance with NFPA 14, "Installation of Standpipe and Hose Systems". |  | Common Sentence | Yes | Fire Suppression
2015 | ON | NBC | Div B | 3.2.5.9.(2) | Standpipe System Design | A dry standpipe that is not connected to a water supply shall not be considered as fulfilling the requirements of this Article. | obc2019_divb | Div B | 3.2.9.2.(2) | 3.2.9.2. Standpipe System Design | A dry standpipe that is not connected to a water supply shall not be considered as fulfilling the requirements of this Article. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.5.9.(3) | Standpipe System Design | If more than one standpipe is provided, the total water supply need not be more than 30 L/s. | obc2019_divb | Div B | 3.2.9.2.(3) | 3.2.9.2. Standpipe System Design | If more than one standpipe is provided, the total water supply need not be more than 30 L/s. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.5.9.(4) | Standpipe System Design | A standpipe need not be installed in a storage garage conforming to Article 3.2.2.90., provided the building is not more than 15 m high. | obc2019_divb | Div B | 3.2.9.1.(6) | 3.2.9.1. Where Required | A standpipe system is not required to be installed in a storage garage conforming to Article 3.2.2.83. provided the building is not more than 15 m high. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.5.9.(5) | Standpipe System Design | The residual water pressure at the design flow rate at the topmost hose connection of a standpipe system that is required to be installed in a building is permitted to be less than 690 kPa provided (a) the building is sprinklered throughout,(b) the water supply at the base of the sprinkler riser is capable of meeting, without a fire pump, the design flow rate and pressure demand of the sprinkler system, including the inside and outside hose allowance, and (c) fire protection equipment is available to deliver, by means of the fire department connection, the full demand flow rate at a residual water pressure of 690 kPa at the topmost hose connection of the standpipe system (see Note A-3.2.5.9.(5)(c)). | obc2019_divb | Div B | 3.2.9.2.(4) | 3.2.9.2. Standpipe System Design | The residual water pressure at the design flow rate at the hydraulically most remote hose connection of a standpipe system that is required to be installed in a building is permitted to be less than 450 kPa provided that, (a) the building is sprinklered, (b) the water supply at the base of the sprinkler riser is capable of meeting the design flow rate and pressure demand of the sprinkler system, including the inside and outside hose allowance, and (c) fire protection equipment is available to deliver, by means of the fire department connection, the full demand flow rate at a residual water pressure of 450 kPa at the hydraulically most remote hose connection of the standpipe system. (See Appendix A.) |  | Common Sentence | Yes | Fire Suppression
2015 | ON | NBC | Div B | 3.2.5.9.(6) | Standpipe System Design | A fire department connection shall be provided for every standpipe system. | obc2019_divb | Div B | 3.2.9.2.(5) | 3.2.9.2. Standpipe System Design | A fire department connection shall be provided for every standpipe system. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.6.1.(1) | Application | This Subsection applies to a building of Group A, D, E or F major occupancy classification that is more than 36 m high, measured between grade and the floor level of the top storey, or 18 m high, measured between grade and the floor level of the top storey, and in which the cumulative or total occupant load on or above any storey above grade, other than the first storey, divided by 1.8 times the width in metres of all exit stairs at that storey, exceeds 300, containing a Group B major occupancy in which the floor level of the highest storey of that major occupancy is more than 18 m above grade, containing a floor area or part of a floor area located above the third storey designed or intended as a Group B, Division 2 or 3 occupancy, or containing a Group C major occupancy whose floor level is more than 18 m above grade. | obc2019_divb | Div B | 3.2.6.1.(1) | 3.2.6.1. Application | This Subsection applies to a building, of Group A, D, E or F major occupancy classification that is more than, 36 m high, measured between grade and the floor level of the top storey, or 18 m high, measured between grade and the floor level of the top storey, and in which the cumulative or total occupant load on or above any storey above grade, other than the first storey, divided by 1.8 times the width in metres of all exit stairs at that storey, exceeds 300, containing a Group B major occupancy in which the floor level of the highest storey of that major occupancy is more than 18 m above grade, containing a floor area or part of a floor area located above the third storey designed or intended as a Group B, Division 2 or 3 occupancy, containing a Group C major occupancy in which the floor level of the highest storey of that major occupancy is more than 18 m above grade, or containing a retirement home, where the floor level of the highest storey of the retirement home is more than 18 m above grade. |  | Common Sentence | Yes | Retirement Homes
2015 | ON | NBC | Div B | 3.2.6.2.(1) | Limits to Smoke Movement | A building to which this Subsection applies shall be designed in accordance with Sentences 3.2.6.2.(2) to 3.2.6.2.(6) and Article 3.2.6.3. to limit the danger to occupants and firefighters from exposure to smoke in a building fire. | obc2019_divb | Div B | 3.2.6.2.(1) | 3.2.6.2. Limits to Smoke Movement | A sprinklered building shall be designed in accordance with Sentences (2) to (5.1) and MMAH Supplementary Standard SB-4, "Measures for Fire Safety in High Buildings", to limit the danger to occupants and firefighters from exposure to smoke in a building fire. |  | Common Sentence | Yes | High Buildings
2015 | ON | NBC | Div B | 3.2.6.2.(2) | Limits to Smoke Movement | A building referred to in Sentence 3.2.6.2.(1) shall be designed so that, during a period of 2 h after the start of a fire, each exit stair serving storeys below the lowest exit level will not contain more than 1% by volume of contaminated air from the fire floor, assuming an outdoor temperature equal to the January design temperature on a 2.5% basis determined in accordance with part 1. (See Note A-3.2.6.2.(2).) | obc2019_divb | Div B | 3.2.6.2.(2) | 3.2.6.2. Limits to Smoke Movement | A building referred to in Sentence (1), shall be designed so that, during a period of 2 h after the start of a fire, each exit stair serving storeys below the lowest exit level will not contain more than 1% by volume of contaminated air from the fire floor, assuming an outdoor temperature equal to the January design temperature on a 2.5% basis determined in conformance with MMAH Supplementary Standard SB-1, "Climatic and Seismic Data". |  | Common Sentence | Yes | High Buildings
2015 | ON | NBC | Div B | 3.2.6.2.(3) | Limits to Smoke Movement | Each stairway that serves storeys above the lowest exit level shall have a vent to the outdoors, at or near the bottom of the stair shaft, that has an openable area of 0.05 m2 for every door between the stair shaft and a floor area, but not less than 1.8 m2, opens directly to the outdoors or into a vestibule that has a similar opening to the outdoors, and has a door or closure that is openable manually, and can remain in the open position during a fire emergency. (See Note A-3.2.6.2.(3).) | obc2019_divb | Div B | 3.2.6.2.(3) | 3.2.6.2. Limits to Smoke Movement | Each stairway that serves storeys above the lowest exit level shall have a vent to the outdoors, at or near the bottom of the stair shaft, that, has an openable area of 0.05 m2 for every door between the stair shaft and a floor area, but not less than 1.8 m2, opens directly to the outdoors or into a vestibule that has a similar opening to the outdoors, and has a door or closure that, is openable manually, and can remain in the open position during a fire emergency. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.6.2.(4) | Limits to Smoke Movement | Measures shall be taken to limit movement of smoke from a fire in a floor area below the lowest exit storey into upper storeys. (See Note A-3.2.6.2.(4).) | obc2019_divb | Div B | 3.2.6.2.(4) | 3.2.6.2. Limits to Smoke Movement | Measures shall be taken to limit movement of smoke from a fire in a floor area below the lowest exit storey into upper storeys. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.6.2.(5) | Limits to Smoke Movement | Except for exhaust fans in kitchens, washrooms and bathrooms in dwelling units, and except for fans used for smoke venting as required by Article 3.2.6.6., air moving fans in a system that serves more than 2 storeys shall be designed and installed so that in the event of a fire these fans can be stopped by means of a manually operated switch at the central alarm and control facility. | obc2019_divb | Div B | 3.2.6.2.(5) | 3.2.6.2. Limits to Smoke Movement | Except for exhaust fans in kitchens, washrooms and bathrooms in dwelling units, and except for fans used for smoke venting as required by Article 3.2.6.6., air moving fans in a system that serves more than 2 storeys shall be designed and installed so that in the event of a fire these fans can be stopped by means of a manually operated switch at the central alarm and control facility. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.6.2.(6) | Limits to Smoke Movement | Except as provided in Article 3.2.4.12. or where there is a conflict with other smoke control measures in the building, air-handling systems used to provide make-up air to public corridors serving suites in a Group C major occupancy shall not shut down automatically upon activation of the fire alarm so as to maintain corridor pressurization. | obc2019_divb | Div B | 3.2.6.2.(5) | 3.2.6.2. Limits to Smoke Movement | (5.1) Except as provided in Article 3.2.4.13. or as otherwise provided in this Part, air handling systems used to provide make-up air to public corridors serving suites in a Group C major occupancy shall not shut down automatically upon actuation of the fire alarm so as to maintain corridor pressurization. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.6.3.(1) | Connected Buildings | If a building described in Article 3.2.6.1. is connected to any other building, measures shall be taken to limit movement of contaminated air from one building into another during a fire. (See Note A-3.2.6.3.(1).) | obc2019_divb | Div B | 3.2.6.3.(1) | 3.2.6.3. Connected Buildings | If a building described in Article 3.2.6.1. is connected to any other building, measures shall be taken to limit movement of contaminated air from one building into another during a fire. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.6.4.(1) | Emergency Operation of Elevators | Manual emergency recall shall be provided for all elevators serving storeys above the first storey. | obc2019_divb | Div B | 3.2.6.4.(1) | 3.2.6.4. Emergency Operation of Elevators | Manual emergency recall shall be provided for all elevators serving storeys above the first storey. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.6.4.(2) | Emergency Operation of Elevators | Key-operated switches for emergency recall required by Sentence 3.2.6.4.(1) shall be provided in a conspicuous location at (a) each elevator lobby on the recall level, and (b) the central alarm and control facility required by Article 3.2.6.7. | obc2019_divb | Div B | 3.2.6.4.(2) | 3.2.6.4. Emergency Operation of Elevators | Key-operated switches for emergency recall described by Sentence (1) shall be provided in a conspicuous location at, (a) each elevator lobby on the recall level, and (b) the central alarm and control facility required in Article 3.2.6.7. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.6.4.(3) | Emergency Operation of Elevators | In-car emergency service switches shall be provided in all elevator cars. | obc2019_divb | Div B | 3.2.6.4.(3) | 3.2.6.4. Emergency Operation of Elevators | In-car emergency service switches shall be provided in all elevator cars. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.6.4.(4) | Emergency Operation of Elevators | Keys to operate the switches required by Sentences 3.2.6.4.(2) and 3.2.6.4.(3) shall be provided in a suitably identified box conspicuously located on the outside of an elevator hoistway near the central alarm and control facility required by Article 3.2.6.7., and kept at the central alarm and control facility. | obc2019_divb | Div B | 3.2.6.4.(4) | 3.2.6.4. Emergency Operation of Elevators | Keys to operate the switches required by Sentences (2) and (3) shall be, provided in a suitably identified box conspicuously located on the outside of an elevator hoistway near the central alarm and control facility required by Article 3.2.6.7., and kept at the central alarm and control facility. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.6.5.(1) | Elevator for Use by Firefighters | At least one elevator shall be provided for use by firefighters in conformance with Sentences 3.2.6.5.(2) to 3.2.6.5.(6). | obc2019_divb | Div B | 3.2.6.5.(1) | 3.2.6.5. Elevator for Use by Firefighters | At least one elevator shall be provided for use by firefighters in conformance with Sentences (2) to (6). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.6.5.(2) | Elevator for Use by Firefighters | The elevator referred to in Sentence 3.2.6.5.(1) shall have a useable platform area not less than 2.2 m2 and shall be capable of carrying a load of 900 kg to the top floor that it serves from a landing on the storey containing the entrance for firefighter access referred to in Articles 3.2.5.4. and 3.2.5.5. within 1 min. | obc2019_divb | Div B | 3.2.6.5.(2) | 3.2.6.5. Elevator for Use by Firefighters | The elevator referred to in Sentence (1) shall have a useable platform area not less than 2.2 m2 and shall be capable of carrying a load of 900 kg to the top floor that it serves from a landing on the storey containing the entrance for firefighter access referred to in Articles 3.2.5.4. and 3.2.5.5. within 1 min. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.6.5.(3) | Elevator for Use by Firefighters | Each elevator for use by firefighters shall (a) be provided with a closure at each shaft opening so that the interlock mechanism remains mechanically engaged and electrical continuity is maintained in the interlock circuits and associated wiring for a period of not less than 1 h when the assembly is subjected to the standard fire exposure described in ULC CAN/ULC-S104-15 Fire Tests of Door Assemblies (b) be protected with a vestibule containing no occupancy and separated from the remainder of the floor area by a fire separation having a fire-resistance rating not less than 45 min, or (c) be protected with a corridor containing no occupancy and separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h. | obc2019_divb | Div B | 3.2.6.5.(3) | 3.2.6.5. Elevator for Use by Firefighters | Except where Measure K of MMAH Supplementary Standard SB-4, "Measures for Fire Safety in High Buildings", is used, each elevator for use by firefighters shall, (a) be provided with a closure at each shaft opening so that the interlock mechanism remains mechanically engaged and electrical continuity is maintained in the interlock circuits and associated wiring for a period of not less than 1 h when the assembly is subjected to the standard fire exposure described in CAN/ULC-S104, "Fire Tests of Door Assemblies", (b) be protected with a vestibule containing no occupancy and separated from the remainder of the floor area by a fire separation having a fire-resistance rating not less than 45 min, or (c) be protected with a corridor containing no occupancy and separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h. |  | Common Sentence | Yes | High Buildings
2015 | ON | NBC | Div B | 3.2.6.5.(4) | Elevator for Use by Firefighters | Except as permitted by Sentence 3.2.6.5.(5), an elevator referred to in Sentence 3.2.6.5.(1) shall be capable of providing transportation from the storey containing the entrance for firefighter access referred to in Articles 3.2.5.4. and 3.2.5.5. to every floor that is above grade in the building and that is normally served by the elevator system. | obc2019_divb | Div B | 3.2.6.5.(4) | 3.2.6.5. Elevator for Use by Firefighters | Except as permitted in Sentence (5), an elevator referred to in Sentence (1) shall be capable of providing transportation from the storey containing the entrance for firefighter access referred to in Articles 3.2.5.4. and 3.2.5.5. to every floor that is above grade in the building and that is normally served by the elevator system. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.6.5.(5) | Elevator for Use by Firefighters | If it is necessary to change elevators to reach any floor referred to in Sentence 3.2.6.5.(4), the system shall be designed so that not more than one change of elevator is required when travelling to any floor in the building from the storey containing the entrance for firefighter access referred to in Articles 3.2.5.4. and 3.2.5.5. | obc2019_divb | Div B | 3.2.6.5.(5) | 3.2.6.5. Elevator for Use by Firefighters | If it is necessary to change elevators to reach any floor referred to in Sentence (4), the system shall be designed so that not more than one change of elevator is required when travelling to any floor in the building from the storey containing the entrance for firefighter access referred to in Articles 3.2.5.4. and 3.2.5.5. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.6.5.(6) | Elevator for Use by Firefighters | Electrical conductors for the operation of the elevator referred to in Sentence 3.2.6.5.(1) shall be installed in service spaces conforming to part 3. that do not contain other combustible material, or protected against exposure to fire from the service entrance of the emergency power supply, or the normal service entrance of the normal power supply, to the equipment served, to ensure operation for a period of 1 h when subjected to the standard fire exposure described in ULC CAN/ULC-S101-14 Fire Endurance Tests of Building Construction and Materials (see Note A-3.2.6.5.(6)(b)). | obc2019_divb | Div B | 3.2.6.5.(6) | 3.2.6.5. Elevator for Use by Firefighters | Electrical conductors for the operation of the elevator referred to in Sentence (1) shall be, installed in service spaces conforming to Section 3.6. that do not contain other combustible material, or protected against exposure to fire from the service entrance of the emergency power supply, or the normal service entrance of the normal power supply, to the equipment served, to ensure operation for a period of 1 h when subjected to the standard fire exposure described in CAN/ULC-S101, "Fire Endurance Tests of Building Construction and Materials". |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.6.6.(1) | Venting to Aid Firefighting | Means of venting each floor area to the outdoors shall be provided by windows, wall panels, smoke shafts, or the building exhaust system. (See Note A-3.2.6.6.(1).) | obc2019_divb | Div B | 3.2.6.6.(1) | 3.2.6.6. Venting to Aid Firefighting | Means of venting each floor area to the outdoors shall be provided by windows, wall panels, smoke shafts or, except as provided by Sentence (5), the building exhaust system. |  | Common Sentence | Yes | High Buildings
2015 | ON | NBC | Div B | 3.2.6.6.(2) | Venting to Aid Firefighting | Fixed glass windows shall not be used for the venting required by Sentence 3.2.6.6.(1) if the breaking of the windows could endanger pedestrians below. | obc2019_divb | Div B | 3.2.6.6.(2) | 3.2.6.6. Venting to Aid Firefighting | Fixed glass windows shall not be used for the venting required by Sentence (1) if the breaking of the windows could endanger pedestrians below. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.6.6.(3) | Venting to Aid Firefighting | Openable windows used for the venting required by Sentence 3.2.6.6.(1) shall be permanently marked so that they are easily identifiable. | obc2019_divb | Div B | 3.2.6.6.(3) | 3.2.6.6. Venting to Aid Firefighting | Openable windows used for the venting required by Sentence (1) shall be permanently marked so that they are easily identifiable. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.6.6.(4) | Venting to Aid Firefighting | Elevator hoistways shall not be designed for the venting required by Sentence 3.2.6.6.(1). | obc2019_divb | Div B | 3.2.6.6.(4) | 3.2.6.6. Venting to Aid Firefighting | Elevator hoistways shall not be designed for the venting required by Sentence (1). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.6.7.(1) | Central Alarm and Control Facility | A central alarm and control facility shall be provided on the storey containing the entrance for firefighter access referred to in Articles 3.2.5.4. and 3.2.5.5. in a location that is readily accessible to firefighters entering the building, and takes into account the effect of background noise likely to occur under fire emergency conditions, so that the facility can properly perform its required function under these conditions. | obc2019_divb | Div B | 3.2.6.7.(1) | 3.2.6.7. Central Alarm and Control Facility | A central alarm and control facility shall be provided on the storey containing the entrance for firefighter access referred to in Articles 3.2.5.4. and 3.2.5.5. in a location that, is readily accessible to firefighters entering the building, and takes into account the effect of background noise likely to occur under fire emergency conditions, so that the facility can properly perform its required function under such conditions. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.6.7.(2) | Central Alarm and Control Facility | The central alarm and control facility required in Sentence (1) shall include, (a) means to control the voice communication system required by Article 3.2.6.8., so that messages can be sent to, (i) all loudspeakers simultaneously, (ii) individual floor areas, and (iii) exit stairwells, (b) means to indicate audibly and visually alert signals and alarm signals and a switch to, (i) silence the audible portion of these signals, and (ii) indicate visually that the audible portion has been silenced, (c) means to indicate visually that elevators are on emergency recall, (d) an annunciator conforming to Article 3.2.4.8., (e) means to transmit alert signals and alarm signals to the fire department in conformance with Article 3.2.4.7., (f) means to release hold-open devices on doors to vestibules, (g) means to manually actuate alarm signals in the building selectively to any zone or zones, (h) means to silence the alarm signals referred to in Clause (g) in conformance with Sentences 3.2.4.22.(2) and (3), (i) means, as appropriate to the measure for fire safety provided in the building, to, (i) actuate auxiliary equipment identified in Articles 3.2.6.2., 3.2.6.3. and 3.2.6.6., or (ii) communicate with a continually staffed auxiliary equipment control centre, (j) means to communicate with telephones in elevator cars, separate from connections to firefighters’ telephones, if elevator cars are required by ASME A17.1/CSA B44, “Safety Code for Elevators and Escalators,” to be equipped with a telephone , (k) means to indicate visually, individual sprinkler system waterflow signals, (l) means to indicate audibly and visually, sprinkler and standpipe system supervisory signals and trouble signals, (m) a switch to silence the audible portion of a supervisory signal or a trouble signal, and (n) visual indication that the audible portion of a supervisory signal or a trouble signal has been silenced. | obc2019_divb | Div B | 3.2.6.7.(2) | 3.2.6.7. Central Alarm and Control Facility | The central alarm and control facility required in Sentence (1) shall include, (a) means to control the voice communication system required by Article 3.2.6.8., so that messages can be sent to, (i) all loudspeakers simultaneously, (ii) individual floor areas, and (iii) exit stairwells, (b) means to indicate audibly and visually alert signals and alarm signals and a switch to, (i) silence the audible portion of these signals, and (ii) indicate visually that the audible portion has been silenced, (c) means to indicate visually that elevators are on emergency recall, (d) an annunciator conforming to Article 3.2.4.9., (e) means to transmit alert signals and alarm signals to the fire department in conformance with Article 3.2.4.8., (f) means to release hold-open devices on doors to vestibules, (g) means to manually actuate alarm signals in the building selectively to any zone or zones, (h) means to silence the alarm signals referred to in Clause (g) in conformance with Sentences 3.2.4.23.(2) and (3), (i means, as appropriate to the measure for fire safety provided in the building, to, (i) actuate auxiliary equipment identified in Articles 3.2.6.2., 3.2.6.3. and 3.2.6.6., or (ii) communicate with a continually staffed auxiliary equipment control centre, (j) means for two-way communications with every elevator car, (k) means to indicate visually, individual sprinkler system waterflow signals, (l) means to indicate audibly and visually, sprinkler and standpipe system supervisory signals and trouble signals, (m) a switch to silence the audible portion of a supervisory signal or a trouble signal, and (n) visual indication that the audible portion of a supervisory signal or a trouble signal has been silenced. |  | Common Sentence | Yes | High Buildings
2015 | ON | NBC | Div B | 3.2.6.8.(1) | Voice Communication System | A voice communication system conforming to Article 3.2.4.22. shall be provided in a building if the floor of the top storey is more than 36 m above grade, or a floor area or part of a floor area located above the third storey is designed or intended for use as a Group B, Division 2 or 3 occupancy. | obc2019_divb | Div B | 3.2.6.8.(1) | 3.2.6.8. Voice Communication System | A voice communication system conforming to Article 3.2.4.23. shall be provided in a building if, the floor of the top storey is more than 36 m above grade, a floor area or part of a floor area located above the third storey is designed or intended for use as a Group B, Division 2 or 3 occupancy, or a floor area or part of a floor area located more than 18 m above grade is designed or intended for use as a retirement home regulated under the Retirement Homes Act, 2010 that is a Group C occupancy. |  | Common Sentence | Yes | Retirement Homes
2015 | ON | NBC | Div B | 3.2.6.9.(1) | Testing | The systems for control of smoke movement and mechanical venting required by Articles 3.2.6.2. and 3.2.6.6. shall be tested to ensure satisfactory operation. (See Note A-3.2.6.9.(1).) | obc2019_divb | Div B | 3.2.6.9.(1) | 3.2.6.9. Testing | The systems for control of smoke movement and mechanical venting required by Articles 3.2.6.2. and 3.2.6.6. shall be tested to ensure satisfactory operation in accordance with the procedures described in MMAH Supplementary Standard SB-4, "Measures for Fire Safety in High Buildings". |  | Common Sentence | Yes | High Buildings
2015 | ON | NBC | Div B | 3.2.7.1.(1) | Minimum Lighting Requirements | An exit, a public corridor, or a corridor providing access to exit for the public or serving patientsâ€™ sleeping rooms or classrooms shall be equipped to provide illumination to an average level not less than 50 lx at floor or tread level and at angles and intersections at changes of level where there are stairs or ramps. | obc2019_divb | Div B | 3.2.7.1.(1) | 3.2.7.1. Minimum Lighting Requirements | An exit, a public corridor, a corridor providing access to exit for the public, a corridor serving patients or residents in a Group B, Division 2 or 3 occupancy, a corridor serving classrooms, an electrical equipment room, a transformer vault and a hoistway pit shall be equipped to provide illumination to an average level not less than 50 lx at floor or tread level and at all points such as angles and intersections at changes of level where there are stairs or ramps. |  | Common Sentence | Yes | Lighting
2015 | ON | NBC | Div B | 3.2.7.1.(2) | Minimum Lighting Requirements | The minimum value of the illumination required by Sentence 3.2.7.1.(1) shall be not less than 10 lx. | obc2019_divb | Div B | 3.2.7.1.(2) | 3.2.7.1. Minimum Lighting Requirements | The minimum value of the illumination required by Sentence (1) shall not be less than 10 1x. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.7.1.(3) | Minimum Lighting Requirements | Rooms and spaces used by the public shall be illuminated as described in Article 9.34.2.7. | obc2019_divb | Div B | 3.2.7.1.(3) | 3.2.7.1. Minimum Lighting Requirements | Rooms and spaces used by the public shall be illuminated as described in Article 9.34.2.7. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.7.1.(4) | Minimum Lighting Requirements | Lighting outlets in a building of residential occupancy shall be provided in conformance with part 9. | obc2019_divb | Div B | 3.2.7.1.(4) | 3.2.7.1. Minimum Lighting Requirements | Lighting outlets in a building of residential occupancy shall be provided in conformance with Subsection 9.34.2. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.7.10.(1) | Protection of Electrical Conductors | The protection of electrical and emergency conductors referred to in Clauses 3.2.7.10.(1) to 3.2.7.10.(1) shall conform to the requirements stated in Sentences 3.2.7.10.(2) to 3.2.7.10.(11) : (a) electrical conductors located within buildings identified in Article 3.2.6.1. serving (i) fire alarms, (ii) emergency lighting, or (iii) emergency equipment within the scope of Articles 3.2.6.2. to 3.2.6.8., (b) emergency conductors serving fire pumps required to be installed under Article 3.2.5.18., and (c) electrical conductors serving mechanical systems serving (i) areas of refuge identified in Sentence 3.3.3.6.(1), or (ii) contained use areas identified in Clauses 3.3.3.7.(4) and 3.3.3.7.(4). | obc2019_divb | Div B | 3.2.7.10.(1) | 3.2.7.10. Protection of Electrical Conductors | Electrical conductors shall conform to Sentences (2) to (9) and (11) if they, (a) are within buildings identified in Article 3.2.6.1. and serve, (i) fire alarm systems, or (ii) emergency equipment within the scope of Articles 3.2.6.2. to 3.2.6.8., (b) serve fire pumps required to be installed under Article 3.2.5.19., (c) serve mechanical systems related to, (i) compartments referred to in Clause 3.3.3.6.(1)(b), (ii) contained use areas referred to in Clauses 3.3.3.7.(4)(a) and (b), or (iii) provisions of Articles 3.2.8.4. to 3.2.8.6. and 3.2.8.9., or (d) serve emergency lighting described in Article 3.2.7.3 |  | Common Sentence | Yes | Emergency Power
2015 | ON | NBC | Div B | 3.2.7.10.(10) | Protection of Electrical Conductors | Distribution panels serving emergency lighting units located on other storeys shall be installed in a service room separated from the floor area by a fire separation having a fire-resistance rating of at least 1 h. | obc2019_divb | Div B | 3.2.7.10.(10) | 3.2.7.10. Protection of Electrical Conductors | Distribution panels serving emergency lighting units located on other storeys shall be installed in a service room separated from the floor area by a fire separation having a fire-resistance rating of at least 1 h. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.7.10.(11) | Protection of Electrical Conductors | Conductors leading from a distribution panel to emergency lighting units located on other storeys shall be protected in accordance with Sentence 3.2.7.10.(2) between the distribution panel and the floor area where the emergency lighting units are located. | obc2019_divb | Div B | 3.2.7.10.(11) | 3.2.7.10. Protection of Electrical Conductors | Conductors leading from a distribution panel referred to in Sentence (10) to emergency lighting units located on other storeys shall be protected in accordance with Sentence (2) between the distribution panel and the floor area where the emergency lighting units are located. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.7.10.(2) | Protection of Electrical Conductors | Except as otherwise required by Sentence 3.2.7.10.(3) and permitted by this Article, electrical conductors that are used in conjunction with systems identified in Sentence 3.2.7.10.(1) shall (a) conform to ULC CAN/ULC-S139-12 Fire Test for Evaluation of Integrity of Electrical Power, Data and Optical Fibre Cables including the hose stream application, to provide a circuit integrity rating of not less than 1 h (see Note A-3.2.7.10.(2)(a) and 3(a)), or (b) be located in a service space that is separated from the remainder of the building by a fire separation that has a fire-resistance rating not less than 1 h. | obc2019_divb | Div B | 3.2.7.10.(2) | 3.2.7.10. Protection of Electrical Conductors | Except as required by Sentence (3) and except as permitted in this Article, electrical conductors referred to in Sentence (1) shall, (a) conform to CAN/ULC-S139, "Fire Test for Evaluation of Integrity of Electrical Power, Data and Optical Fibre Cables", including the hose stream application, to provide a circuit integrity rating of not less than 1 h, or (b) be located in a service space that is separated from the remainder of the building by a fire separation that has a fire-resistance rating of not less than 1 h. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.7.10.(3) | Protection of Electrical Conductors | Electrical conductors identified in Sentence 3.2.7.10.(1) shall conform to ULC CAN/ULC-S139-12 Fire Test for Evaluation of Integrity of Electrical Power, Data and Optical Fibre Cables including the hose stream application, to provide a circuit integrity rating of not less than 2 h (see Note A-3.2.7.10.(2)(a)), or be located in a service space that is separated from the remainder of the building by a fire separation that has a fire-resistance rating not less than 2 h. | obc2019_divb | Div B | 3.2.7.10.(3) | 3.2.7.10. Protection of Electrical Conductors | Electrical conductors that are used in conjunction with systems referred to in Clause (1)(c) shall, conform to CAN/ULC-S139, "Fire Test for Evaluation of Integrity of Electrical Power, Data and Optical Fibre Cables", including the hose stream application, to provide a circuit integrity rating of not less than 2 h, or (See A-3.2.7.10.(2)(a) in Appendix A) be located in a service space that is separated from the remainder of the building by a fire separation that has a fire-resistance rating of not less than 2 h. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.7.10.(4) | Protection of Electrical Conductors | The service spaces referred to in Clauses 3.2.7.10.(2)(b) and 3.2.7.10.(3)(b) shall not contain any combustible materials other than the conductors being protected. | obc2019_divb | Div B | 3.2.7.10.(4) | 3.2.7.10. Protection of Electrical Conductors | The service spaces referred to in Clause (2)(b) or (3)(b) shall not contain any combustible materials other than the electrical conductors being protected. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.7.10.(5) | Protection of Electrical Conductors | Except as stated in Sentences 3.2.7.10.(7) and 3.2.7.10.(9), the electrical conductors referred to in Sentence 3.2.7.10.(1) are those that extend from the source of emergency power to the equipment served, or the distribution equipment supplying power to the equipment served, if both are in the same room (see Note A-3.2.7.10.(5)(b)). | obc2019_divb | Div B | 3.2.7.10.(5) | 3.2.7.10. Protection of Electrical Conductors | Except as permitted by Sentences (7) and (9), the electrical conductors referred to in Sentence (1) are those that extend from the source of emergency power to, the equipment served, or the distribution equipment supplying power to the equipment served, if both are in the same room. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.7.10.(6) | Protection of Electrical Conductors | If a fire alarm transponder or annunciator in one fire compartment is connected to a central processing unit or another transponder or annunciator located in a different fire compartment, the electrical conductors connecting them shall be protected in accordance with Sentence 3.2.7.10.(2). | obc2019_divb | Div B | 3.2.7.10.(6) | 3.2.7.10. Protection of Electrical Conductors | If a fire alarm transponder or annunciator located in one fire compartment is connected to a central processing unit or another transponder or annunciator located in a different fire compartment, the electrical conductors connecting them shall be protected in accordance with Sentence (2). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.7.10.(7) | Protection of Electrical Conductors | Fire alarm system branch circuits within a storey that connect transponders and individual devices need not conform to Sentence 3.2.7.10.(2). (See Note A-3.2.7.10.(7).) | obc2019_divb | Div B | 3.2.7.10.(7) | 3.2.7.10. Protection of Electrical Conductors | Fire alarm system branch circuits within a storey that connect transponders and individual devices need not conform to Sentence (2). (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.7.10.(8) | Protection of Electrical Conductors | Except as permitted in Sentence 3.2.7.10.(9), if a distribution panel supplies power to emergency lighting, the power supply conductors leading up to the distribution panel shall be protected in accordance with Sentence 3.2.7.10.(2). | obc2019_divb | Div B | 3.2.7.10.(8) | 3.2.7.10. Protection of Electrical Conductors | Except as permitted by Sentence (9), if a distribution panel supplies power to emergency lighting, the power supply conductors leading up to the distribution panel shall be protected in accordance with Sentence (2). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.7.10.(9) | Protection of Electrical Conductors | Conductors leading from a distribution panel referred to in Sentence 3.2.7.10.(8) to emergency lighting units in the same storey need not conform to Sentence 3.2.7.10.(2). | obc2019_divb | Div B | 3.2.7.10.(9) | 3.2.7.10. Protection of Electrical Conductors | Conductors leading from a distribution panel referred to in Sentence (8) to emergency lighting units in the same storey need not conform to Sentence (2). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.7.2.(1) | Recessed Lighting Fixtures | A recessed lighting fixture shall not be located in an insulated ceiling unless the fixture is designed for this type of installation. | obc2019_divb | Div B | 3.2.7.2.(1) | 3.2.7.2. Recessed Lighting Fixtures | A recessed lighting fixture shall not be located in an insulated ceiling unless the fixture is designed for this type of installation. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.7.3.(1) | Emergency Lighting | Emergency lighting shall be provided to an average level of illumination not less than 10 lx at floor or tread level in (a) exits, (b) principal routes providing access to exit in open floor areas and in service rooms, (c) corridors used by the public, (d) corridors serving sleeping rooms in a treatment occupancy, (e) corridors serving sleeping rooms in a care occupancy, except corridors serving sleeping rooms within individual suites of care occupancy, (f) corridors serving classrooms, (g) underground walkways, (h) public corridors, (i) floor areas or parts thereof where the public may congregate (i) in Group A, Division 1 occupancies, or (ii) in Group A, Division 2 and 3 occupancies having an occupant load of 60 or more, (j) floor areas or parts thereof of daycare centres where persons are cared for, (k) food preparation areas in commercial kitchens, and (i) public washrooms that are equipped to serve more than one person at a time. | obc2019_divb | Div B | 3.2.7.3.(1) | 3.2.7.3. Emergency Lighting | Emergency lighting shall be provided to an average level of illumination not less than 10 lx at floor or tread level in, (a) exits, (b) principal routes providing access to exit in an open floor area and in service rooms, (c) corridors used by the public, (d) corridors serving patients’ or residents’ sleeping rooms in a Group B, Division 2 or 3 occupancy, (e) corridors serving classrooms, (f) underground walkways, (g) public corridors, (h) floor areas or parts of them where the public may congregate in, (i) Group A, Division 1 occupancies, or (ii) Group A, Divisions 2 and 3 occupancies having an occupant load of 60 or more, (i) floor areas or parts of them in day care centres where persons are cared for, (j) food preparation areas in commercial kitchens, (k) principal routes providing access to exit in a floor area that is not subdivided into rooms or suites of rooms served by corridors in a business and personal services occupancy, a mercantile occupancy or an industrial occupancy, (l) internal corridors or aisles serving as principal routes to exits in a business and personal services occupancy, a mercantile occupancy or an industrial occupancy that is subdivided into rooms or suites of rooms, and is not served by a public corridor, and (m) washrooms with fixtures for public use. |  | Common Sentence | Yes | Lighting
2015 | ON | NBC | Div B | 3.2.7.3.(1) | Emergency Lighting Exit Width | The minimum widths of exits shall conform to Tables 3.4.3.2.-A and 3.4.3.2.-B. | obc2019_divb | Div B | 3.4.3.2.(7) | 3.4.3.2. Exit Width | The width of an exit shall be not less than, (a) 1 100 mm for corridors and passageways, (b) 1 100 mm for ramps not serving patients’ or residents’ sleeping rooms, (c) 1 100 mm for stairs, not serving patients’ or residents’ sleeping rooms, that serve more than two storeys above the lowest exit level or more than one storey below the lowest exit level, (d) 900 mm for stairs, not serving patients’ or residents’ sleeping rooms, that serve not more than two storeys above the lowest exit level or not more than one storey below the lowest exit level, (e) 1 650 mm for stairs and ramps serving patients’ or residents’ sleeping rooms, (f) 1 050 mm for doorways serving patients’ or residents’ sleeping rooms, and (g) 790 mm for doorways not serving patients’ or residents’ sleeping rooms. |  | Common Sentence | Yes | Exits
2015 | ON | NBC | Div B | 3.2.7.3.(2) | Emergency Lighting | Emergency lighting to provide an average level of illumination of not less than 10 lx at floor or catwalk level shall be included in a service space referred to in Sentence 3.2.1.1.(8). | obc2019_divb | Div B | 3.2.7.3.(2) | 3.2.7.3. Emergency Lighting | Emergency lighting to provide an average level of illumination of not less than 10 lx at floor or catwalk level shall be included, (a) in a service space referred to in Sentence 3.2.1.1.(9), and (b) on a shelf and rack storage system, in locations described in Sentence 3.16.1.5.(2). |  | Common Sentence | Yes | Falling, Tripping, Slipping Protection
2015 | ON | NBC | Div B | 3.2.7.3.(3) | Emergency Lighting | The minimum value of the illumination required by Sentences (1) and (2) shall be not less than 1 lx. | obc2019_divb | Div B | 3.2.7.3.(3) | 3.2.7.3. Emergency Lighting | The minimum value of the illumination required by Sentences (1) and (2) shall not be less than 1 lx. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.7.3.(4) | Emergency Lighting | In addition to the requirements of Sentences 3.2.7.3.(1) to 3.2.7.3.(3), the installation of battery-operated emergency lighting in buildings or part thereof where treatment is provided shall conform to the appropriate requirements of CSA Z32-09 Electrical Safety and Essential Electrical Systems in Health Care Facilities | obc2019_divb | Div B | 3.2.7.3.(4) | 3.2.7.3. Emergency Lighting | In addition to the requirements of Sentences (1) to (3), the installation of battery-operated emergency lighting in health care facilities shall conform to the appropriate requirements of CSA Z32, "Electrical Safety and Essential Electrical Systems in Health Care Facilities". |  | Common Sentence | Yes | Lighting
2015 | ON | NBC | Div B | 3.2.7.4.(1) | Emergency Power for Lighting | An emergency power supply shall be (a) provided to maintain the emergency lighting required by this Subsection from a power source such as batteries or generators that will continue to supply power in the event that the regular power supply to the building is interrupted, and (b) so designed and installed that upon failure of the regular power it will assume the electrical load automatically for a period of (i) 2 h for a building within the scope of Subsection 3.2.6., (ii) 1 h for a building of Group B major occupancy classification that is not within the scope of Subsection 3.2.6., (iii) 1 h for a building constructed in accordance with Article 3.2.2.50. or 3.2.2.58., and (iv) 30 min for a building of any other occupancy. | obc2019_divb | Div B | 3.2.7.4.(1) | 3.2.7.4. Emergency Power for Lighting | An emergency power supply shall be, (a) provided to maintain the emergency lighting required by this Subsection from a power source such as batteries or generators that will continue to supply power in the event that the regular power supply to the building is interrupted, and (b) so designed and installed that upon failure of the regular power it will assume the electrical load automatically for a period of, (i) 2 h for a building within the scope of Subsection 3.2.6., (ii) 1 h for a building of Group B major occupancy classification that is not within the scope of Subsection 3.2.6., (ii.1) 1 h for a building that contains a Group C major occupancy retirement home and that is not within the scope of Subsection 3.2.6., (iii) 1 h for a building within the scope of Article 3.2.2.43A. or 3.2.2.50A., and (iv) 30 min for any other building. |  | Common Sentence | Yes | Lighting
2015 | ON | NBC | Div B | 3.2.7.4.(2) | Emergency Power for Lighting | If self-contained emergency lighting units are used, they shall conform to CSA C22.2 No. 141-10 Emergency Lighting Equipment | obc2019_divb | Div B | 3.2.7.4.(2) | 3.2.7.4. Emergency Power for Lighting | If self-contained emergency lighting units are used, they shall conform to CSA C22.2 No. 141, "Emergency Lighting Equipment". |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.7.5.(1) | Emergency Power Supply Installation | Except as required by Articles 3.2.7.6. and 3.2.7.7., an emergency electrical power supply system shall be installed in conformance with CSA C282-15 Emergency Electrical Power Supply for Buildings (See Sentence 3.2.7.8.(1) for emergency electrical power supply for voice communication systems.) | obc2019_divb | Div B | 3.2.7.5.(1) | 3.2.7.5. Emergency Power Supply Installation | Except as required by Articles 3.2.7.6. and 3.2.7.7., an emergency electrical power system shall be installed in conformance with CSA C282, "Emergency Electrical Power Supply for Buildings". |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.7.6.(1) | Emergency Power for Treatment Occupancies | Except as required by Article 3.2.7.7., an emergency electrical power supply system for emergency equipment required by this Part for treatment occupancies shall be installed in conformance with CSA Z32-09 Electrical Safety and Essential Electrical Systems in Health Care Facilities (See Note A-3.2.7.6.(1).) | obc2019_divb | Div B | 3.2.7.6.(1) | 3.2.7.6. Emergency Power for Hospitals | Except as required by Article 3.2.7.7., an emergency electrical power system for emergency equipment required by this Part for health care facilities shall be installed in conformance with CSA Z32, "Electrical Safety and Essential Electrical Systems in Health Care Facilities". (See Appendix A.) |  | Common Sentence | Yes | Emergency Power
2015 | ON | NBC | Div B | 3.2.7.7.(1) | Fuel Supply Shut-off Valves | If a liquid or gas fuel-fired engine or turbine for an emergency electric power supply is dependent on a fuel supply from outside the building, the fuel supply shall be provided with a suitably-identified separate shut-off valve outside the building. | obc2019_divb | Div B | 3.2.7.7.(1) | 3.2.7.7. Fuel Supply Shut-Off Valves and Exhaust Pipes | If a liquid or gas fuel-fired engine or turbine for an emergency electric power supply is dependent on a fuel supply from outside the building, the fuel supply shall be provided with a suitably-identified separate shut-off valve outside the building. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.7.8.(1) | Emergency Power for Fire Alarm Systems | Fire alarm systems, including those incorporating a voice communication system, shall be provided with an emergency power supply conforming to Sentences 3.2.7.8.(2) , 3.2.7.8.(3) and 3.2.7.8.(4). | obc2019_divb | Div B | 3.2.7.8.(1) | 3.2.7.8. Emergency Power for Fire Alarm Systems | Fire alarm systems, including those incorporating a voice communication system, shall be provided with an emergency power supply conforming to Sentences (2) to (4). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.7.8.(2) | Emergency Power for Fire Alarm Systems | The emergency power supply required by Sentence 3.2.7.8.(1) shall be supplied from (a) a generator, (b) batteries, or (c) a combination thereof. | obc2019_divb | Div B | 3.2.7.8.(2) | 3.2.7.8. Emergency Power for Fire Alarm Systems | The emergency power supply required by Sentence (1) shall be supplied from, (a) a generator, (b) batteries, or (c) a combination of the items described in Clauses (a) and (b). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.7.8.(3) | Emergency Power for Fire Alarm Systems | The emergency power supply required by Sentence 3.2.7.8.(1) shall be capable of providing supervisory power for not less than 24 h, and immediately following that period, emergency power under full load for not less than 2 h for a building within the scope of part 3., 1 h for a building classified as a Group B major occupancy that is not within the scope of part 3., 1 h for a building constructed in accordance with Article 3.2.2.50. or 3.2.2.58., 5 min for a building not required to be equipped with an annunciator, and 30 min for any other building. | obc2019_divb | Div B | 3.2.7.8.(3) | 3.2.7.8. Emergency Power for Fire Alarm Systems | The emergency power supply required by Sentence (1) shall be capable of providing, supervisory power for not less than 24 h, and immediately following, emergency power under full load for not less than, 2 h for a building within the scope of Subsection 3.2.6., 1 h for a building classified as Group B major occupancy that is not within the scope of Subsection 3.2.6., (ii.1) 1 h for a building that contains a Group C major occupancy retirement home and that is not within the scope of Subsection 3.2.6., 1 h for a building within the scope of Article 3.2.2.43A. or 3.2.2.50A., 5 min for a building not required to be equipped with an annunciator, and 30 min for any other building. |  | Common Sentence | Yes | Emergency Power
2015 | ON | NBC | Div B | 3.2.7.8.(4) | Emergency Power for Fire Alarm Systems | The emergency power supply required by Sentence 3.2.7.8.(1) shall be designed so that, in the event of a failure of the normal power source, there is an immediate automatic transfer to emergency power with no loss of information. | obc2019_divb | Div B | 3.2.7.8.(4) | 3.2.7.8. Emergency Power for Fire Alarm Systems | The emergency power supply required by Sentence (1) shall be designed so that, in the event of a failure of the normal power source, there is an immediate automatic transfer to emergency power with no loss of information. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.7.9.(1) | Emergency Power for Building Services | An emergency power supply capable of operating under a full load for not less than 2 h shall be provided by an emergency generator for (a) every elevator serving storeys above the first storey in a building that is more than 36 m high measured between grade and the floor level of the top storey and every elevator for firefighters in conformance with Sentence (2), (b) water supply for firefighting in conformance with Article 3.2.5.7., if the supply is dependent on electrical power supplied to the building, (c) fans and other electrical equipment that are installed to maintain the air quality specified in Articles 3.2.6.2. and 3.3.3.6., (d) fans required for venting by Article 3.2.6.6., and (e) fans required by Clause 3.2.8.4.(1)(c) and Article 3.2.8.7. in buildings within the scope of Subsection 3.2.6. (See Note A-3.2.7.9.(1).) | obc2019_divb | Div B | 3.2.8.10.(1) | 3.2.8.10. Emergency Power Supply | In a building that is more than 18 m in height, measured between grade and the floor level of the top storey, an emergency power supply capable of operating under a full load for at least 2 h shall be provided by an emergency generator or by a separate service not supplied by the same substation as the primary source for fans required for smoke control purposes in Articles 3.2.8.4., 3.2.8.5., 3.2.8.6. and 3.2.8.9. |  | Common Sentence | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B | 3.2.7.9.(1) | Emergency Power for Building Services | An emergency power supply capable of operating under a full load for not less than 2 h shall be provided by an emergency generator for (a) every elevator serving storeys above the first storey in a building that is more than 36 m high measured between grade and the floor level of the top storey and every elevator for firefighters in conformance with Sentence 3.2.7.9.(2),(b) water supply for firefighting in conformance with Article 3.2.5.7., if the supply is dependent on electrical power supplied to the building, (c) fans and other electrical equipment that are installed to maintain the air quality specified in Articles 3.2.6.2. and 3.3.3.6. , (d) fans required for venting by Article 3.2.6.6., and (e) fans required by Sentence 3.2.8.4.(1) and Article 3.2.8.7. in buildings within the scope of part 3. | obc2019_divb | Div B | 3.2.7.9.(1) | 3.2.7.9. Emergency Power for Building Services | An emergency power supply capable of operating under a full load for not less than 2 h shall be provided by an emergency generator for, (a) every elevator serving storeys above the first storey in a building that is more than 36 m high measured between grade and the floor level of the top storey and every elevator for firefighters in conformance with Sentence (2),(b) water supply for firefighting in conformance with Article 3.2.5.7., if the supply is dependent on electrical power supplied to the building, and the building is within the scope of Subsection 3.2.6., (c) fans and other electrical equipment that are installed to maintain the air quality specified in Articles 3.2.6.2. and 3.3.3.6., other than air handling systems described in Sentence 3.2.6.2.(6), and (d) fans required for venting by Article 3.2.6.6. |  | Common Sentence | Yes | Emergency Power
2015 | ON | NBC | Div B | 3.2.7.9.(2) | Emergency Power for Building Services | Except as permitted by Sentence 3.2.7.9.(3), the emergency power supply for elevators required by Sentence 3.2.7.9.(1) shall be capable of operating all elevators for firefighters plus one additional elevator simultaneously. | obc2019_divb | Div B | 3.2.7.9.(2) | 3.2.7.9. Emergency Power for Building Services | Except as permitted by Sentence (3), the emergency power supply for elevators required by Clause (1)(a) shall be capable of operating all elevators for firefighters plus one additional elevator simultaneously. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.7.9.(3) | Emergency Power for Building Services | Sentence 3.2.7.9.(2) does not apply if the time to recall all elevators under emergency power supply is not more than 5 min, each from its most remote storey to the storey containing the entrance for firefighter access referred to in Articles 3.2.5.4. and 3.2.5.5., or to a transfer lobby. | obc2019_divb | Div B | 3.2.7.9.(3) | 3.2.7.9. Emergency Power for Building Services | Sentence (2) does not apply if the time to recall all elevators under emergency power supply is not more than 5 min, each from its most remote storey to, the storey containing the entrance for firefighter access referred to in Articles 3.2.5.4 and 3.2.5.5., or to a transfer lobby. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.8.1.(1) | Application | Except as permitted by Article 3.2.8.2. and Sentence 3.3.4.2.(3), the portions of a floor area or a mezzanine that do not terminate at an exterior wall, a firewall or a vertical shaft shall terminate at a vertical fire separation having a fire-resistance rating not less than that required for the floor assembly and extending from the floor assembly to the underside of the floor or roof assembly above, or be protected in conformance with the requirements of Articles 3.2.8.3. to 3.2.8.8. | obc2019_divb | Div B | 3.2.8.1.(1) | 3.2.8.1. Application | Except as permitted by Article 3.2.8.2. and Sentence 3.3.4.2.(3), the portions of a floor area or a mezzanine that do not terminate at an exterior wall, a firewall or a vertical shaft shall, terminate at a vertical fire separation having a fire-resistance rating not less than that required for the floor assembly and extending from the floor assembly to the underside of the floor or roof assembly above, or be protected in conformance with the requirements of Articles 3.2.8.3. to 3.2.8.11. |  | Common Sentence | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B | 3.2.8.1.(2) | Application | The penetration of a floor assembly by an exit or a vertical service space shall conform to the requirements of Sections 3. , 3. and 3. | obc2019_divb | Div B | 3.2.8.1.(2) | 3.2.8.1. Application | The penetration of a floor assembly by an exit or a vertical service space shall conform to the requirements of Sections 3.4. to 3.6. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.8.1.(3) | Application | A floor area containing sleeping rooms in a building of Group B, Division 2 major occupancy shall not be constructed as part of an interconnected floor space. | obc2019_divb | Div B | 3.2.8.1.(3) | 3.2.8.1. Application | A floor area containing sleeping rooms in a building of Group B, Division 2 or 3 major occupancy shall not be constructed as part of an interconnected floor space. |  | Common Sentence | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B | 3.2.8.2.(1) | Exceptions to Special Protection | A mezzanine need not terminate at a vertical fire separation nor be protected in conformance with the requirements of Articles 3.2.8.3. to 3.2.8.8. provided the mezzanine (a) serves a Group A, Division 1 major occupancy, (b) serves a Group A, Division 3 major occupancy in a building not more than 2 storeys in building height, or (c) serves a Group A, C, D, E or F major occupancy and (i) is 500 m2 or less in area, and (ii) conforms to Sentence 3.2.1.1.(3) or 3.2.1.1.(4). | obc2019_divb | Div B | 3.2.8.2.(1) | 3.2.8.2. Exceptions to Special Protection | A mezzanine need not terminate at a vertical fire separation nor be protected in conformance with the requirements of Articles 3.2.8.3. to 3.2.8.11. provided the mezzanine, (a) serves a Group A, Division 1 major occupancy, (b) serves a Group A, Division 3 major occupancy in a building not more than 2 storeys in building height, (c) serves a Group A, C, D, E or F major occupancy and the mezzanine conforms to Sentence 3.2.1.1.(3) or (8), (d) is not considered a storey in Sentence 3.2.1.1.(4) in calculating building height provided the mezzanine is not more than 500 m2 in area and does not contain a Group B occupancy, or (e) is not considered a storey in calculating building height in Sentence 3.2.1.1.(7). |  | Common Sentence | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B | 3.2.8.2.(2) | Exceptions to Special Protection | Except for floors referred to in Sentence 3.1.10.3.(1) and Article 3.2.1.2., openings through a horizontal fire separation for vehicular ramps in a storage garage are not required to be protected with closures and need not conform to this Subsection. | obc2019_divb | Div B | 3.2.8.2.(2) | 3.2.8.2. Exceptions to Special Protection | Except for floors referred to in Sentence 3.1.10.3.(1) and Article 3.2.1.2., openings through a horizontal fire separation for vehicular ramps in a storage garage are not required to be protected with closures and need not conform to this Subsection. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.8.2.(3) | Exceptions to Special Protection | If a closure in an opening in a fire separation would disrupt the nature of a manufacturing process, such as a continuous flow of material from storey to storey, the closure for the opening is permitted to be omitted provided precautions are taken to offset the resulting hazard. (See Note A-3.2.8.2.(3).) | obc2019_divb | Div B | 3.2.8.2.(3) | 3.2.8.2. Exceptions to Special Protection | If a closure in an opening in a fire separation would disrupt the nature of a manufacturing process, such as a continuous flow of material from storey to storey, the closure for the opening is permitted to be omitted provided precautions are taken to offset the resulting hazard. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.2.8.2.(4) | Exceptions to Special Protection | An interconnected floor space in a Group B, Division 1 occupancy need not conform to the requirements of Articles 3.2.8.3. to 3.2.8.8. provided the interconnected floor space does not interconnect more than 2 adjacent storeys. | obc2019_divb | Div B | 3.2.8.2.(4) | 3.2.8.2. Exceptions to Special Protection | An interconnected floor space in a Group B, Division 1 occupancy need not conform to the requirements of Articles 3.2.8.3. to 3.2.8.11. provided the interconnected floor space does not interconnect more than 2 adjacent storeys. |  | Common Sentence | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B | 3.2.8.2.(5) | Exceptions to Special Protection | Except as permitted by Sentence 3.2.8.2.(6), openings for escalators and inclined moving walks need not conform to the requirements in Articles 3.2.8.3. to 3.2.8.8. provided (a) the opening for each escalator or walk does not exceed 10 m2 , (b) the building is sprinklered throughout, and (c) the interconnected floor space contains only Group A, Division 1, 2 or 3, Group D or Group E major occupancies (see Note A-3.2.8.2.(6)(c)). | obc2019_divb | Div B | 3.2.8.2.(5) | 3.2.8.2. Exceptions to Special Protection | Except as permitted by Sentence (6), openings for stairways, escalators and inclined moving walks need not conform to the requirements in Articles 3.2.8.3. to 3.2.8.11. provided, (a) the opening for each stairway, escalator or walk does not exceed 10 m2, (b) the building is sprinklered throughout, and (c) the interconnected floor space contains only Group A, Division 1, 2 or 3, Group D or Group E occupancies. |  | Common Sentence | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B | 3.2.8.2.(6) | Exceptions to Special Protection | An interconnected floor space need not conform to the requirements of Articles 3.2.8.3. to 3.2.8.8., provided (a) it consists of the first storey and the storey next above or below it, but not both, (b) it is sprinklered throughout or, where the building area is not more than one half of the area permitted by Subsection 3.2.2., the openings through the floor are used only for stairways, escalators or moving walks (see Note A-3.2.8.2.(6)(b)), and (c) it contains only Group A, Division 1, 2 or 3, Group D, Group E, or Group F, Division 2 or 3 major occupancies (see Note A-3.2.8.2.(6)(c)). | obc2019_divb | Div B | 3.2.8.2.(6) | 3.2.8.2. Exceptions to Special Protection | An interconnected floor space need not conform to the requirements of Articles 3.2.8.3. to 3.2.8.11. provided, (a) the interconnected floor space consists of the first storey and the storey next above or below it, but not both, (b) the interconnected floor space is sprinklered, and (c) the interconnected floor space contains only Group A, Division 1, 2 or 3, Group D, Group E, or Group F, Division 2 or 3 occupancies. |  | Common Sentence | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B | 3.2.8.3.(1) | Sprinklers | A building containing an interconnected floor space shall be sprinklered throughout. | obc2019_divb | Div B | 3.2.8.7.(1) | 3.2.8.7. Sprinklers | In a building containing an interconnected floor space, storeys that are wholly or partially within an interconnected floor space and all storeys below an interconnected floor space shall be sprinklered. |  | Common Sentence | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B | 3.2.8.4.(1) | Vestibules | An exit opening into an interconnected floor space shall be protected at each (a) with doorways that are not less than 1.8 m apart, (b) that is separated from the remainder of the floor area by a fire separation that is not required to have a fire-resistance rating (see Note A-3.1.8.1.(1)(b)), and (c) that is designed to limit the passage of smoke so that the exit stair shaft does not contain more than 1% by volume of contaminated air from the fire floor, assuming an outdoor temperature equal to the January design temperature on a 2.5% basis determined in accordance with Subsection 1.1.3. (see Note A-3.2.8.4.(1)(c)). | obc2019_divb | Div B | 3.2.8.4.(3) | 3.2.8.4. Exits | Where a vestibule protecting an exit stairshaft is incorporated into the design of the building to meet the requirements of Sentence (1) or (2), such vestibule shall, (a) be designed so that each doorway for a door opening into the vestibule is located at least 1 800 mm from a door or doors opening outward from the vestibule, (b) be separated from the remainder of the floor area by a fire separation having a fire-resistance rating at least equal to that required for the exit that it serves except that the fire-resistance rating of a fire separation between the vestibule and a public corridor need not exceed 45 min, and (c) not have a door or doors opening into more than one exit stairshaft. |  | Common Sentence | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B | 3.2.8.4.(1) | Vestibules | An exit opening into an interconnected floor space shall be protected at each opening into the interconnected floor space by a vestibule (a) with doorways that are not less than 1.8 m apart, (b) that is separated from the remainder of the floor area by a fire separation that is not required to have a fire-resistance rating (see Note A-3.1.8.1.(1)(b)), and (c) that is designed to limit the passage of smoke so that the exit stair shaft does not contain more than 1% by volume of contaminated air from the fire floor, assuming an outdoor temperature equal to the January design temperature on a 2.5% basis determined in accordance with Subsection 1.1.3. (see Note A-3.2.8.4.(1)(c)). | obc2019_divb | Div B | 3.2.8.4.(1) | 3.2.8.4. Exits | A building that is more than 18 m in height, measured between grade and the floor level of the top storey, and that contains an interconnected floor space, shall be designed to limit the passage of smoke from a fire into exit stairshafts opening into an interconnected floor space so that during a 2 h period after the start of fire, such stairshafts will not contain more than 1% by volume of contaminated air from the fire floor, assuming an outdoor temperature equal to the January design temperature on a 2.5% basis. |  | Common Sentence | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B | 3.2.8.4.(3) | Vestibules | If an elevator hoistway opens into an interconnected floor space and into storeys above the interconnected floor space, either the elevator doors opening into the interconnected floor space or the elevator doors opening into the storeys above the interconnected floor space shall be protected by vestibules conforming to Sentence 3.2.8.4.(1). | obc2019_divb | Div B | 3.2.8.5.(1) | 3.2.8.5. Elevators | Except as provided in Sentence (2), where an elevator shaft opens into an interconnected floor space and into storeys that are above such space and that have floor levels more than 18 m above grade, either the elevator doors opening into the interconnected floor space or the elevator doors opening into the storeys above the interconnected floor space shall be protected by vestibules that, (a) are designed to restrict the passage of contaminated air to the limit described in Sentence 3.2.8.4.(1), and (b) conform to the requirements of Sentence 3.2.8.4.(3). |  | Common Sentence | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B | 3.2.8.4.(3) | Vestibules | If an elevator hoistway opens into an interconnected floor space and into storeys above the interconnected floor space, either the elevator doors opening into the interconnected floor space or the elevator doors opening into the storeys above the interconnected floor space shall be protected by vestibules conforming to Sentence (1). | obc2019_divb | Div B | 3.5.3.1.(3) | 3.5.3.1. Fire Separations for Elevator Hoistways | Where the elevator described in Sentence (2) has doors opening into storeys above or below the interconnected floor space it shall be protected by vestibules conforming to the requirements of Sentence 3.2.8.5.(1). |  | Common Sentence | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B | 3.2.8.5.(1) | Protected Floor Space | A protected floor space used to satisfy the requirements of Clause 3.4.3.2.(6)(b) shall (a) be separated from the interconnected floor space by a fire separation having a fire-resistance rating not less than that required for the floor assembly of the storey in which it is located, (b) have all openings in the vertical fire separation between a protected floor space and the adjacent interconnected floor space protected by vestibules conforming to Sentence 3.2.8.4.(1), and (c) be designed so that it is not necessary to enter the interconnected floor space to reach an exit. | obc2019_divb | Div B | 3.2.8.4.(5) | 3.2.8.4. Exits | Where a portion of a floor area is not within an interconnected floor space, required access to exit from such portion of a floor area shall not lead through an interconnected floor space. |  | Common Sentence | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B | 3.2.8.7.(1) | Mechanical Exhaust System | A mechanical exhaust system shall be provided to remove air from an interconnected floor space at a rate of 4 air changes per hour. (See Note A-3.2.8.7.(1).) | obc2019_divb | Div B | 3.2.8.9.(6) | 3.2.8.9. Smoke Control | A mechanical exhaust shall be provided to remove air at the top of an interconnected floor space at the rate of at least six air changes per hour, except that where the volume of the interconnected floor space exceeds 17 000 m3, only four air changes per hour need be provided. |  | Common Sentence | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B | 3.2.8.7.(1) | Mechanical Exhaust System | A mechanical exhaust system shall be provided to remove air from an interconnected floor space at a rate of 4 air changes per hour. (See Note A-3.2.8.7.(1).) | obc2019_divb | Div B | 3.2.8.9.(1) | 3.2.8.9. Smoke Control | A smoke control system conforming to Sentences (2) to (8) shall be designed to control the movement of smoke within a building containing an interconnected floor space. |  | Common Sentence | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B | 3.2.8.7.(2) | Mechanical Exhaust System | The mechanical exhaust system required by Sentence (1) shall be actuated by a switch located on the storey containing the entrance for firefighter access referred to in Articles 3.2.5.4. and 3.2.5.5. near the annunciator for the fire alarm system. | obc2019_divb | Div B | 3.2.8.9.(8) | 3.2.8.9. Smoke Control | Overriding manual controls for the smoke control system shall be provided for fire department use at an acceptable location in the vicinity of the fire alarm annunciator. |  | Common Sentence | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B | 3.2.9.1.(1) | Testing | Where fire protection and life safety systems and systems with fire protection and life safety functions are integrated with each other, they shall be tested as a whole in accordance with ULC CAN/ULC-S1001-11 Integrated Systems Testing of Fire Protection and Life Safety Systems,” to verify that they have been properly integrated. (See Note A-3.2.9.1.(1).) | obc2019_divb | Div B | 3.2.8.11.(1) | 3.2.8.11. Testing | The systems for smoke control and venting described in Articles 3.2.8.4., 3.2.8.5., 3.2.8.6. and 3.2.8.9. shall be tested to ensure satisfactory operation. |  | Common Sentence | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B | 3.2.9.1.(1) | Testing | Where fire protection and life safety systems and systems with fire protection and life safety functions are integrated with each other, they shall be tested as a whole in accordance with ULC CAN/ULC-S1001-11 Integrated Systems Testing of Fire Protection and Life Safety Systems to verify that they have been properly integrated. (See Note A-3.2.9.1.(1).) | obc2019_divb | Div B | 3.2.10.1.(1) | 3.2.10.1. Testing | Where fire protection and life safety systems, and systems with fire protection and life safety functions, are integrated with each other, the systems shall be tested as a whole in accordance with CAN/ULC-S1001, "Integrated Systems Testing of Fire Protection and Life Safety Systems", to verify that the systems have been properly integrated. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.1.(1) | Separation of Suites | Except as permitted by Sentences 3.3.1.1.(2)and 3.3.1.1.(3), each suite in other than business and personal services occupancies shall be separated from adjoining suites by a fire separation having a fire-resistance rating not less than 1 h. (See also Subsection 3.3.3. for care, treatment or detention occupancies, Article 3.3.4.2. for residential occupancies, and Article 3.1.8.7. for fire dampers.) | obc2019_divb | Div B | 3.3.1.1.(1) | 3.3.1.1. Separation of Suites | Except as permitted by Sentences (2) and (3), each suite in other than business and personal services occupancies shall be separated from adjoining suites by a fire separation having a fire-resistance rating not less than 1 h. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.1.(2) | Separation of Suites | The fire-resistance rating of the fire separation required by Sentence (1) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for (a) the floor assembly above the floor area, or (b) the floor assembly below the floor area, if there is no floor assembly above. | obc2019_divb | Div B | 3.3.1.1.(2) | 3.3.1.1. Separation of Suites | The fire-resistance rating of the fire separation required by Sentence (1) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for, (a) the floor assembly above the floor area, or (b) the floor assembly below the floor area, if there is no floor assembly above. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.1.(3) | Separation of Suites | Occupancies that are served by public corridors conforming to Sentence 3.3.1.4.(4)(b) in a building that is sprinklered throughout, are not required to be separated from one another by fire separations provided the occupancies are (a) suites of business and personal services occupancy, (b) fast food vending operations that do not provide seating for customers, (c) suites of mercantile occupancy, or (d) any combination of these occupancies. | obc2019_divb | Div B | 3.3.1.1.(3) | 3.3.1.1. Separation of Suites | Occupancies that are served by public corridors conforming to Clause 3.3.1.4.(4)(b) in a building that is sprinklered, are not required to be separated from one another by fire separations provided the occupancies are, (a) suites of business and personal services occupancy, (b) fast food vending operations that do not provide seating for customers, (c) suites of mercantile occupancy, or (d) any combination of these occupancies. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.10.(1) | Aisles | Except as otherwise stated in this Section, aisles shall be provided in conformance with the NFC. | obc2019_divb | Div B | 3.3.1.9.(15) | 3.3.1.9. Corridors | Except as otherwise required by this Section, aisles shall be provided in conformance with the Fire Code made under the Fire Protection and Prevention Act, 1997. |  | Common Sentence | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.3.1.11.(1) | Door Swing | Except as permitted by Sentence 3.3.1.11.(5) and Article 3.3.1.12., a door that opens into a corridor or other facility providing access to exit from a suite or room not located within a suite shall swing on a vertical axis. | obc2019_divb | Div B | 3.3.1.10.(1) | 3.3.1.10. Door Swing | Except as permitted by Sentence (5) and Article 3.3.1.11., a door that opens into a corridor or other facility providing access to exit from a suite, or a room not located within a suite, shall swing on a vertical axis. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.11.(2) | Door Swing | Except as permitted by Article 3.3.1.12., a door that opens into a corridor or other facility providing access to exit from a room or suite that is used or intended for an occupant load more than 60 or for a high-hazard industrial occupancy shall swing in the direction of travel to the exit. | obc2019_divb | Div B | 3.3.1.10.(2) | 3.3.1.10. Door Swing | Except as permitted by Article 3.3.1.11., a door that opens into a corridor or other facility providing access to exit from a room or suite shall swing in the direction of travel to the exit if the room or suite is used or intended for, an occupant load more than 60, a high hazard industrial occupancy, or a hazardous classroom in an elementary or secondary school. |  | Common Sentence | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.3.1.11.(3) | Door Swing | Every door that divides a corridor that is not wholly contained within a suite shall swing on a vertical axis in the direction of travel to the exit. | obc2019_divb | Div B | 3.3.1.10.(3) | 3.3.1.10. Door Swing | Every door that divides a corridor that is not wholly contained within a suite shall swing on a vertical axis in the direction of travel to the exit where the corridor provides access to exit for, an occupant load more than 60, a high hazard industrial occupancy, a hazardous classroom in an elementary or secondary school, a Group B, Division 2 or 3 occupancy, or a retirement home. |  | Common Sentence | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.3.1.11.(4) | Door Swing | If a pair of doors is installed in a corridor that provides access to exit in both directions, the doors shall swing in opposite directions, with the door on the right hand side swinging in the direction of travel to the exit. | obc2019_divb | Div B | 3.3.1.10.(4) | 3.3.1.10. Door Swing | If a pair of doors is installed in a corridor that provides access to exit in both directions, the doors shall swing in opposite directions, with the door on the right hand side swinging in the direction of travel to the exit. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.11.(5) | Door Swing | Doors that serve storage suites not more than 28 m2 in area in warehousing buildings need not conform to Sentence 3.3.1.11.(1). | obc2019_divb | Div B | 3.3.1.10.(5) | 3.3.1.10. Door Swing | Doors that serve individual storage spaces not more than 28 m2 in area in self-service storage buildings need not conform to Sentence (1). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.12.(1) | Sliding Doors | Except as permitted by Sentences 3.3.1.12.(2) and 3.3.1.11.(5) , a sliding door provided in the locations described in Article 3.3.1.11. shall be designed and installed to swing on the vertical axis in the direction of travel to the exit when pressure is applied, and be identified as a swinging door by means of a label or decal affixed to it. | obc2019_divb | Div B | 3.3.1.11.(1) | 3.3.1.11. Sliding Doors | Except as permitted by Sentences (2) and 3.3.1.10.(5), a sliding door provided in the locations described in Article 3.3.1.10. shall, be designed and installed to swing on the vertical axis in the direction of travel to the exit when pressure is applied, and be identified as a swinging door by means of a label or decal affixed to it. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.12.(2) | Sliding Doors | In a Group B, Division 1 occupancy, or in an impeded egress zone in other occupancies, sliding doors used in an access to exit need not conform to Sentence 3.3.1.12.(1) and Article 3.3.1.11. | obc2019_divb | Div B | 3.3.1.11.(2) | 3.3.1.11. Sliding Doors | In a Group B, Division 1 occupancy, or in an impeded egress zone in other occupancies, sliding doors used in an access to exit need not conform to Sentence (1) and Article 3.3.1.10. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.12.(3) | Sliding Doors | Movable partitions used to separate a public corridor from an adjacent business and personal services occupancy or a mercantile occupancy need not conform to Sentence 3.3.1.12.(1) and Sentences 3.3.1.11.(1) and 3.3.1.11.(2), provided the partitions are not located in the only means of egress. (See Note A-3.3.1.12.(3).) | obc2019_divb | Div B | 3.3.1.11.(3) | 3.3.1.11. Sliding Doors | Movable partitions used to separate a public corridor from an adjacent business and personal services occupancy or a mercantile occupancy need not conform to Sentence (1) and Sentences 3.3.1.10.(1) and (2) provided the partitions are not located in the only means of egress. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.13.(1) | Doors and Door Hardware | Except as required by Article 3.3.3.4., a door that opens into or is located within a public corridor or other facility that provides access to exit from a suite shall provide a clear opening of not less than 800 mm if there is only one door leaf, in a doorway with multiple leaves, have the active leaf providing a clear opening of not less than 800 mm, not open onto a step, and have a threshold not more than 13 mm higher than the surrounding finished floor surface, except where it is used to confine the spillage of flammable liquids within a service room or within a room in an industrial occupancy, or provides access to an exterior balcony, unless the balcony is required by Sentence 3.3.1.7.(1). | obc2019_divb | Div B | 3.3.1.12.(1) | 3.3.1.12. Doors and Door Hardware | Except as required by Article 3.3.3.4. and Sentences 3.3.4.11.(11), 3.8.3.3.(1) and (2), a door that opens into or is located within a public corridor or other facility that provides access to exit from a suite, shall provide a clear opening of not less than 800 mm, if there is only one door leaf, shall, in a doorway with multiple leaves, have the active leaf providing a clear opening of not less than 800 mm, shall not open onto a step, and shall not have a threshold more than 13 mm higher than the floor surface except where, the threshold is used to contain spillage, or the doorway provides access to an exterior balcony, other than a balcony required by Sentence 3.3.1.7.(2). |  | Common Sentence | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.3.1.13.(10) | Doors and Door Hardware | Locking devices permitted by Sentence 3.3.1.13.(6) that are electrically operated shall be designed to operate on emergency power, and capable of manual release by security personnel. | obc2019_divb | Div B | 3.3.1.12.(9) | 3.3.1.12. Doors and Door Hardware | Locking devices permitted by Sentence (6) that are electrically operated shall be, designed to operate on emergency power, and capable of manual release by security personnel. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.13.(2) | Doors and Door Hardware | Except as provided in Sentences (6)and (7), a door in an access to exit shall be readily openable in travelling to an exit without requiring keys, special devices or specialized knowledge of the door-opening mechanism. | obc2019_divb | Div B | 3.3.1.12.(2) | 3.3.1.12. Doors and Door Hardware | A door in an access to exit shall be readily openable in travelling to an exit without requiring keys, special devices or specialized knowledge of the door opening mechanism, except that this requirement does not apply to a door serving a contained use area, or an impeded egress zone, provided the locking devices conform to Sentence (6). |  | Common Sentence | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.3.1.13.(3) | Doors and Door Hardware | Except as permitted by Sentence 3.3.1.13.(4), door release hardware shall comply with Sentence 3.8.3.8.(1) and the door shall be openable with not more than one releasing operation. (See also Sentence 3.8.3.6.(4).) | obc2019_divb | Div B | 3.3.1.12.(3) | 3.3.1.12. Doors and Door Hardware | Except as permitted by Sentence (4), door release hardware shall be operable by one hand and the door shall be openable with not more than one releasing operation. |  | Common Sentence | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.3.1.13.(4) | Doors and Door Hardware | An egress door from an individual dwelling unit or from a suite of residential occupancy is permitted to be provided with additional devices that require a releasing operation additional to the main door release hardware, provided the devices are readily operable from the inside without the use of keys, special devices or specialized knowledge. (See Note A-3.3.1.13.(4).) | obc2019_divb | Div B | 3.3.1.12.(4) | 3.3.1.12. Doors and Door Hardware | Except in a retirement home, an egress door from an individual dwelling unit or from a suite of residential occupancy is permitted to be provided with additional devices that require a releasing operation additional to the main door release hardware, provided the devices are readily operable from the inside without the use of keys, special devices or specialized knowledge. (See Appendix A.) |  | Common Sentence | Yes | Retirement Homes
2015 | ON | NBC | Div B | 3.3.1.13.(5) | Doors and Door Hardware | Door release hardware shall be installed not more than 1?200 mm above the finished floor. | obc2019_divb | Div B | 3.3.1.12.(5) | 3.3.1.12. Doors and Door Hardware | Door release hardware shall be installed not more than 1 200 mm above the finished floor. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.13.(6) | Doors and Door Hardware | An egress door in an access to exit serving a contained use area or an impeded egress zone is permitted to be equipped with locking devices, provided they can be released either locally or remotely in conformance with Sentence 3.3.1.13.(8) or 3.3.1.13.(9). (See Note A-3.3.1.13.(6).) | obc2019_divb | Div B | 3.3.1.12.(6) | 3.3.1.12. Doors and Door Hardware | A door in a means of egress serving a contained use area or an impeded egress zone is permitted to be equipped with locking devices that can be released either locally or remotely in conformance with Sentence (7) or (8). (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.13.(7) | Doors and Door Hardware | A door in an access to exit is permitted to be equipped with an electromagnetic lock conforming to Sentence 3.4.6.16.(4) or 3.4.6.16.(5). | obc2019_divb | Div B | 3.3.1.12.(10) | 3.3.1.12. Doors and Door Hardware | A door in an access to exit is permitted to be equipped with an electromagnetic locking device conforming to Sentence 3.4.6.16.(4), except that this permission does not apply to a door, (a) in an elementary or secondary school, (b) a door leading from a Group F, Division 1 occupancy, or (c) except as provided in Sentence (11), requiring a latch release device by Article 3.3.2.6. |  | Common Sentence | Yes | Electromagnetic Locks
2015 | ON | NBC | Div B | 3.3.1.13.(8) | Doors and Door Hardware | Local locking devices permitted by Sentence 3.3.1.13.(6) shall be operable by a key from both sides of the door. | obc2019_divb | Div B | 3.3.1.12.(7) | 3.3.1.12. Doors and Door Hardware | Local locking devices permitted by Sentence (6) shall be operable by a key from both sides of the door. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.13.(9) | Doors and Door Hardware | Controls for the remote release of door locking devices permitted by Sentence 3.3.1.13.(6) shall be located in an area readily available to security personnel. | obc2019_divb | Div B | 3.3.1.12.(8) | 3.3.1.12. Doors and Door Hardware | Controls for the remote release of door locking devices permitted by Sentence (6) shall be located in an area readily available to security personnel. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.14.(1) | Ramps and Stairways | Except as permitted by Sentence (2), Article 3.3.4.7. and Subsectin 3.3.2., ramps and stairways that do not serve as exits shall conform to the requirements for exit ramps and stairways stated in Sentence 3.4.3.2.(8) and Articles 3.4.3.4., and 3.4.6.1. to 3.4.6.9. | obc2019_divb | Div B | 3.3.1.13.(1) | 3.3.1.13. Ramps and Stairways | Except as permitted by Sentence (2), Article 3.3.4.7. and Subsection 3.3.2., ramps and stairways that do not serve as exits shall conform to the dimensional, guard, handrail and slip-resistance requirements for exit ramps and stairways of Sentence 3.4.3.2.(7) and Articles 3.4.3.5. and 3.4.6.1. to 3.4.6.9. |  | Common Sentence | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.3.1.14.(2) | Ramps and Stairways | Ramps and stairways that serve service rooms, service spaces or industrial occupancies need not comply with Sentence 3.3.1.14.(1), provided they are intended only for occasional use for servicing equipment and machinery, and they do not serve as exits. | obc2019_divb | Div B | 3.3.1.13.(2) | 3.3.1.13. Ramps and Stairways | Ramps and stairways that do not conform to the requirements of Sentence (1) and are intended only for occasional use for servicing equipment and machinery are permitted, to serve service rooms and service spaces, and in industrial occupancies. |  | Common Sentence | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.3.1.15.(1) | Exterior Passageways | An exterior passageway leading to a required exit shall conform to the requirements of part 3. for exterior exit passageways. | obc2019_divb | Div B | 3.3.1.14.(1) | 3.3.1.14. Exterior Passageways | An exterior passageway leading to a required exit shall conform to the requirements of Section 3.4. for exterior exit passageways. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.16.(1) | Tapered Treads in a Curved Flight Curved Flights in Exits | Exit stair flights shall consist solely of (a) straight flights, or (b) curved flights complying with Sentence (2). | obc2019_divb | Div B | 3.4.6.9.(1) | 3.4.6.9. Curved Flights in Exits | Flights used as an exit shall consist solely of, straight flights, or curved flights complying with Sentence (2). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.16.(1) | Tapered Treads in a Curved Flight | Flights of stairs shall consist solely of straight flights, or curved flights complying with Sentence 3.3.1.16.(2). | obc2019_divb | Div B | 3.3.1.15.(1) | 3.3.1.15. Tapered Treads in a Curved Flight | Flights shall consist solely of, straight flights, or curved flights complying with Sentence (2). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.16.(2) | Tapered Treads in a Curved Flight | Tapered treads in a curved flight that is not required as an exit shall have a minimum run of 150 mm, a run not less than 280 mm when measured at a point 300 mm from the centre line of the handrail at the narrow end of the tread, and a riser conforming to Sentence 3.4.6.8.(2). | obc2019_divb | Div B | 3.3.1.15.(2) | 3.3.1.15. Tapered Treads in a Curved Flight | Tapered treads in a curved flight that is not required as an exit shall have, a minimum run of 150 mm, a run not less than 280 mm when measured at a point 300 mm from the centre line of the inside handrail, and a riser conforming to Sentence 3.4.6.8.(2). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.16.(3) | Tapered Treads in a Curved Flight | Tapered treads shall have a consistent angle and uniform run and rise dimensions in accordance with the construction tolerances stipulated in Article 3.4.6.8. when measured at a point 300 mm from the centre line of the handrail at the narrow end of the tread. | obc2019_divb | Div B | 3.3.1.15.(3) | 3.3.1.15. Tapered Treads in a Curved Flight | Tapered treads shall have a consistent angle and uniform run and rise dimensions in accordance with the construction tolerances described in Article 3.4.6.8. when measured at a point 300 mm from the centre line of the inside handrail. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.16.(4) | Tapered Treads in a Curved Flight | All tapered treads within a flight shall turn in the same direction. | obc2019_divb | Div B | 3.3.1.15.(4) | 3.3.1.15. Tapered Treads in a Curved Flight | All tapered treads within a flight shall turn in the same direction. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.17.(1) | Capacity of Access to Exits | The capacity of an access to exit shall be based on the occupant load of the portion of the floor area served. | obc2019_divb | Div B | 3.3.1.16.(1) | 3.3.1.16. Capacity of Access to Exits | The capacity of an access to exit shall be based on the occupant load of the portionof the floor area served. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.17.(2) | Capacity of Access to Exits | In an access to exit the required width of ramps with a slope not more than 1 in 8, doorways, and corridors shall be based on not less than 6.1 mm per person. | obc2019_divb | Div B | 3.3.1.16.(2) | 3.3.1.16. Capacity of Access to Exits | In an access to exit the required width of ramps with a slope not more than 1 in 8, doorways, and corridors shall be based on not less than 6.1 mm per person. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.17.(3) | Capacity of Access to Exits | In an access to exit the required width of a ramp with a slope more than 1 in 8 shall be based on not less than 9.2 mm per person. | obc2019_divb | Div B | 3.3.1.16.(3) | 3.3.1.16. Capacity of Access to Exits | In an access to exit the required width of a ramp with a slope more than 1 in 8 shall be based on not less than 9.2 mm per person. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.17.(4) | Capacity of Access to Exits | In an access to exit from a floor area used or intended to be used for patients in a Group B, Division 2 occupancy or residents in a Group B, Division 3 occupancy, the required width of corridors, doorways, and ramps shall be based on not less than 18.4 mm per person. | obc2019_divb | Div B | 3.3.1.16.(4) | 3.3.1.16. Capacity of Access to Exits | In an access to exit from a floor area used or intended to be used for patients or residents in a Group B, Division 2 or Division 3 occupancy, the required width of corridors, doorways, and ramps shall be based on not less than 18.4 mm per person. |  | Common Sentence | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.3.1.17.(5) | Capacity of Access to Exits | The capacity of stairs in an access to exit shall conform to the requirements for stairs in Sentences 3.4.3.2.(1) to 3.4.3.2.(3). | obc2019_divb | Div B | 3.3.1.16.(5) | 3.3.1.16. Capacity of Access to Exits | The capacity of stairs in an access to exit shall conform to the requirements for stairs in Sentences 3.4.3.2.(1) to (3). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.17.(6) | Capacity of Access to Exits | In a building that is not sprinklered throughout in accordance with Sentence 3.2.5.12.(1), an access to exit that is part of the principal entrance serving a dance hall or a licensed beverage establishment with an occupant load more than 250 shall provide at least one half of the required exit width. | obc2019_divb | Div B | 3.3.1.16.(6) | 3.3.1.16. Capacity of Access to Exits | In a building that is not sprinklered in accordance with Sentence 3.2.5.13.(1), an access to exit that is part of the principal entrance serving a dance hall or a licensed beverage establishment with an occupant load more than 250 shall be at least one-half of the required exit width. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.18.(1) | Guards | Except as provided in Sentence 3.3.1.18.(5) and Article 3.3.2.9., a guard not less than 1?070 mm high shall be provided around any roof to which access is provided for purposes other than maintenance, at openings into smoke shafts referred to in part 3. that are less than 1?070 mm above the floor, and at each raised floor, mezzanine, balcony, gallery, interior or exterior vehicular ramp, and at other locations where (see Note A-9.8.8.1.) the difference in elevation is more than 600 mm between the walking surface and the adjacent surface, or the adjacent surface within 1.2 m of the walking surface has a slope of more than 1 in 2. | obc2019_divb | Div B | 3.3.1.17.(1) | 3.3.1.17. Guards | Except as provided in Sentence (6) and Articles 3.3.2.8. and 3.3.4.7., a guard not less than 1 070 mm high shall be provided, around each roof to which access is provided for other than maintenance, at openings into smoke shafts referred to in Subsection 3.2.6. that are less than 1 070 mm above the floor, and at each raised floor, mezzanine, balcony, gallery, interior or exterior vehicular ramp, and at other locations where, the difference in level is more than 600 mm between the walking surface and the adjacent surface, or the adjacent surface within 1 200 mm of the walking surface has a slope of more than 1 in 2 away from the walking surface. |  | Common Sentence | Yes | Falling, Tripping, Slipping Protection
2015 | ON | NBC | Div B | 3.3.1.18.(2) | Guards | Except as provided in Sentences (3) and 3.3.2.9.(4) and Articles 3.3.4.7. and 3.3.5.10., openings through guards shall be of a size that prevents the passage of a spherical object whose diameter is more than 100 mm. | obc2019_divb | Div B | 3.3.1.17.(2) | 3.3.1.17. Guards | Except as provided in Sentence (3) and Sentence 3.3.2.8.(4), openings through any guard that is required by Sentence (1) shall be of a size that will prevent the passage of a sphere having a diameter more than 100 mm unless it can be shown that the location and size of openings that exceed this limit do not represent a hazard. |  | Common Sentence | Yes | Falling, Tripping, Slipping Protection
2015 | ON | NBC | Div B | 3.3.1.18.(3) | Guards | Openings through guards other than those required by Sentence 3.3.1.18.(1) that serve occupancies other than industrial occupancies shall be of a size that prevents the passage of a spherical object whose diameter is 100 mm, or permits the passage of a spherical object whose diameter is 200 mm. | obc2019_divb | Div B | 3.3.1.17.(4) | 3.3.1.17. Guards | Openings through any guard that is not required by Sentence (1) and that serves a building of other than industrial occupancy, shall be of a size that, (a) will prevent the passage of a sphere having a diameter more than 100 mm, or (b) will permit the passage of a sphere having a diameter more than 200 mm unless it can be shown that the location and size of openings that exceed these limits do not represent a hazard. |  | Common Sentence | Yes | Falling, Tripping, Slipping Protection
2015 | ON | NBC | Div B | 3.3.1.18.(4) | Guards | Except for guards conforming to Article 3.3.5.10., guards that protect a level located more than one storey or 4.2 m above the adjacent level shall be designed so that no member, attachment or opening located between 140 mm and 900 mm above the level protected by the guard facilitates climbing. (See Note A-9.8.8.6.(1).) | obc2019_divb | Div B | 3.3.1.17.(5) | 3.3.1.17. Guards | Unless it can be shown that the location and size of openings do not present a hazard, a guard shall be designed so that no member, attachment or opening located between 140 mm and 900 mm above the level protected by the guard will facilitate climbing. |  | Common Sentence | Yes | Falling, Tripping, Slipping Protection
2015 | ON | NBC | Div B | 3.3.1.18.(5) | Guards | Sentence 3.3.1.18.(1) does not apply to the front edges of stages, to loading docks, or where access is provided for maintenance purposes only. | obc2019_divb | Div B | 3.3.1.17.(6) | 3.3.1.17. Guards | Sentence (1) does not apply, to the front edges of stages, to loading docks, to floor pits in repair garages, or where access is provided for maintenance purposes only. |  | Common Sentence | Yes | Falling, Tripping, Slipping Protection
2015 | ON | NBC | Div B | 3.3.1.19.(1) | Transparent Doors and Panels | Except as permitted by Sentence 3.3.1.19.(5), a glass or transparent door shall be designed and constructed so that the existence and position of the door is readily apparent, by attaching visually contrasting hardware, bars or other permanent fixtures to it. | obc2019_divb | Div B | 3.3.1.18.(1) | 3.3.1.18. Transparent Doors and Panels | Except for dwelling units and as permitted by Sentence (4), a glass or transparent door shall be designed and constructed so that the existence and position of the door is readily apparent, by attaching visually contrasting hardware, bars or other permanent fixtures to it. |  | Common Sentence | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.3.1.19.(2) | Transparent Doors and Panels | The visibility of fully glazed transparent doors, sidelights and panels shall be enhanced through the inclusion of mullions, markings or other elements that (a) are visually contrasting, (b) are at least 50 mm high, (c) extend the full width of the door, sidelight or panel, and (d) are located between 1 350 mm and 1 500 mm above the floor. | obc2019_divb | Div B | 3.3.1.18.(1) | 3.3.1.18. Transparent Doors and Panels | (1.1) Fully glazed transparent doors, and fully glazed transparent sidelights and panels with widths greater than 300 mm, shall be marked in conformance with Sentence 3.8.3.3.(15). |  | Common Sentence | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.3.1.19.(2) | Transparent Doors and Panels | The visibility of fully glazed transparent doors, sidelights and panels shall be enhanced through the inclusion of mullions, markings or other elements that (a) are visually contrasting, (b) are at least 50mm high, (c) extend the full width of the door, sidelight or panel, and (d) are located between 1 350 mm and 1 500 mm above the floor. | obc2019_divb | Div B | 3.8.3.3.(15) | 3.8.3.3. Doorways and Doors | A door in a barrier-free path of travel consisting of a sheet of glass shall be marked with a continuous opaque strip that, (a) shall be colour and brightness contrasted to the background of the door, (b) shall be at least 50 mm wide, (c) shall be located across the width of the door at a height of 1 350 mm to 1 500 mm above the finished floor, and (d) may incorporate a logo or symbol provided such logo or symbol does not diminish, (i) the opacity of the strip, (ii) the width of the strip, (iii) the colour and brightness contrast of the strip to the background of the door, and (iv) the continuity of the strip across the width of the door. |  | Common Sentence | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B | 3.3.1.19.(3) | Transparent Doors and Panels | A glass door shall be constructed of laminated or tempered safety glass conforming to CGSB CAN/CGSB-12.1-M90 Tempered or Laminated Safety Glass or wired glass conforming to CGSB CAN/CGSB-12.11-M90 Wired Safety Glass | obc2019_divb | Div B | 3.3.1.18.(2) | 3.3.1.18. Transparent Doors and Panels | A glass door shall be constructed of, laminated or tempered safety glass conforming to CAN/CGSB-12.1-M, "Tempered or Laminated Safety Glass", or wired glass conforming to CAN/CGSB-12.11-M, "Wired Safety Glass". |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.19.(4) | Transparent Doors and Panels | Except as permitted by Sentence 3.3.1.19.(5), transparent panels used in an access to exit that, because of their physical configuration or design, could be mistaken as a means of egress shall be made inaccessible by barriers or railings. | obc2019_divb | Div B | 3.3.1.18.(3) | 3.3.1.18. Transparent Doors and Panels | Except as permitted by Sentence (4), transparent panels used in an access to exit that, because of their physical configuration or design, could be mistaken as a means of egress shall be made inaccessible by barriers or railings. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.19.(5) | Transparent Doors and Panels | Sliding glass partitions that separate a public corridor from an adjacent occupancy and that are open during normal working hours need not conform to Sentences 3.3.1.19.(1) and 3.3.1.19.(4), provided the partitions are suitably marked in conformance with Sentence 3.3.1.19.(2) to indicate their existence and position. | obc2019_divb | Div B | 3.3.1.18.(4) | 3.3.1.18. Transparent Doors and Panels | Sliding glass partitions that separate a public corridor from an adjacent occupancy and that are intended to be open during normal working hours need not conform to Sentences (1) and (3), provided the partitions are marked in conformance with Sentence 3.8.3.3.(15). |  | Common Sentence | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.3.1.19.(6) | Transparent Doors and Panels | Where vision glass is provided in doors or transparent sidelights, the lowest edge of the glass shall be no higher than 900 mm above floor level. | obc2019_divb | Div B | 3.3.1.18.(4) | 3.3.1.18. Transparent Doors and Panels | (4.1) Glass in a vision panel in a door or in a transparent sidelight shall conform to Sentence 3.8.3.3.(14). |  | Common Sentence | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.3.1.19.(7) | Transparent Doors and Panels | Glass in doors and in sidelights that could be mistaken for doors, within or at the entrances to dwelling units and in public areas, shall conform to the requirements of Article 9.6.1.4. | obc2019_divb | Div B | 3.3.1.18.(5) | 3.3.1.18. Transparent Doors and Panels | Glass in doors and glass sidelights that could be mistaken for doors, within or at the entrances to dwelling units and in public areas, shall conform to the requirements of Article 9.6.1.4. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.19.(8) | Transparent Doors and Panels | A window in a public area that extends to less than 1?000 mm above the floor and is located above the second storey in a building of residential occupancy, shall be protected by a barrier or railing to not less than 1?070 mm above the floor, or the window shall be non-openable and designed to withstand the lateral design loads for balcony guards required by Article 4.1.5.14. | obc2019_divb | Div B | 3.3.1.18.(6) | 3.3.1.18. Transparent Doors and Panels | A window in a public area that extends to less than 1 070 mm above the floor and is located above the second storey in a building of residential occupancy, shall be protected by a barrier or railing from the floor to not less than 1 070 mm above the floor, or the window shall be non-openable and designed to withstand the lateral design loads for balcony guards required by Article 4.1.5.14. |  | Common Sentence | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.3.1.2.(1) | Hazardous Substances, Equipment and Processes | Except as provided in Subsections 3.3.5. and 3.3.6., the storage, handling and use of hazardous substances shall be in conformance with (a) provincial or territorial regulations or municipal bylaws, or (b) in the absence of the regulations or bylaws referred to in Clause (a), the NFC. (See Note A-3.3.1.2.(1).) | obc2019_divb | Div B | 3.3.1.2.(1) | 3.3.1.2. Hazardous Substances, Equipment and Processes | Except as provided in Subsection 3.3.6., the storage, handling and use of the hazardous substances shall be in conformance with, (a) the Fire Code made under the Fire Protection and Prevention Act, 1997, or (b) the CCBFC NRCC 56192, “National Fire Code of Canada”, in the absence of regulations referred to in Clause (a). |  | Common Sentence | Yes | Fire Hazards
2015 | ON | NBC | Div B | 3.3.1.2.(2) | Hazardous Substances, Equipment and Processes | Systems for the ventilation of cooking equipment that is not within a dwelling unit and is used in processes producing grease-laden vapours shall be designed and installed in conformance with Articles 3.6.3.5., 6.3.1.7.and 6.9.1.3.(See Note A-3.3.1.2.(2).) | obc2019_divb | Div B | 3.3.1.2.(2) | 3.3.1.2. Hazardous Substances, Equipment and Processes | Systems for the ventilation of cooking equipment that is not within a dwelling unit and is used in processes producing grease-laden vapours shall be designed and installed in conformance with Articles 3.6.3.5 and 6.2.2.6. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.2.(3) | Hazardous Substances, Equipment and Processes | A fuel-fired appliance shall not be installed in a corridor serving as an access to exit. | obc2019_divb | Div B | 3.3.1.2.(3) | 3.3.1.2. Hazardous Substances, Equipment and Processes | A fuel-fired appliance shall not be installed in a corridor serving as an access to exit. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.20.(1) | Exhaust Ventilation and Explosion Venting | Except as provided in Sentence 3.3.1.20.(2), an exhaust ventilation system designed in conformance with the appropriate requirements of part 6. shall be provided in a building or part of a building in which dust, fumes, gases, vapour or other impurities or contaminants have the potential to create a fire or explosion hazard. (See also Article 4.2.4.13.) | obc2019_divb | Div B | 3.3.1.19.(1) | 3.3.1.19. Exhaust Ventilation and Explosion Venting | Except as provided in Sentence (2), an exhaust ventilation system designed in conformance with the appropriate requirements of Part 6 shall be provided in a building or part of a building in which dust, fumes, gases, vapour or other impurities or contaminants have the potential to create a fire or explosion hazard. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.20.(2) | Exhaust Ventilation and Explosion Venting | Where a fire separation required to have a fire-resistance rating is penetrated by a ventilation system required by Sentence 3.3.1.20.(1) for power-ventilated enclosures in laboratories, the ducts shall be (a) continuously enclosed from the first penetrated fire separation to any subsequent fire separations or concealed spaces and all the way through to the outdoors so that the highest fire-resistance rating of all the penetrated fire separations is maintained, and (b) exempted from the requirement to be equipped with a fire damper, smoke damper and fire/smoke damper as stated in Article 3.1.8.7. | obc2019_divb | Div B | 3.3.1.19.(3) | 3.3.1.19. Exhaust Ventilation and Explosion Venting | Ducts described in Sentence (2) need not be equipped with a fire damper, a smoke damper or a combination smoke and fire damper. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.20.(2) | Exhaust Ventilation and Explosion Venting | Where a fire separation required to have a fire-resistance rating is penetrated by a ventilation system required by Sentence 3.3.1.20.(1) for power-ventilated enclosures in laboratories, the ducts shall be (a) continuously enclosed from the first penetrated fire separation to any subsequent fire separations or concealed spaces and all the way through to the outdoors so that the highest fire-resistance rating of all the penetrated fire separations is maintained, and (b) exempted from the requirement to be equipped with a fire damper, smoke damper and fire/smoke damper as stated in Article 3.1.8.7. | obc2019_divb | Div B | 3.3.1.19.(2) | 3.3.1.19. Exhaust Ventilation and Explosion Venting | Where a fire separation required to have a fire-resistance rating is penetrated by a ventilation system required by Sentence (1) for power-ventilated enclosures in laboratories, the ducts shall be continuously enclosed from the first penetrated fire separation to any subsequent fire separations or concealed spaces and to the outdoors so that the highest fire-resistance rating of all the penetrated fire separations is maintained. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.20.(3) | Exhaust Ventilation and Explosion Venting | Explosion relief devices, vents or other protective measures conforming to Subsection 6.3.1. and Article 6.9.1.2. shall be provided for a space in which substances or conditions that have the potential to create an explosion hazard are present as a result of the principal use of a building. | obc2019_divb | Div B | 3.3.1.19.(4) | 3.3.1.19. Exhaust Ventilation and Explosion Venting | Explosion relief devices, vents or other protective measures conforming to Subsection 6.2.2. shall be provided for a space in which substances or conditions that have the potential to create an explosion hazard are present as a result of the principal use of a building. |  | Common Sentence | Yes | Fire hazards
2015 | ON | NBC | Div B | 3.3.1.21.(1) | Janitorsâ€™ Rooms | Except as permitted by Sentences 3.3.1.21.(2) and 3.3.1.21.(3), a room or space within a floor area for the storage of janitorial supplies shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h. | obc2019_divb | Div B | 3.3.1.20.(1) | 3.3.1.20. Janitorsâ€™ Rooms | Except as permitted by Sentences (2) and (3), a room or space within a floor area for the storage of janitorial supplies shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.21.(2) | Separation of Suites | The fire-resistance rating of the fire separation required by Sentence 3.3.1.1.(1) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by part 3. is permitted to be less than 1 h for the floor assembly above the floor area, or the floor assembly below the floor area, if there is no floor assembly above. | obc2019_divb | Div B | 3.3.1.20.(2) | 3.3.1.20. Janitorsâ€™ Rooms | The fire-resistance rating of the fire separation required by Sentence (1) is permitted to be not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for, the floor assembly above the floor area, or the floor assembly below the floor area, if there is no floor assembly above. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.21.(3) | Janitors Rooms | The fire separation required by Sentence 3.3.1.21.(1) is not required to have a fire-resistance rating if the floor area in which the room or space is located is sprinklered throughout. | obc2019_divb | Div B | 3.3.1.20.(3) | 3.3.1.20. Janitors Rooms | The fire separation required by Sentence (1) is not required to have a fire-resistance rating if the floor area in which the room or space is located is sprinklered. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.22.(1) | Common Laundry Rooms | Except as permitted by Sentences 3.3.1.22.(2) and 3.3.1.22.(3), in a building of residential occupancy, a laundry room in a floor area that is not within a dwelling unit shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h. | obc2019_divb | Div B | 3.3.1.21.(1) | 3.3.1.21. Common Laundry Rooms | Except as permitted by Sentences (2) and (3), in a building of residential occupancy, a laundry room in a floor area that is not within a dwelling unit shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.22.(2) | Common Laundry Rooms | The fire-resistance rating of the fire separation required by Sentence 3.3.1.1.(1) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by part 3. is permitted to be less than 1 h for (a) the floor assembly above the floor area, or (b) the floor assembly below the floor area, if there is no floor assembly above. | obc2019_divb | Div B | 3.3.1.21.(2) | 3.3.1.21. Common Laundry Rooms | The fire-resistance rating of the fire separation required by Sentence (1) is permitted to be not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for, the floor assembly above the floor area, or the floor assembly below the floor area, if there is no floor assembly above. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.22.(3) | Common Laundry Rooms | The fire separation required by Sentence 3.3.1.22.(1) is not required to have a fire-resistance rating if the floor area in which the laundry room is located is sprinklered throughout. | obc2019_divb | Div B | 3.3.1.21.(3) | 3.3.1.21. Common Laundry Rooms | The fire separation required by Sentence (1) is not required to have a fire-resistance rating if the floor area in which the laundry room is located is sprinklered. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.23.(1) | Obstructions | No obstruction shall be permitted in any occupancy that would restrict the width of a normal means of egress from any part of a floor area to less than 750 mm unless an alternative means of egress is provided adjacent to, accessible from, and plainly visible from the obstructed means of egress. (See Note A-3.3.1.23.(1).) | obc2019_divb | Div B | 3.3.1.22.(1) | 3.3.1.22. Obstructions | No obstruction shall be permitted in any occupancy that would restrict the width of a normal means of egress from any part of a floor area to less than 750 mm unless an unobstructed alternative means of egress is provided adjacent to, accessible from, and plainly visible from the obstructed means of egress. (See Appendix A.) |  | Common Sentence | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.3.1.24.(1) | Signs in Service Spaces | Illuminated signs conforming to Sentences 3.4.5.1.(2) and 3.4.5.1.(6) shall be provided to indicate the direction to egress points in a service space referred to in Sentence 3.2.1.1.(8). | obc2019_divb | Div B | 3.3.1.23.(1) | 3.3.1.23. Signs in Service Spaces | Illuminated signs conforming to Sentence 3.4.5.1.(2) or (7) shall be provided to indicate the direction to egress points in a service space referred to in Sentence 3.2.1.1.(9). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.25.(1) | Welding and Cutting | Except as provided in Sentence 3.3.1.25.(2), welding and cutting operations shall be carried out in a room separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h, or protected by an automatic fire extinguishing system. | obc2019_divb | Div B | 3.3.1.24.(1) | 3.3.1.24. Welding and Cutting | Except as provided in Sentence (2), welding and cutting operations shall be located in a room, separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h, or protected by an automatic fire extinguishing system. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.25.(2) | Welding and Cutting | Sentence 3.3.1.25.(1) shall not apply to industrial occupancies where the welding and cutting operations do not present a fire or explosion hazard to adjacent areas. | obc2019_divb | Div B | 3.3.1.24.(2) | 3.3.1.24. Welding and Cutting | Sentence (1) does not apply to an industrial occupancy where the welding and cutting operations do not present a fire or explosion hazard to adjacent areas. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.3.(1) | Means of Egress | Access to exit within floor areas shall conform to Subsections 3.3.2. to 3.3.5.,in addition to the requirements of this Subsection. | obc2019_divb | Div B | 3.3.1.3.(1) | 3.3.1.3. Means of Egress | Access to exit within floor areas shall conform to Subsections 3.3.2. to 3.3.6., in addition to the requirements of this Subsection. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.3.(2) | Means of Egress | If a podium, terrace, platform or contained open space is provided, egress requirements shall conform to the appropriate requirements of Sentence 3.3.1.5.(1) for rooms and suites. | obc2019_divb | Div B | 3.3.1.3.(2) | 3.3.1.3. Means of Egress | If a podium, terrace, platform or contained open space is provided, egress requirements shall conform to the appropriate requirements of Sentence 3.3.1.5.(1) for rooms and suites. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.3.(3) | Means of Egress | Means of egress shall be provided from every roof which is intended for occupancy, and from every podium, terrace, platform or contained open space. | obc2019_divb | Div B | 3.3.1.3.(3) | 3.3.1.3. Means of Egress | Means of egress shall be provided from every roof that is intended for occupancy, and from every podium, terrace, platform or contained open space. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.3.(4) | Means of Egress | At least two separate means of egress shall be provided from a roof, used or intended for an occupant load more than 60, to stairs designed in conformance with the requirements regarding exit stairs stated in Section 3.4. | obc2019_divb | Div B | 3.3.1.3.(4) | 3.3.1.3. Means of Egress | At least two separate means of egress shall be provided from a roof, used or intended for an occupant load more than 60, to stairs designed in conformance with the exit stair requirements of Section 3.4. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.3.(5) | Means of Egress | A rooftop enclosure shall be provided with an access to exit that leads to an exit at the roof level, or on the storey immediately below the roof. | obc2019_divb | Div B | 3.3.1.3.(5) | 3.3.1.3. Means of Egress | A rooftop enclosure shall be provided with an access to exit that leads to an exit, at the roof level, or on the storey immediately below the roof. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.3.(6) | Means of Egress | A rooftop enclosure which is more than 200 m2 in area shall be provided with at least 2 means of egress. | obc2019_divb | Div B | 3.3.1.3.(6) | 3.3.1.3. Means of Egress | A rooftop enclosure that is more than 200 m2 in area shall be provided with at least two means of egress. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.3.(7) | Means of Egress | Two points of egress shall be provided for a service space referred to in Sentence 3.2.1.1.(8) if (a) the area is more than 200 m2 , or (b) the travel distance measured from any point in the service space to a point of egress is more than 25 m. | obc2019_divb | Div B | 3.3.1.3.(7) | 3.3.1.3. Means of Egress | Two points of egress shall be provided for a service space referred to in Sentence 3.2.1.1.(9) if, (a) the area is more than 200 m2, or (b) the travel distance measured from any point in the service space to a point of egress is more than 25 m. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.3.(8) | Means of Egress | Except as permitted by Sentences 3.3.4.4.(5) and 3.3.4.4.(6), each suite in a floor area that contains more than one suite shall have (a) an exterior exit doorway, or (b) a doorway (i) into a public corridor, or (ii) to an exterior passageway. | obc2019_divb | Div B | 3.3.1.3.(8) | 3.3.1.3. Means of Egress | Except as required by Sentence 3.3.4.4.(8) and permitted by Sentences 3.3.4.4.(5) and (6), each suite in a floor area that contains more than one suite shall have, (a) an exterior exit doorway, or (b) a doorway, (i) into a public corridor, or (ii) to an exterior passageway. |  | Common Sentence | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.3.1.3.(9) | Means of Egress | Except as permitted by this Section and by Sentence 3.4.2.1.(2), at the point where a doorway referred to in Sentence (8) opens onto a public corridor or exterior passageway, it shall be possible to go in opposite directions to each of 2 separate exits. | obc2019_divb | Div B | 3.3.1.3.(9) | 3.3.1.3. Means of Egress | Except as permitted by this Section and by Sentence 3.4.2.1.(2), at the point where a doorway referred to in Sentence (8) opens onto a public corridor or exterior passageway, it shall be possible to go in opposite directions to each of two separate exits. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.4.(1) | Public Corridor Separations | Except as otherwise required by this Part or as permitted by Sentence (4), a public corridor shall be separated from the remainder of the storey by a fire separation. | obc2019_divb | Div B | 3.3.1.4.(1) | 3.3.1.4. Public Corridor Separations | Except as otherwise required by this Part or as permitted by Sentence (4), a public corridor shall be separated from the remainder of the storey by a fire separation. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.4.(2) | Public Corridor Separations | Except as permitted by Sentence (3) and Clauses (4)(a) and (4)(b), the fire separation between a public corridor and the remainder of the storey shall have a fire-resistance rating not less than 45 min. | obc2019_divb | Div B | 3.3.1.4.(2) | 3.3.1.4. Public Corridor Separations | Except as permitted by Sentence (3) and Clauses (4)(a) and (b), the fire separation between a public corridor and the remainder of the storey shall have a fire-resistance rating not less than 45 min. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.4.(3) | Public Corridor Separations | If a storey is sprinklered throughout, no fire-resistance rating is required for a fire separation between a public corridor and the remainder of the storey, provided the corridor does not serve a care, treatment or detention occupancy or a residential occupancy. (See Note A-3.1.8.1.(1)(b).) | obc2019_divb | Div B | 3.3.1.4.(3) | 3.3.1.4. Public Corridor Separations | If a storey is sprinklered, no fire-resistance rating is required for a fire separation between a public corridor and the remainder of the storey provided the corridor does not serve a care, care and treatment, detention or residential occupancy. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.4.(4) | Public Corridor Separations | No fire separation is required in a sprinklered floor area between a public corridor and (a) except as required by Sentences 3.3.3.5.(8) and 3.3.4.2.(1), and notwithstanding Sentence 3.4.2.4.(2), the remainder of a storey, provided the travel distance from any part of the floor area to an exit is not more than 45 m, (b) a room or a suite, provided the public corridor complies with Sentence 3.3.1.9.(6) and Sentence 3.4.2.5.(1), or (c) a space containing plumbing fixtures required by Subsection 3.7.2., provided the space and the public corridor are separated from the remainder of the storey by a fire separation having a fire-resistance rating not less than that required between the public corridor and the remainder of the storey. | obc2019_divb | Div B | 3.3.1.4.(4) | 3.3.1.4. Public Corridor Separations | No fire separation is required in a sprinklered floor area between a public corridor and, (a) except as required by Sentences 3.3.3.5.(9) and 3.3.4.2.(1) and notwithstanding Sentences 3.4.2.4.(2), the remainder of a storey provided the travel distance from any part of the floor area to an exit is not more than 45 m., (b) a room or suite provided the public corridor complies with Sentence 3.3.1.9.(6) and Clause 3.4.2.5.(1)(d), or (c) a space containing plumbing fixtures required by Subsection 3.7.4. provided the space and the public corridor are separated from the remainder of the storey by a fire separation that has a fire-resistance rating not less than that required between the public corridor and the remainder of the storey. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.5.(1) | Egress Doorways | Except for dwelling units, a minimum of 2 egress doorways located so that one doorway could provide egress from the room or suite as required by Article 3.3.1.3. if the other doorway becomes inaccessible to the occupants due to a fire which originates in the room or suite, shall be provided for every room and every suite (a) that is used for a high-hazard industrial occupancy and whose area is more than 15 m2 , (b) intended for an occupant load more than 60, (c) in a floor area that is not sprinklered throughout, and (i) the area of a room or suite is more than the value in Table 3.3.1.5.-A, or (ii) the travel distance within the room or suite to the nearest egress doorway is more than the value in Table 3.3.1.5.-A, or (d) in a floor area that is sprinklered throughout and does not contain a high-hazard industrial occupancy and (i) the travel distance to an egress doorway is more than 25 m, or (ii) the area of the room or suite is more than the value in Table 3.3.1.5.-B. | obc2019_divb | Div B | 3.3.1.5.(1) | 3.3.1.5. Egress Doorways | Except for dwelling units, a minimum of two egress doorways located so that one doorway could provide egress from the room or suite as required by Article 3.3.1.3. if the other doorway becomes inaccessible to the occupants due to a fire that originates in the room or suite, shall be provided for every room and every suite, (a) whose area is more than 15 m2 and is used for, (i) a high hazard industrial occupancy, or (ii) a hazardous room, (b) intended for an occupant load more than 60, (c) in a floor area that is not sprinklered if, (i) the area of a room or suite is more than the value in Table 3.3.1.5.A., or (ii) the travel distance within the room or suite to the nearest egress doorway, is more than the value in Table 3.3.1.5.A., (d) in a floor area that is sprinklered and does not contain a high hazard industrial occupancy if, (i) the travel distance to an egress doorway is more than 25 m, or (ii) the area of the room or suite is more than the value in Table 3.3.1.5.B., or (e) where the area of the room is more than 100 m2 and it is a hazardous classroom in elementary or secondary school. |  | Common Sentence | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.3.1.5.(2) | Egress Doorways | Where 2 egress doorways are required by Sentence 3.3.1.5.(1), they shall be placed at a distance from one another equal to or greater than one third of the maximum overall diagonal dimension of the area to be served, measured as the shortest distance that smoke would have to travel between the nearest required egress doors. | obc2019_divb | Div B | 3.3.1.5.(2) | 3.3.1.5. Egress Doorways | Where two egress doorways are required by Sentence (1), they shall be placed at a distance from one another equal to or greater than one-third of the maximum overall diagonal dimension of the room or suite to be served, measured as the shortest distance that smoke would have to travel between the nearest required egress doors. |  | Common Sentence | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.3.1.6.(1) | Travel Distance | If more than one egress doorway is required from a room or suite referred to in Article 3.3.1.5., the travel distance within the room or suite to the nearest egress doorway shall not exceed the maximum travel distances specified in Clauses 3.4.2.5.(1) , 3.4.2.5.(1) , 3.4.2.5.(1) and 3.4.2.5.(1) for exits. | obc2019_divb | Div B | 3.3.1.6.(1) | 3.3.1.6. Travel Distance | If more than one egress doorway is required from a room or suite referred to in Article 3.3.1.5., the travel distance within the room or suite to the nearest egress doorway shall not exceed the maximum travel distances specified in Clauses 3.4.2.5.(1)(a), (b), (c) and (f) for exits. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.7.(1) | Protection on Floor Areas with a Barrier-Free Path of Travel | Every floor area above or below the first storey that is not sprinklered throughout and that has a barrier-free path of travel shall (a) be served by an elevator (i) conforming to Sentences 3.2.6.5.(4) to (6), (ii) protected against fire in conformance with Clauses 3.2.6.5.(3)(b) or (c), and (iii) in a building over 3 storeys in building height, protected against smoke movement so that the hoistway will not contain more than 1% by volume of contaminated air from a fire floor during a period of 2 h after the start of a fire, assuming an outdoor temperature equal to the January design temperature on a 2.5% basis determined in conformance with Subsection 1.1.3., b) be divided into at least 2 zones by fire separations conforming to Sentences (2), (3) and 3.1.8.5.(6) so that (see Note A-3.3.1.7.(1)(b)) (i) persons with physical disabilities can be accommodated in each zone, and (ii) the travel distance from any point in one zone to a doorway leading to another zone shall be not more than the value for travel distance permitted by Sentence 3.4.2.5.(1) for the occupancy classification of the zone, (c) in the case of residential occupancies, be provided with balconies conforming to Sentence (4), except on the storey containing the barrier-free entrance required by Article 3.8.2.2., (d) have an exterior exit at ground level, or (e) have a ramp leading to ground level. (See Note A-3.3.1.7.(1).) | obc2019_divb | Div B | 3.3.1.7.(2) | 3.3.1.7. Protection on Floor Areas with a Barrier-Free Path | In residential occupancies, the requirements of Sentence (1) are waived if a balcony conforming to Sentence (7) is provided for each suite, except for suites on the storey containing the barrier-free entrance described in Article 3.8.1.2. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.7.(1) | Protection on Floor Areas with a Barrier-Free Path of Travel | Every floor area above or below the first storey that is not sprinklered throughout and that has a barrier-free path of travel shall (a) be served by an elevator (i) conforming to Sentences 3.2.6.5.(4) to (6), (ii) protected against fire in conformance with Clauses 3.2.6.5.(3)(b) or (c), and (iii) in a building over 3 storeys in building height, protected against smoke movement so that the hoistway will not contain more than 1% by volume of contaminated air from a fire floor during a period of 2 h after the start of a fire, assuming an outdoor temperature equal to the January design temperature on a 2.5% basis determined in conformance with Subsection 1.1.3., b) be divided into at least 2 zones by fire separations conforming to Sentences (2), (3) and 3.1.8.5.(6) so that (see Note A-3.3.1.7.(1)(b)) (i) persons with physical disabilities can be accommodated in each zone, and (ii) the travel distance from any point in one zone to a doorway leading to another zone shall be not more than the value for travel distance permitted by Sentence 3.4.2.5.(1) for the occupancy classification of the zone, (c) in the case of residential occupancies, be provided with balconies conforming to Sentence (4), except on the storey containing the barrier-free entrance required by Article 3.8.2.2., (d) have an exterior exit at ground level, or (e) have a ramp leading to ground level. (See Note A-3.3.1.7.(1).) | obc2019_divb | Div B | 3.3.1.7.(3) | 3.3.1.7. Protection on Floor Areas with a Barrier-Free Path | The requirements of Sentences (1) and (2) are waived when the building is sprinklered. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.7.(1) | Protection on Floor Areas with a Barrier-Free Path of Travel | Every floor area above or below the first storey that is not sprinklered throughout and that has a barrier-free path of travel shall (a) be served by an elevator (i) conforming to Sentences 3.2.6.5.(4) to 3.2.6.5.(6), (ii) protected against fire in conformance with Clauses 3.2.6.5.(3)(b) or (c), and (iii) in a building over 3 storeys in building height, protected against smoke movement so that the hoistway will not contain more than 1% by volume of contaminated air from a fire floor during a period of 2 h after the start of a fire, assuming an outdoor temperature equal to the January design temperature on a 2.5% basis determined in conformance with Subsection 1.1.3, (b) be divided into at least 2 zones by fire separations conforming to Sentences 3.3.1.7.(2) , 3.3.1.7.(3) and 3.1.8.5.(6) so that (see Note A-3.3.1.7.(1)(b)) (i) persons with physical disabilities can be accommodated in each zone, and (ii) the travel distance from any point in one zone to a doorway leading to another zone shall be not more than the value for travel distance permitted by Sentence 3.4.2.5.(1) for the occupancy classification of the zone, (c) in the case of residential occupancies, be provided with balconies conforming to Sentence 3.3.1.7.(4), except on the storey containing the barrier-free entrance required by Article 3.8.2.2., (d) have an exterior exit at ground level, or (e) have a ramp leading to ground level. | obc2019_divb | Div B | 3.3.1.7.(1) | 3.3.1.7. Protection on Floor Areas with a Barrier-Free Path | Except as provided in Sentences (2) and (3), every floor area above or below the first storey that has a barrier-free path of travel shall, (a) be served by an elevator, (i) conforming to Sentences 3.2.6.5.(4) to (6), (ii) protected against fire in conformance with Clause 3.2.6.5.(3)(b) or (c), and (iii) in a building over 3 storeys in building height, protected against smoke movement so that the hoistway will not contain more than 1% by volume of contaminated air from a fire floor during a period of 2 h after the start of a fire, assuming an outdoor temperature equal to the January design temperature on a 2.5% basis determined in conformance with MMAH Supplementary Standard SB-1, "Climatic and Seismic Data", or (b) be divided into at least two zones by fire separations conforming to Sentences (4) and (5) and 3.1.8.5.(6) so that, (See Appendix A.) (i) persons with physical disabilities can be accommodated in each zone, (ii) the travel distance from any point in one zone to a doorway leading to another zone shall be not more than the value for travel distance permitted by Sentence 3.4.2.5.(1) for the occupancy classification of the zone, and (iii) a barrier-free path of travel is provided to an exit. |  | Common Sentence | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B | 3.3.1.7.(2) | Protection on Floor Areas with a Barrier-Free Path of Travel | Except as permitted by Sentence (3), the fire separations referred to in Clause (1)(b) shall have a fire-resistance rating not less than 1 h. | obc2019_divb | Div B | 3.3.1.7.(4) | 3.3.1.7. Protection on Floor Areas with a Barrier-Free Path | Except as permitted by Sentence (5), the fire separations referred to in Clause (1)(b) shall have a fire-resistance rating not less than 1 h. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.7.(3) | Protection on Floor Areas with a Barrier-Free Path of Travel | The fire-resistance rating of the fire separations referred to in Clause (1)(b) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for (a) the floor assembly above the floor area, or (b) the floor assembly below the floor area, if there is no floor assembly above. | obc2019_divb | Div B | 3.3.1.7.(5) | 3.3.1.7. Protection on Floor Areas with a Barrier-Free Path | The fire-resistance rating of the fire separations referred to in Clause (1)(b) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for, the floor assembly above the floor area, or the floor assembly below the floor area, if there is no floor assembly above. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.7.(4) | Protection on Floor Areas with a Barrier-Free Path of Travel | A balcony required by Clause (1)(c) shall (a) have direct barrier-free access from the suite or floor area (b) be not less than 1.5 m deep from the outside face of the exterior wall to the inside edge of the balcony, and (c) provide not less than 1.5 m2 of balcony space for each non-ambulatory occupant and 0.5 m2 for each ambulatory occupant. | obc2019_divb | Div B | 3.3.1.7.(7) | 3.3.1.7. Protection on Floor Areas with a Barrier-Free Path | A balcony required by Sentence (2) shall, (a) be provided with a door way having a clear width of not less that 800 mm when the door is in the open position, (b) have no projection above the walking surface more than 13 mm, (c) be not less than 1.5 m deep from the outside face of the exterior wall to the inside edge of the balcony, and (d) provide not less than 0.5 m2 for each occupant of the suite. |  | Common Sentence | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B | 3.3.1.8.(1) | Headroom Clearance | Except within the floor area of a storage garage, the minimum headroom clearance in every access to exit shall conform to the requirements of Article 3.4.3.4. for exits. (See also Sentence 3.3.5.4.(5).) | obc2019_divb | Div B | 3.3.1.8.(1) | 3.3.1.8. Headroom Clearance | Except within the floor area of a storage garage, the minimum headroom clearance in every access to exit shall conform to the requirements of Article 3.4.3.5. for exits. |  | Common Sentence | No | Means of Egress
2015 | ON | NBC | Div B | 3.3.1.9.(1) | Corridors | The minimum width of a public corridor shall be 1?100 mm. | obc2019_divb | Div B | 3.3.1.9.(1) | 3.3.1.9. Corridors | The minimum width of a public corridor shall be 1 100 mm. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.9.(2) | Corridors | Except as required by Sentence 3.3.3.3.(3), the minimum unobstructed width of a corridor used by the public or a corridor serving classrooms or patients’ sleeping rooms shall be 1 100 mm. | obc2019_divb | Div B | 3.3.1.9.(2) | 3.3.1.9. Corridors | Except as required by Sentences 3.3.3.3.(2) and (3), the minimum unobstructed width shall be 1 100 mm for every, (a) corridor used by the public, (b) corridor serving classrooms, and (c) corridor in a Group B, Division 2 or 3 occupancy where the corridor (i) serves a service room, (ii) serves an administrative area, (iii) will not be used by non-ambulatory outpatients, or (iv) will not be used by non-ambulatory residents. |  | Common Sentence | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.3.1.9.(3) | Corridors | against smoke movement so that the hoistway will not | obc2019_divb | Div B | 3.3.1.9.(3) | 3.3.1.9. Corridors | Except as permitted by Sentence (4), obstructions located within 1 980 mm of the floor shall not project more than 100 mm horizontally in a manner that would create a hazard for a person with a visual disability traveling adjacent to the walls in, an exit passageway, a public corridor, a corridor used by the public, a corridor serving classrooms, or a corridor serving patientsÃ¢â‚¬â„¢ or residentsÃ¢â‚¬â„¢ sleeping rooms in a Group B, Division 2 or Division 3 occupancy. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.9.(4) | Corridors | The horizontal projection of an obstruction referred to in Sentence (3) is permitted to be more than 100 mm provided the clearance between the obstruction and the floor is less than 680 mm.(See Note A-3.3.1.9.(4).) | obc2019_divb | Div B | 3.3.1.9.(4) | 3.3.1.9. Corridors | The horizontal projection of an obstruction referred to in Sentence (3) is permitted to be more than 100 mm provided the clearance between the obstruction and the floor is less than 680 mm. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.9.(5) | Corridors | If a corridor contains an occupancy, the occupancy shall not reduce the unobstructed width of the corridor to less than its required width. | obc2019_divb | Div B | 3.3.1.9.(5) | 3.3.1.9. Corridors | If a corridor contains an occupancy, the occupancy shall not reduce the unobstructed width of the corridor to less than its required width. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.9.(6) | Corridors | If a public corridor conforming to Clause 3.4.2.5.(1)(d) contains an occupancy, (a) the occupancy shall be located so that for pedestrian travel there is an unobstructed width not less than 3 m at all times adjacent and parallel to all rooms and suites that front onto the public corridor, and (b) the combined area of all occupancies in the public corridor shall be not more than 15% of the area of the public corridor. | obc2019_divb | Div B | 3.3.1.9.(6) | 3.3.1.9. Corridors | If a public corridor conforming to Clause 3.4.2.5.(1)(d) contains an occupancy, the occupancy shall be located so that for pedestrian travel there is an unobstructed width not less than 3 m at all times adjacent and parallel to all rooms and suites that front onto the public corridor, and the combined area of all occupancies in the public corridor shall be not more than 15% of the area of the public corridor. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.1.9.(7) | Corridors | Except for a dead-end corridor that is entirely within a suite or as permitted by Sentences 3.3.3.3.(1) and 3.3.4.4.(6), a dead-end corridor is permitted provided it is not more than 6 m long. | obc2019_divb | Div B | 3.3.1.9.(11) | 3.3.1.9. Corridors | A dead end public corridor is permitted in a business and personal services occupancy where, the dead end corridor, serves an occupant load of not more than 30 persons, is not more than 9 m long, and is provided with doors having self-closing devices, or there is a second and separate egress doorway from each room or suite not leading into a dead end corridor. |  | Common Sentence | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.3.1.9.(7) | Corridors | Except for a dead-end corridor that is entirely within a suite or as permitted by Sentences 3.3.3.3.(1) and 3.3.4.4.(6), a dead-end corridor is permitted provided it is not more than 6 m long. | obc2019_divb | Div B | 3.3.1.9.(7) | 3.3.1.9. Corridors | Except as provided in Sentence 3.3.3.3.(1), a dead end corridor shall conform to Sentences (8) to (14). |  | Common Sentence | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.3.1.9.(7) | Corridors | Except for a dead-end corridor that is entirely within a suite or as permitted by Sentences 3.3.3.3.(1) and 3.3.4.4.(6), a dead-end corridor is permitted provided it is not more than 6 m long. | obc2019_divb | Div B | 3.3.1.9.(9) | 3.3.1.9. Corridors | Except as provided in Sentence 3.3.4.11.(10) and except for corridors served by a single exit as described in Sentence 3.3.4.4.(6), a dead end public corridor is permitted in a residential occupancy provided it is not more than 6 m long. |  | Common Sentence | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.3.2.1.(1) | Scope | This Subsection applies to assembly occupancies and to outdoor places of assembly. | obc2019_divb | Div B | 3.3.2.1.(1) | 3.3.2.1. Scope | This Subsection applies to assembly occupancies and to outdoor places of assembly. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.10.(1) | Handrails in Aisles with Steps | Handrails shall be provided in aisles with steps in conformance with Table 3.3.2.10. | obc2019_divb | Div B | 3.3.2.8.(1) | 3.3.2.8A. Handrails in Aisles with Steps (See Appendix A.) | Handrails shall be provided in aisles with steps in conformance with Table 3.3.2.8A. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.10.(2) | Handrails in Aisles with Steps | Handrails installed along aisle centre lines as required by Table 3.3.2.10. shall (a) comply with Sentences 3.4.6.5.(5) to 3.4.6.5.(7) and 3.4.6.5.(14), (b) have gaps not less than 560 mm and not more than 915 mm wide, measured horizontally, at intervals not exceeding five rows, (c) comply with Sentence 3.4.6.5.(11) at terminations and required gaps, and (d) have an intermediate rail located 305 mm below the principal handrail. | obc2019_divb | Div B | 3.3.2.8.(2) | 3.3.2.8A. Handrails in Aisles with Steps (See Appendix A.) | Handrails installed along aisle centre lines as required by Table 3.3.2.8A. shall, (a) comply with Sentences 3.4.6.5.(3) to (5), (7) and (12), (b) have gaps not less than 560 mm and not more than 915 mm wide, measured horizontally, at intervals not exceeding five rows of seats, (c) comply with Sentence 3.4.6.5.(11) at terminations and required gaps, and (d) have an intermediate rail located 305 mm below the principal handrail. |  | Common Sentence | Yes | Falling, Tripping, Slipping Protection
2015 | ON | NBC | Div B | 3.3.2.11.(1) | Outdoor Places of Assembly | A Group A, Division 4 occupancy and each tier or balcony that has a capacity of more than 1?000 persons shall have not less than 3 separate exits , or 4?000 persons shall have not less than 4 separate exits . | obc2019_divb | Div B | 3.3.2.9.(1) | 3.3.2.9. Outdoor Places of Assembly | A Group A, Division 4 occupancy and each tier or balcony that has a capacity of more than, 1 000 persons shall have no fewer than three separate exits, or 4 000 persons shall have no fewer than four separate exits. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.11.(2) | Outdoor Places of Assembly | In a Group A, Division 4 occupancy, every seat shall be located so that the travel distance is not more than 45 m measured along the path of travel from the seat to the ground, an exit, an opening to a passageway leading from the seating area, or a portal, a vomitory or any other opening through the seating deck structure. | obc2019_divb | Div B | 3.3.2.9.(2) | 3.3.2.8A. Handrails in Aisles with Steps (See Appendix A.) | Handrails installed along aisle centre lines as required by Table 3.3.2.8A. shall, comply with Sentences 3.4.6.5.(3) to (5), (7) and (12), have gaps not less than 560 mm and not more than 915 mm wide, measured horizontally, at intervals not exceeding five rows of seats, comply with Sentence 3.4.6.5.(11) at terminations and required gaps, and have an intermediate rail located 305 mm below the principal handrail. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.11.(5) | Outdoor Places of Assembly | Aisles in a Group A, Division 4 occupancy shall (a) be located so that there are not more than 20 seats between any seat and the nearest aisle, and (b) be not less than 1?200 mm wide, except that an aisle serving less than 60 persons is permitted to be 750 mm wide. | obc2019_divb | Div B | 3.3.2.9.(5) | 3.3.2.9. Outdoor Places of Assembly | Aisles in a Group A, Division 4 occupancy, (a) shall be located so that there are not more than 20 seats between any seat and the nearest aisle, and (b) shall be not less than 1 200 mm wide, except that an aisle serving less than 60 persons is permitted to be 750 mm wide. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.12.(2) | Bleachers | If the vertical distance between seating platforms in bleachers is more than 280 mm, an intermediate step shall be provided the full width of the aisle and proportioned to provide 2 equal risers between platforms. | obc2019_divb | Div B | 3.3.2.10.(2) | 3.3.2.10. Bleachers | If the vertical distance between seating platforms in bleachers is more than 280 mm, an intermediate step shall be provided the full width of the aisle and proportioned to provide two equal risers between platforms. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.12.(3) | Bleachers | If the vertical distance between seating platforms in bleachers is more than 450 mm, 2 intermediate steps shall be provided the full width of the aisle so that there are 3 equal risers between platforms. | obc2019_divb | Div B | 3.3.2.10.(3) | 3.3.2.10. Bleachers | If the vertical distance between seating platforms in bleachers is more than 450 mm, two intermediate steps shall be provided the full width of the aisle so that there are three equal risers between platforms. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.12.(4) | Bleachers | If the passageway between rows of seats is not a closed deck, footboards shall be provided so that the total width of the footboards shall be not less than three quarters of the centre-to-centre spacing between rows of seats, and the spacing between footboard members shall be not more than 25 mm. | obc2019_divb | Div B | 3.3.2.10.(4) | 3.3.2.9. Outdoor Places of Assembly | The capacity of a means of egress for a Group A, Division 4 occupancy shall conform to the requirements of Sentence 3.4.3.2.(3). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.12.(5) | Bleachers | Openings above footboards and below the seats in rows of bleacher seats shall be provided with intermediate construction so that there is no opening that would permit the passage of a sphere of more than 100 mm in diameter. | obc2019_divb | Div B | 3.3.2.10.(5) | 3.3.2.10. Bleachers | Openings above footboards and below the seats in rows of bleachers shall be of a size that will prevent the passage of a sphere having a diameter more than 100 mm. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.13.(1) | Libraries | Except as permitted by Sentence 3.3.2.13.(2), a library book storage room that is not normally accessible to the public shall be separated from the remainder of the building by a fire separation with a fire-resistance rating not less than 2 h if it is more than 250 m2 in area, or contains book stacks that are more than 10 m high, or penetrate more than one floor assembly. | obc2019_divb | Div B | 3.3.2.11.(1) | 3.3.2.11. Libraries | Except as permitted by Sentence (2), a library book storage room that is not normally accessible to the public shall be separated from the remainder of the building by a fire separation with a fire-resistance rating not less than 2 h if it, is more than 250 m2 in area, or contains book stacks that, are more than 10 m high, or penetrate more than one floor assembly. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.13.(1) | Libraries | Except as permitted by Sentence 3.3.2.13.(2), a library book storage room that is not normally accessible to the public shall be separated from the remainder of the building by a fire separation with a fire-resistance rating not less than 2 h if it is more than 250 m2 in area, or contains book stacks that are more than 10 m high, or penetrate more than one floor assembly. | obc2019_divb | Div B | 3.3.2.10.(1) | 3.3.2.9. Outdoor Places of Assembly | A Group A, Division 4 occupancy and each tier or balcony that has a capacity of more than, 1 000 persons shall have no fewer than three separate exits, or 4 000 persons shall have no fewer than four separate exits. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.13.(2) | Libraries | The fire separation required by Sentence 3.3.2.13.(1) is not required if the book storage room is sprinklered. | obc2019_divb | Div B | 3.3.2.11.(2) | 3.3.2.11. Libraries | The fire separation required by Sentence (1) is not required if the book storage room is sprinklered. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.13.(3) | Libraries | Open book shelves are permitted above and below a mezzanine floor in a library building provided the height of the shelves is not more than 2.1 m but not more than 75% of the floor-to-ceiling height of the space above or below the mezzanine floor assembly. | obc2019_divb | Div B | 3.3.2.11.(3) | 3.3.2.10. Bleachers | If the vertical distance between seating platforms in bleachers is more than 450 mm, two intermediate steps shall be provided the full width of the aisle so that there are three equal risers between platforms. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.14.(1) | Stages for Theatrical Performances | A stage for theatrical performances and ancillary spaces, including workshops, dressing rooms and storage areas, shall be sprinklered. | obc2019_divb | Div B | 3.3.2.12.(1) | 3.3.2.11. Libraries | Except as permitted by Sentence (2), a library book storage room that is not normally accessible to the public shall be separated from the remainder of the building by a fire separation with a fire-resistance rating not less than 2 h if it, is more than 250 m2 in area, or contains book stacks that, are more than 10 m high, or penetrate more than one floor assembly. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.14.(2) | Stages for Theatrical Performances | A fire separation with a fire-resistance rating not less than 1 h shall be provided between a stage for theatrical performances and ancillary spaces, including workshops, dressing rooms and storage areas. | obc2019_divb | Div B | 3.3.2.12.(2) | 3.3.2.11. Libraries | The fire separation required by Sentence (1) is not required if the book storage room is sprinklered. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.14.(3) | Stages for Theatrical Performances | Except as permitted by Sentence 3.3.2.14.(6), a stage for theatrical performances and ancillary spaces, including workshops, dressing rooms and storage areas, shall be separated from the seating area by a fire separation having a fire-resistance rating not less than 1 h, except for a proscenium opening protected with a sprinkler deluge system conforming to the requirements of NFPA 13-2013 Installation of Sprinkler Systems an unframed fire curtain if the opening is not more than 20 m wide, or a semi-rigid fire curtain if the opening is more than 20 m wide. | obc2019_divb | Div B | 3.3.2.12.(3) | 3.3.2.12. Stages for Theatrical Performances | Except as permitted by Sentence (6), a stage for theatrical performances and ancillary spaces, including workshops, dressing rooms and storage areas, shall be separated from the seating area by a fire separation having a fire-resistance rating not less than 1 h, except for a proscenium opening protected with, a sprinkler deluge system conforming to the requirements of NFPA 13 "Installation of Sprinkler Systems", an unframed fire curtain if the opening is not more than 20 m wide, or a semi-rigid fire curtain if the opening is more than 20 m wide. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.14.(4) | Stages for Theatrical Performances | A fire curtain required by Sentence 3.3.2.14.(3) shall be of a type acceptable to the authority having jurisdiction and designed to close (a) automatically upon the actuation of the sprinkler system, (b) automatically upon actuation of the fire alarm system, and (c) manually by remote control devices located at the curtain control panel and at each side of the stage. | obc2019_divb | Div B | 3.3.2.12.(4) | 3.3.2.12. Stages for Theatrical Performances | A fire curtain required by Sentence (3) shall be of a type designed to close, (a) automatically upon the actuation of the sprinkler system, (b) automatically upon actuation of the fire alarm system, (c) manually by remote control devices located at the curtain control panel and at each side of the stage, and (d) automatically by heat-actuated devices. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.3.2.14.(5) | Stages for Theatrical Performances | At least 2 vents for the purpose of venting fire and smoke to the outside of a building shall be provided above a stage designed for theatrical performances and shall (a) have an aggregate area not less than one eighth of the area of the stage behind the proscenium opening, and (b) be arranged to open automatically upon actuation of the sprinkler system. | obc2019_divb | Div B | 3.3.2.12.(5) | 3.3.2.12. Stages for Theatrical Performances | At least two vents for the purpose of venting fire and smoke to the outside of a building shall be provided above a stage designed for theatrical performances and shall, (a) have an aggregate area not less than one-eighth of the area of the stage behind the proscenium opening, and (b) be arranged to open automatically upon actuation of the sprinkler system. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.14.(6) | Stages for Theatrical Performances | The fire separation referred to in Sentence 3.3.2.14.(3) is not required between a stage and a seating area in a building that is sprinklered throughout, provided a sprinkler deluge system is installed at the boundary between the stage and the seating area. | obc2019_divb | Div B | 3.3.2.12.(6) | 3.3.2.12. Stages for Theatrical Performances | The fire separation referred to in Sentence (3) is not required between a stage and a seating area in a floor area that is sprinklered, provided a sprinkler deluge system is installed at the boundary between the stage and the seating area. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.15.(1) | Risers for Stairs | In a Group A, Division 2 occupancy used for the serving of food and beverages, an interior flight of stairs with fewer than 3 risers is permitted provided it (a) is not less than 900 mm wide, (b) is illuminated at all times that occupants are on the premises, and (c) has a handrail on each side. | obc2019_divb | Div B | 3.3.2.13.(1) | 3.3.2.13. Risers for Stairs | In a Group A, Division 2 occupancy used for the serving of food and beverages, an interior flight with fewer than three risers is permitted provided it, (a) is not less than 900 mm wide, (b) is illuminated at all times that occupants are on the premises, and (c) has a handrail on each side. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.16.(1) | Storage Rooms | Where storage rooms are required by Part 4 of Division B of the NFC for the storage of flammable liquids or combustible liquids in assembly occupancies, such rooms shall not be located above or below the first storey. | obc2019_divb | Div B | 3.3.2.14.(1) | 3.3.2.14 Storage Rooms | A room intended for the storage of flammable liquids or combustible liquids required by the Fire Code made under the Fire Protection and Prevention Act, 1997 shall not be located above or below the first storey of the building. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.2.(1) | Fire Separations | Except as permitted by Sentence 3.3.2.2.(2), the seating area of a Group A, Division 1 occupancy shall be separated from adjacent occupancies in the floor area by a fire separation having a fire-resistance rating not less than 1 h if the occupant load in the seating area exceeds 200. | obc2019_divb | Div B | 3.3.2.2.(1) | 3.3.2.2. Fire Separations | Except as permitted by Sentence (2), the seating area of a Group A, Division 1 occupancy shall be separated from adjacent occupancies in the floor area by a fire separation having a fire-resistance rating not less than 1 h if the occupant load in the seating area exceeds 200. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.2.(2) | Fire Separations | The fire-resistance rating of the fire separation required by Sentence 3.3.2.2.(1) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by part 3. is permitted to be less than 1 h for the floor assembly above the floor area, or the floor assembly below the floor area, if there is no floor assembly above. | obc2019_divb | Div B | 3.3.2.2.(2) | 3.3.2.2. Fire Separations | The fire-resistance rating of the fire separation required by Sentence (1) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for, the floor assembly above the floor area, or the floor assembly below the floor area, if there is no floor assembly above. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.2.(2) | Fire Separations | The fire-resistance rating of the fire separation required by Sentence 3.3.2.2.(1) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by part 3. is permitted to be less than 1 h for the floor assembly above the floor area, or the floor assembly below the floor area, if there is no floor assembly above. | obc2019_divb | Div B | 3.3.2.5.(2) | 3.3.2.5. Corridors | The fire-resistance rating of the fire separation required by Sentence (1) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for, the floor assembly above the floor area, or the floor assembly below the floor area, if there is no floor assembly above. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.2.(3) | Fire Separations | If usable space exists under tiers of seats in arena-type buildings, a fire separation with a fire-resistance rating not less than 45 min shall be provided between the space and the seats or the space shall be sprinklered. | obc2019_divb | Div B | 3.3.2.2.(3) | 3.3.2.2. Fire Separations | If usable space exists under tiers of seats in arena type buildings, a fire separation with a fire-resistance rating not less than 45 min shall be provided between the space and the seats or the space shall be sprinklered. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.4.(1) | Fixed Seats | Except for the requirements of Article 3.3.2.8. for bench-type seats and except as required or permitted by Sentence 3.3.2.4.(2) and Articles 3.3.2.11. and 3.3.2.12., fixed seats in places of assembly shall be attached or secured to the floor, platform or platform riser, provided with arms and back, and arranged in rows having an unobstructed passage not less than 400 mm wide measured horizontally between plumb lines from the backs of the seats in one row and the edges of the furthest forward projection of the seats in the next row in the unoccupied position. | obc2019_divb | Div B | 3.3.2.3.(1) | 3.3.2.3. Fixed Seats | Except for the requirements of Article 3.3.2.7. for bench-type seats and except as required or permitted by Sentence (2) and Articles 3.3.2.9. and 3.3.2.10., fixed seats in places of assembly shall be, attached or secured to the floor, platform or platform riser, provided with arms and back, and arranged in rows having an unobstructed passage not less than 400 mm wide measured horizontally between plumb lines from the backs of the seats in one row and the edges of the furthest forward projection of the seats in the next row in the unoccupied position. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.4.(2) | Fixed Seats | For fixed seats with backs and with folding tablet arms, the value of 400 mm required by Sentence 3.3.2.4.(1) shall be measured when the tablet arms are in the use position, but is permitted to be measured in the stored position provided there are not more than 7 seats between any seat and the nearest aisle, the seats are located in a lecture hall or an auditorium used for instructional purposes, and the tablet arm, when raised manually to a vertical position, falls by the force of gravity to the stored position. | obc2019_divb | Div B | 3.3.2.3.(2) | 3.3.2.3. Fixed Seats | For fixed seats with backs and with folding tablet arms, the value of 400 mm required by Clause (1)(c) shall be measured when the tablet arms are in the use position, but is permitted to be measured in the stored position provided, there are not more than seven seats between any seat and the nearest aisle, the seats are located in a lecture hall or an auditorium used for instructional purposes, and the tablet arm, when raised manually to a vertical position, falls by the force of gravity to the stored position. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.4.(3) | Fixed Seats | Except as permitted by Sentence 3.3.2.4.(4), aisles shall be located so that there are not more than 7 seats with backs or 20 seats without backs between any seat and the nearest aisle. | obc2019_divb | Div B | 3.3.2.3.(3) | 3.3.2.3. Fixed Seats | Except as permitted by Sentences (4) and (5), aisles shall be located so that there are not more than seven seats with backs or 20 seats without backs between any seat and the nearest aisle. |  | Common Sentence | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.3.2.4.(4) | Fixed Seats | The requirements of Sentence 3.3.2.4.(3) do not apply if egress doorways are provided to serve both ends of rows of seats, each doorway referred to in Sentence 3.3.2.4.(4) serves not more than 3 rows of seats, and each row contains not more than 100 seats. | obc2019_divb | Div B | 3.3.2.3.(4) | 3.3.2.3. Fixed Seats | The requirements of Sentence (3) do not apply if, egress doorways are provided to serve both ends of rows of seats, each doorway referred to in Clause (a) serves not more than three rows of seats, and each row contains not more than 100 seats. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.5.(1) | Aisles | Except as required by Articles 3.3.2.11. and 3.3.2.12., aisles leading to exits shall be provided in conformance with Sentences 3.3.2.5.(2) to 3.3.2.5.(17) in places of assembly which contain fixed seats. | obc2019_divb | Div B | 3.3.2.4.(1) | 3.3.2.4. Aisles | Except as required by Articles, 3.3.2.9. and 3.3.2.10., aisles leading to egress doors or exits shall be provided in conformance with Sentences (2) to (27) in places of assembly that contain fixed seats. |  | Common Sentence | Yes | Assembly Seating
2015 | ON | NBC | Div B | 3.3.2.5.(10) | Aisles | The passageway between rows of seats served by a stepped aisle shall be level at right angles to the line of travel. | obc2019_divb | Div B | 3.3.2.4.(20) | 3.3.2.4. Aisles | The passageway between rows of seats served by a stepped aisle shall be level at right angles to the line of travel. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.5.(11) | Aisles | The riser of a step in an aisle shall be not less than 110 mm high, and not more than 200 mm high. | obc2019_divb | Div B | 3.3.2.4.(21) | 3.3.2.4. Aisles | The riser of a step in an aisle shall be, not less than 110 mm high, and not more than 200 mm high. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.5.(12) | Aisles | Variations are permitted in riser height provided the height of adjacent risers does not vary by more than 6 mm, and the width of a tread or a platform in the direction of travel is not less than 430 mm. | obc2019_divb | Div B | 3.3.2.4.(22) | 3.3.2.4. Aisles | Variations are permitted in riser height provided, the height of adjacent risers does not vary by more than 6 mm, and the depth of a tread or a platform in the direction of travel is not less than 430 mm. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.5.(13) | Aisles | Steps in an aisle shall have a run not less than 230 mm exclusive of nosings, have a tread width not less than 250 mm, extend to the adjacent rows of seats in a manner that will not create a hazard from tripping, and have a finish on the treads conforming to Sentence 3.4.6.1.(1). | obc2019_divb | Div B | 3.3.2.4.(23) | 3.3.2.4. Aisles | Steps in an aisle shall, have a run not less than 230 mm exclusive of nosings, have a tread depth not less than 250 mm, extend to the adjacent rows of seats in a manner that will not create a hazard from tripping, and have a finish on the treads conforming to Sentence 3.4.6.1.(1). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.5.(14) | Aisles | The location of every riser in an aisle shall be made apparent from both directions of travel by strategically placed lighting or contrasting marking stripes. | obc2019_divb | Div B | 3.3.2.4.(24) | 3.3.2.4. Aisles | The location of every riser in an aisle shall be made apparent from both directions of travel by strategically placed lighting or contrasting marking stripes. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.5.(15) | Aisles | A platform in an aisle shall be level, except that a slope not more than 1 in 50 is permitted for a platform that is not less than 430 mm wide in the direction of exit travel. | obc2019_divb | Div B | 3.3.2.4.(25) | 3.3.2.4. Aisles | A platform in an aisle shall be level, except that a slope not more than 1 in 50 is permitted for a platform that is not less than 430 mm deep in the direction of exit travel. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.5.(16) | Aisles | If a step is used at the entry to a row of seats from a stepped aisle, an unobstructed platform not less than 800 mm square shall be provided adjacent to the aisle. | obc2019_divb | Div B | 3.3.2.4.(26) | 3.3.2.4. Aisles | If a step is used at the entry to a row of seats from a stepped aisle, an unobstructed platform not less than 800 mm square shall be provided adjacent to the aisle. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.5.(17) | Aisles | The finish of the surface of a platform in or adjacent to a stepped aisle shall conform to Sentence 3.4.6.1.(1). | obc2019_divb | Div B | 3.3.2.4.(27) | 3.3.2.4. Aisles | The finish of the surface of a platform in or adjacent to a stepped aisle shall conform to Sentence 3.4.6.1.(1). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.5.(2) | Aisles | The minimum clear width of aisles shall be not less than 1?100 mm, except that the width is permitted to be reduced to not less than 750 mm if serving not more than 60 seats, and 900 mm if serving seats on one side only. | obc2019_divb | Div B | 3.3.2.4.(5) | 3.3.2.4. Aisles | The minimum clear width of aisles shall be not less than 1 100 mm , except that the width is permitted to be reduced to not less than, 750 mm if serving not more than 60 seats, and 900 mm if serving seats on one side only. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.5.(3) | Aisles | Except in the case of bleacher seats, the minimum clear width of aisles referred to in Sentence 3.3.2.5.(2) shall be measured at the point farthest from an exit, cross aisle or foyer and shall be increased by 25 mm for each metre of distance toward the exit, cross aisle or foyer. | obc2019_divb | Div B | 3.3.2.4.(7) | 3.3.2.4. Aisles | Except for an aisle serving bleacher seats, where rows of seats discharge into an aisle, the minimum clear width required by Sentence (5) shall be increased by 25 mm for each metre of length of the aisle measured in the direction towards an exit. |  | Common Sentence | Yes | Assembly Seating
2015 | ON | NBC | Div B | 3.3.2.5.(3) | Aisles | Except in the case of bleacher seats, the minimum clear width of aisles referred to in Sentence 3.3.2.5.(2) shall be measured at the point farthest from an exit, cross aisle or foyer and shall be increased by 25 mm for each metre of distance toward the exit, cross aisle or foyer. | obc2019_divb | Div B | 3.3.2.4.(6) | 3.3.2.4. Aisles | The minimum clear width of each aisle shall be measured at the point in the aisle furthest from, an egress doorway referred to in Clause (15)(a), an exit referred to in Clause (15)(b), or an exit referred to in Sentence (16). |  | Common Sentence | Yes | Assembly Seating
2015 | ON | NBC | Div B | 3.3.2.5.(4) | Aisles | Aisles shall terminate in a cross aisle, foyer or exit, and the width of the cross aisle, foyer or exit shall be not less than the required width of the widest aisle plus 50% of the total required width of the remaining aisles that it serves. | obc2019_divb | Div B | 3.3.2.4.(8) | 3.3.2.4. Aisles | The width of a converging aisle shall be not less than the required width of the widest aisle plus 50% of the total required width of the remaining aisles that it serves. |  | Common Sentence | Yes | Assembly Seating
2015 | ON | NBC | Div B | 3.3.2.5.(4) | Aisles | Aisles shall terminate in a cross aisle, foyer or exit, and the width of the cross aisle, foyer or exit shall be not less than the required width of the widest aisle plus 50% of the total required width of the remaining aisles that it serves. | obc2019_divb | Div B | 3.3.2.4.(3) | 3.3.2.4. Aisles | An aisle shall terminate at, a converging aisle, an egress doorway from the seating area, or an exit from the seating area. |  | Common Sentence | Yes | Assembly Seating
2015 | ON | NBC | Div B | 3.3.2.5.(5) | Aisles | Dead-end aisles shall be not more than 6 m long. | obc2019_divb | Div B | 3.3.2.4.(12) | 3.3.2.4. Aisles | Except as provided in Sentences (13) and (14), dead-end aisles shall be not more than 6 m long. |  | Common Sentence | Yes | Assembly Seating
2015 | ON | NBC | Div B | 3.3.2.5.(6) | Aisles | The length of travel to an exit door by any aisle shall be not more than 45m. | obc2019_divb | Div B | 3.3.2.4.(16) | 3.3.2.4. Aisles | Where a seating area is not required to be separated by Sentences 3.3.2.2.(1) and (2) or 3.3.2.2.(8), the travel distance shall be not more than 45 m measured from the most remote point of the aisle to an exit. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.5.(6) | Aisles | The length of travel to an exit door by any aisle shall be not more than 45m. | obc2019_divb | Div B | 3.3.2.4.(15) | 3.3.2.4. Aisles | Where a seating area is separated as required by Sentences 3.3.2.2.(1) and (2) or 3.3.2.2.(8), the length of travel by any aisle shall be not more than 45 m measured from the most remote point of the aisle to, an egress doorway in the required separation, or an exit leading directly from the seating area. |  | Common Sentence | Yes | Assembly Seating
2015 | ON | NBC | Div B | 3.3.2.5.(7) | Aisles | Side aisles shall be not less than 1?100 mm wide if seating is provided in conformance with Sentence 3.3.2.4.(4). | obc2019_divb | Div B | 3.3.2.4.(17) | 3.3.2.4. Aisles | Side aisles shall be not less than 1 100 mm wide if seating is provided in conformance with Sentence 3.3.2.3.(4). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.5.(8) | Aisles | An aisle that has a slope not more than 1 in 8 shall not be stepped. | obc2019_divb | Div B | 3.3.2.4.(18) | 3.3.2.4. Aisles | An aisle that has a slope not more than 1 in 8 shall not be stepped. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.5.(9) | Aisles | An aisle that slopes more than 1 in 8 shall be stepped. | obc2019_divb | Div B | 3.3.2.4.(19) | 3.3.2.4. Aisles | An aisle that slopes more than 1 in 8 shall be stepped. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.6.(1) | Corridors | Except as permitted by Sentences 3.3.2.6.(2) to 3.3.2.6.(4), a corridor used by the public in an assembly occupancy as an access to exit shall be separated from the remainder of the floor area by a fire separation having a fire-resistance rating not less than 1 h. | obc2019_divb | Div B | 3.3.2.5.(1) | 3.3.2.5. Corridors | Except as permitted by Sentences (2) to (4), a corridor used by the public in an assembly occupancy as an access to exit shall be separated from the remainder of the floor area by a fire separation having a fire-resistance rating not less than 1 h. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.6.(3) | Corridors | The fire-resistance rating required by Sentence 3.3.2.6.(1) is permitted to be waived if the floor area in which the corridor is located is sprinklered throughout. | obc2019_divb | Div B | 3.3.2.5.(3) | 3.3.2.5. Corridors | The fire-resistance rating required by Sentence (1) is permitted to be waived if the floor area in which the corridor is located is sprinklered. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.6.(4) | Corridors | The requirement for a fire separation stated in Sentence 3.3.2.6.(1) is permitted to be waived if the distance from any point in the floor area to an exit measured along the path of travel to the exit does not exceed the travel distance permitted by Article 3.4.2.5. | obc2019_divb | Div B | 3.3.2.5.(4) | 3.3.2.5. Corridors | The fire separation required by Sentence (1) is permitted to be waived if the distance from any point in the floor area to an exit measured along the path of travel to an exit does not exceed the travel distance permitted by Article 3.4.2.5. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.7.(1) | Doors | A door equipped with a latching mechanism in an access to exit from a room or suite of assembly occupancy containing an occupant load more than 100 shall be equipped with a device that will release the latch and allow the door to swing wide open when a force not more than that specified in Sentence 3.8.3.6.(8) is applied to the device in the direction of travel to the exit. | obc2019_divb | Div B | 3.3.2.6.(1) | 3.3.2.6. Doors | A door equipped with a latching mechanism in an access to exit from a room or suite of assembly occupancy containing an occupant load more than 100 shall be equipped with a device that will release the latch and allow the door to swing wide open when a force not more than that specified in Sentence 3.8.3.3.(7) is applied to the device in the direction of travel to the exit. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.8.(1) | Fixed Bench-Type Seats without Arms | If fixed bench-type seats without arms are provided, the seat width per person shall be assumed to be 450 mm. | obc2019_divb | Div B | 3.3.2.7.(1) | 3.3.2.7. Fixed Bench-Type Seats Without Arms | If fixed bench-type seats without arms are provided, the seat width per person shall be assumed to be 450 mm. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.8.(2) | Fixed Bench-Type Seats without Arms | The centre-to-centre spacing between rows of bench-type seats shall be not less than 760 mm if back rests are provided, and not less than 550 mm if back rests are not provided. | obc2019_divb | Div B | 3.3.2.7.(2) | 3.3.2.7. Fixed Bench-Type Seats Without Arms | The centre-to-centre spacing between rows of bench-type seats shall be not less than 760 mm if back rests are provided, and not less than 550 mm if back rests are not provided. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.8.(3) | Fixed Bench-Type Seats without Arms | A clear space of not less than 300 mm shall be provided between the back of each seat and the front of the seat immediately behind it. | obc2019_divb | Div B | 3.3.2.7.(3) | 3.3.2.7. Fixed Bench-Type Seats Without Arms | A clear space of not less than 300 mm shall be provided between the back of each seat and the front of the seat immediately behind it. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.9.(1) | Guards | Except as required by Sentences 3.3.2.9.(2) to 3.3.2.9.(4) for bleacher seats, guards shall be installed in outdoor and indoor places of assembly with fixed seats so that at the fascia of every box, balcony or gallery where the seats extend to the edge, the height of guards is not less than 760 mm in front of the seats, and 920 mm if located at the end of aisles or at the foot of steps, the height of guards along every cross aisle other than those adjacent to the fascia of every box, balcony or gallery is not less than 660 mm, except that guards need not be provided if the backs of the seats along the front side of the aisle are not less than 600 mm above the floor of the aisle, and where the seating is arranged in successive tiers and the height of rise between platforms is more than 450 mm, the height of guards is not less than 660 mm along the entire row of seats at the edge of the platform. | obc2019_divb | Div B | 3.3.2.8.(1) | 3.3.2.8. Guards | Except as required by Sentences (2) to (4) for bleacher seats, guards shall be installed in outdoor and indoor places of assembly with fixed seats so that, at the fascia of every box, balcony or gallery where the seats extend to the edge, the height of guards is not less than, 760 mm in front of the seats, and 920 mm if located at the end of aisles or at the foot of steps, the height of guards along every cross aisle other than those adjacent to the fascia of every box, balcony or gallery is not less than 660 mm, except that guards need not be provided if the backs of the seats along the front side of the aisle are not less than 600 mm above the floor of the aisle, and where the seating is arranged in successive tiers and the height of rise between platforms is more than 450 mm, the height of guards is not less than 660 mm along the entire row of seats at the edge of the platform. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.9.(2) | Guards | The backs and ends of bleacher seats more than 1?200 mm above the ground or floor that are not adjacent to a wall shall be protected with a guard not less than 1?070 mm high above an adjacent aisle surface or foot rest, and not less than 920 mm high above the centre of an adjacent seat board. | obc2019_divb | Div B | 3.3.2.8.(2) | 3.3.2.8. Guards | The backs and ends of bleacher seats more than 1 200 mm above the ground or floor that are not adjacent to a wall shall be protected with a guard, not less than 1 070 mm high above an adjacent aisle surface or foot rest, and not less than 920 mm high above the centre of an adjacent seat board. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.9.(3) | Guards | If the front of a bleacher is more than 600 mm above the ground or floor, it shall be protected with a guard not less than 840 mm high above the front foot rest. | obc2019_divb | Div B | 3.3.2.8.(3) | 3.3.2.8. Guards | If the front of a bleacher is more than 600 mm above the ground or floor, it shall be protected with a guard not less than 840 mm high above the front foot rest. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.2.9.(4) | Guards | The size of any opening in a guard required by Sentences 3.3.2.9.(2) and 3.3.2.9.(3) shall not allow the passage of a sphere whose diameter is more than 300 mm. | obc2019_divb | Div B | 3.3.2.8.(4) | 3.3.2.8. Guards | Openings through any guard that is required by Sentences (2) and (3) shall be of a size that will prevent the passage of a sphere having a diameter more than 300 mm. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.3.1.(1) | Application | This Subsection applies to care, treatment and detention occupancies. (See Note A-3.3.3.1.(1).) | obc2019_divb | Div B | 3.3.3.1.(1) | 3.3.3.1. Scope | This Subsection applies to care occupancies, care and treatment occupancies and detention occupancies. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.3.2.(1) | Separations between Care, Treatment or Detention Occupancies | The fire separation required by Sentence 3.3.5.5.(1) between a care, treatment or detention occupancy and a repair garage shall have no openings. | obc2019_divb | Div B | 3.3.3.2.(1) | 3.3.3.2. Fire Separations | The fire separation required by Sentence 3.3.5.5.(1) between a care, care and treatment or detention occupancy and a repair garage shall have no openings. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.3.3.(1) | Corridors | Except as provided in Sentence (2), a corridor used by the public or serving patients' or residents’ sleeping rooms shall have no dead-end portion. Corridors are permitted to have dead-portions, where (a) the area served by the dead-end portion has a second and separate means of egress, or (b) the corridor serves a suite of care occupancy and the dead-end portion does not exceed 6 m. | obc2019_divb | Div B | 3.3.3.3.(1) | 3.3.3.3. Corridors | A corridor used by the public or serving patients or residents shall have no dead-end portion unless the area served by the dead-end portion has a second and separate means of egress. |  | Common Sentence | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.3.3.3.(3) | Corridors | Corridors shall be not less than (a) 2 400 mm wide in buildings of treatment occupancy where the corridors may be used to move patients or residents in beds, (b) 1 650 mm wide (i) in buildings of care or treatment occupancy where the corridors will not be used to move patients or residents in beds, and (ii) in buildings of care occupancy with more than 10 residents and where the corridors serve the residents, or (c) 1 100 mm wide in buildings of care occupancy with not more than 10 residents. | obc2019_divb | Div B | 3.3.3.3.(5) | 3.3.3.3. Corridors | A corridor in a Group B, Division 3 occupancy that contains sleeping accommodation for not more than 10 persons and not more than six occupants require assistance in evacuation in case of an emergency need not comply with Sentence (3). |  | Common Sentence | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.3.3.3.(3) | Corridors | Corridors shall be not less than (a) 2 400 mm wide in buildings of treatment occupancy where the corridors may be used to move patients or residents in beds, (b) 1 650 mm wide (i) in buildings of care or treatment occupancy where the corridors will not be used to move patients or residents in beds, and (ii) in buildings of care occupancy with more than 10 residents and where the corridors serve the residents, or (c) 1 100 mm wide in buildings of care occupancy with not more than 10 residents. | obc2019_divb | Div B | 3.3.3.3.(2) | 3.3.3.3. Corridors | A corridor serving patients in a hospital shall be not less than 2 400 mm wide |  | Common Sentence | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.3.3.3.(3) | Corridors | Corridors shall be not less than (a) 2 400 mm wide in buildings of treatment occupancy where the corridors may be used to move patients or residents in beds, (b) 1 650 mm wide (i) in buildings of care or treatment occupancy where the corridors will not be used to move patients or residents in beds, and (ii) in buildings of care occupancy with more than 10 residents and where the corridors serve the residents, or (c) 1 100 mm wide in buildings of care occupancy with not more than 10 residents. | obc2019_divb | Div B | 3.3.3.3.(3) | 3.3.3.3. Corridors | Except as permitted in Sentence (5), a corridor serving residents who are not ambulatory in a Group B, Division 2 or 3 occupancy shall be not less than 1 650 mm wide. |  | Common Sentence | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.3.3.3.(4) | Corridors | Paired doors in a corridor referred to in Clause 3.3.3.3.(3)(a) shall (a) swing in opposite directions, the right-hand door swinging in the direction of travel, and (b) be not less than 1100 mm wide. | obc2019_divb | Div B | 3.3.3.3.(4) | 3.3.3.3. Corridors | Paired doors in a corridor serving patients or residents shall, swing in opposite directions, the right hand door swinging in the direction of travel, and be not less than 1 100 mm wide. |  | Common Sentence | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.3.3.4.(2) | Doorway Width | The minimum clear width of doorways through which it is necessary to move patients in bed shall be 1?050 mm. (See Note A-3.3.3.4.(2).) | obc2019_divb | Div B | 3.3.3.4.(1) | 3.3.3.4. Doorway Width | In a Group B, Division 2 or 3 occupancy, the minimum clear width of doorways through which it is necessary to move a patient or resident in a bed shall be 1 050 mm. (See Appendix A.) |  | Common Sentence | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.3.3.5.(1) | Compartments and Fire Separations | Floor areas containing patients’ or residents’ sleeping rooms in a care or treatment occupancy where overnight sleeping accommodation is provided for more than a total of 10 patients or residents shall conform to Sentences (2) to (13). | obc2019_divb | Div B | 3.3.3.2.(2) | 3.3.3.2. Fire Separations | Except as permitted by Sentence (4), in a Group B, Division 3 occupancy, walls between sleeping rooms and adjacent rooms shall be constructed as fire separations having a fire-resistance rating not less than 1 h, except that the fire-resistance rating need not be more than 45 min where the floor assembly is not required to be more than 45 min. |  | Common Sentence | Yes | Care Occupancy
2015 | ON | NBC | Div B | 3.3.3.5.(1) | Compartments and Fire Separations | Floor areas containing patientsâ€™ or residents'€™ sleeping rooms in a care or treatment occupancy where overnight sleeping accommodation is provided for more than a total of 10 patients or residents shall conform to Sentences 3.3.3.5.(2) to 3.3.3.5.(13). | obc2019_divb | Div B | 3.3.3.5.(1) | 3.3.3.5. Hospitals and Long-Term Care Homes | Floor areas containing patientsÃ¢â‚¬â„¢ or residentsÃ¢â‚¬â„¢ sleeping rooms in a hospital or long-term care home shall conform to Sentences (2) to (12). (See Appendix A.) |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.3.3.5.(11) | Compartments and Fire Separations | A door in a fire separation required by Sentence 3.3.3.5.(8) is permitted to be equipped with a roller latch. | obc2019_divb | Div B | 3.3.3.5.(11) | 3.3.3.5. Hospitals and Long-Term Care Homes | A door in a fire separation required by Sentence (9) is permitted to be equipped with a roller latch. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.3.5.(12) | Compartments and Fire Separations | Except as permitted by Sentence 3.3.3.5.(13), a fire separation required by Sentence 3.3.3.5.(8) shall not have any grilles, louvres or other openings. | obc2019_divb | Div B | 3.3.3.5.(12) | 3.3.3.5. Hospitals and Long-Term Care Homes | A fire separation required by Sentence (9) shall not contain any grilles, louvres or other openings. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.3.3.5.(2) | Compartments and Fire Separations | Except as permitted by Sentence 3.3.3.5.(3), a floor area described in Sentence 3.3.3.5.(1) shall be divided into not less than 2 fire compartments, each not more than 1000 m2 in area. | obc2019_divb | Div B | 3.3.3.5.(2) | 3.3.3.5. Hospitals and Long-Term Care Homes | Except as permitted by Sentence (3), a floor area containing patients or residents sleeping rooms in a hospital or long-term care home shall be divided into no fewer than two fire compartments, each not more than 1 000 m2 in area. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.3.3.5.(3) | Compartments and Fire Separations | The floor area on either side of a horizontal exit conforming to Article 3.4.6.10. is permitted to be considered as a fire compartment in applying the requirements of this Article. | obc2019_divb | Div B | 3.3.3.5.(3) | 3.3.3.5. Hospitals and Long-Term Care Homes | The floor area on either side of a horizontal exit conforming to Article 3.4.6.10. is permitted to be considered as a fire compartment in applying the requirements of this Article. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.3.5.(4) | Compartments and Fire Separations | Except as permitted by Sentence 3.3.3.5.(5), fire separations separating fire compartments required by Sentence 3.3.3.5.(2) shall have a fire-resistance rating not less than 1 h. | obc2019_divb | Div B | 3.3.3.5.(4) | 3.3.3.5. Hospitals and Long-Term Care Homes | Except as permitted by Sentence (5), fire separations separating fire compartments required by Sentence (2) shall have a fire-resistance rating not less than 1 h. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.3.5.(5) | Compartments and Fire Separations | The fire-resistance rating of a fire separation referred to in Sentence 3.3.3.5.(4) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by part 3. is permitted to be less than 1 h for the floor assembly above the floor area, or the floor assembly below the floor area, if there is no floor assembly above. | obc2019_divb | Div B | 3.3.3.5.(5) | 3.3.3.5. Hospitals and Long-Term Care Homes | The fire-resistance rating of a fire separation referred to in Sentence (4) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for, the floor assembly above the floor area, or the floor assembly below the floor area, if there is no floor assembly above. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.3.5.(6) | Compartments and Fire Separations | The travel distance from any point within each fire compartment referred to in Sentence 3.3.3.5.(2) to a door to an adjoining fire compartment shall be not more than 45 m. | obc2019_divb | Div B | 3.3.3.5.(7) | 3.3.3.5. Hospitals and Long-Term Care Homes | The travel distance from any point within each fire compartment referred to in Sentence (2) to a door to an adjoining fire compartment shall be not more than 45 m. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.3.5.(7) | Compartments and Fire Separations | Each fire compartment referred to in Sentence 3.3.3.5.(2) shall be capable of accommodating, in addition to its own occupants, the occupants of the largest adjacent fire compartment based on a clear floor space of 2.5 m2 per patient in the adjacent fire compartment. | obc2019_divb | Div B | 3.3.3.5.(8) | 3.3.3.5. Hospitals and Long-Term Care Homes | Each fire compartment referred to in Sentence (2) shall be capable of accommodating, in addition to its own occupants, the occupants of the largest adjacent fire compartment based on a clear floor space of 2.5 m2 per patient or resident in the adjacent fire compartment. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.3.3.5.(8) | Compartments and Fire Separations | Except as provided in Sentences 3.3.3.5.(9) to 3.3.3.5.(13), walls between patients or residents sleeping rooms and the remainder of the floor area shall be constructed as fire separations but are not required to have a fire-resistance rating unless one is required by other provisions in this Part. (See Note A-3.1.8.1.(1)(b).) | obc2019_divb | Div B | 3.3.3.5.(9) | 3.3.3.5. Hospitals and Long-Term Care Homes | Except as permitted by Sentences (10) and (11), walls between patients or residents sleeping rooms and the remainder of the floor area shall be constructed as fire separations but are not required to have a fire-resistance rating unless a fire-resistance rating is required by other provisions in this Part. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.3.3.5.(9) | Compartments and Fire Separations | The fire separation requirements of Sentence 3.3.3.5.(8) do not apply to walls within a group of intercommunicating patientsâ€™ or residents'€™ sleeping rooms, provided the group of rooms does not contain more than 5 patients or residents, or include storage, bathing or toilet facilities serving persons not occupying the group of rooms. | obc2019_divb | Div B | 3.3.3.5.(10) | 3.3.3.5. Hospitals and Long-Term Care Homes | The fire separation requirements of Sentence (9) do not apply to walls within a group of intercommunicating patientsÃ¢â‚¬â„¢ or residentsÃ¢â‚¬â„¢ rooms, provided the group of rooms does not contain more than five patients or residents, or include storage, bathing or toilet facilities serving persons not occupying the group of rooms. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.3.6.(1) | Areas of Refuge | Compartments containing rooms such as operating rooms, recovery rooms, delivery rooms and intensive care units, from which it is impracticable to move patients in an emergency, shall be (a) separated from adjacent spaces by fire separations having a fire-resistance rating not less than 1 h, and (b) provided with a mechanical air supply so that during a period of 2 h after the start of a fire in another space, the compartments will not contain more than 1% by volume of contaminated air from the fire area. | obc2019_divb | Div B | 3.3.3.6.(1) | 3.3.3.6. Protection for Special Care and Treatment Facilities | Compartments containing rooms such as operating rooms, recovery rooms, delivery rooms, intensive care units and critical care units, from which it is impracticable to move patients in an emergency, shall be,(a) separated from adjacent spaces by fire separations having a fire-resistance rating not less than 1 h, and (b) provided with a mechanical air supply so that during a period of 2 h after the start of a fire in another space, the compartments will not contain more than 1% by volume of contaminated air from the fire area. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.3.3.7.(1) | Contained Use Areas | A contained use area shall conform to Sentences 3.3.3.7.(2) to 3.3.3.7.(5). | obc2019_divb | Div B | 3.3.3.7.(1) | 3.3.3.7. Contained Use Areas | A contained use area shall conform to Sentences (2) to (5). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.3.7.(2) | Contained Use Areas | A contained use area shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h. | obc2019_divb | Div B | 3.3.3.7.(2) | 3.3.3.7. Contained Use Areas | A contained use area shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.3.7.(3) | Contained Use Areas | Except as permitted by Sentence 3.3.3.7.(4), a building that includes a contained use area shall be sprinklered throughout. | obc2019_divb | Div B | 3.3.3.7.(3) | 3.3.3.7. Contained Use Areas | Except as permitted by Sentence (4), a building that includes a contained use area shall be sprinklered. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.3.7.(4) | Contained Use Areas | A contained use area, in a building for which Articles 3.2.2.20. to 3.2.2.90. do not require the installation of an automatic sprinkler system, is not required to be sprinklered as required by Sentence 3.3.3.7.(3) provided (a) the building is designed so that during a period of 2 h after the start of a fire in the contained use area other fire compartments will not contain more than 1% by volume of contaminated air from the contained use area, (b) the building is designed so that during a period of 2 h after the start of a fire in another part of the building the contained use area will not contain more than 1% by volume of contaminated air from the other part of the building, (c) all doors are designed to be remotely released in conformance with Sentence 3.3.1.13.(6), and (d) the contained use area does not contain any rooms lined with combustible padding. | obc2019_divb | Div B | 3.3.3.7.(4) | 3.3.3.7. Contained Use Areas | A contained use area, in a building for which Articles 3.2.2.20. to 3.2.2.83. do not require the installation of an automatic sprinkler system, is not required to be sprinklered as required by Sentence (3) provided, (a) the building is designed so that during a period of 2 h after the start of a fire in the contained use area, other fire compartments will not contain more than 1% by volume of contaminated air from the contained use area, (b) the building is designed so that during a period of 2 h after the start of a fire in another part of the building, the contained use area will not contain more than 1% by volume of contaminated air from the other part of the building, (c) all doors are designed to be remotely released in conformance with Sentence 3.3.1.12.(6), and (d) the contained use area does not contain any rooms lined with combustible padding. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.3.7.(5) | Contained Use Areas | A corridor serving a contained use area shall have no dead-end portion unless the area served by the dead-end portion has a second and separate means of egress. | obc2019_divb | Div B | 3.3.3.7.(5) | 3.3.3.7. Contained Use Areas | A corridor serving a contained use area shall have no dead-end portion unless the area served by the dead-end portion has a second and separate means of egress. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.4.1.(1) | Scope | This Subsection applies to residential occupancies. | obc2019_divb | Div B | 3.3.4.1.(1) | 3.3.4.1. Scope | This Subsection applies to residential occupancies. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.4.2.(1) | Fire Separations | Except as permitted by Sentences 3.3.4.2.(2) and 3.2.2.9.(2), suites of residential occupancy shall be separated from each other and the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h. | obc2019_divb | Div B | 3.3.4.2.(1) | 3.3.4.2. Fire Separations | Except as permitted by Sentences (2) and 3.2.2.9.(2), suites of residential occupancy shall be separated from each other and the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.4.2.(2) | Fire Separations | The fire-resistance rating of the fire separation required by Sentence 3.3.2.2.(1) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by part 3. is permitted to be less than 1 h for the floor assembly above the floor area, or the floor assembly below the floor area, if there is no floor assembly above. | obc2019_divb | Div B | 3.3.4.2.(2) | 3.3.4.2. Fire Separations | The fire-resistance rating of the fire separation required by Sentence (1) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for, the floor assembly above the floor area, or the floor assembly below the floor area, if there is no floor assembly above. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.4.2.(3) | Fire Separations | Floor assemblies within a dwelling unit need not be constructed as fire separations provided (a) the distance between the lowest floor level and the upper most floor level within the dwelling unit is not more than 6m, and (b) the dwelling unit is separated from the remainder of the building by a fire separation having a fire-resistance rating not less than (i) 1h if the building is not sprinklered throughout, (ii) 45min if the building is sprinklered throughout and it is not more than 3 storeys in building height, or (iii) 1h if the building is sprinklered throughout and it is more than 3 storeys in building height. | obc2019_divb | Div B | 3.3.4.2.(3) | 3.3.4.2. Fire Separations | Floor assemblies within a dwelling unit need not be constructed as fire separations provided, (a) the distance between the lowest floor level and the uppermost floor level within the dwelling unit is not more than 6 m, and (b) the dwelling unit is separated from the remainder of the building by a fire separation having a fire-resistance rating not less than, (i) 45 min if the building is sprinklered and is not more than 3 storeys in building height, (ii) 1 h if the building is sprinklered and is more than 3 storeys in building height, (iii) 1 h if the building is not sprinklered and is not more than 6 storeys in building height, or (iv) 2 h if the building is not sprinklered and is more than 6 storeys in building height. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.3.4.2.(4) | Fire Separations | The fire-resistance rating of the fire separation required by Sentence 3.3.5.6.(1) is permitted to be waived if the fire separation is located between a dwelling unit and an attached storage garage containing not more than 5 vehicles, provided the dwelling unit and the attached storage garage are sprinklered, the dwelling unit and the attached storage garage are separated from the remainder of the building in conformance with Sentences 3.3.4.2.(1) , 3.3.4.2.(2) and 3.3.4.2.(3), there are no air duct systems connecting the storage garage and the dwelling unit, the construction between the storage garage and the dwelling unit provides an effective barrier to gas and exhaust fumes, and every door between the storage garage and the dwelling unit is tight fitting and weather-stripped to provide an effective barrier against the passage of gas and exhaust fumes, fitted with a self-closing device, and not located in a room intended for sleeping. | obc2019_divb | Div B | 3.3.4.2.(4) | 3.3.4.2. Fire Separations | Except in a retirement home, the fire-resistance rating of the fire separation located between a dwelling unit and an attached storage garage need not conform to that required by Sentence 3.3.5.6.(1) provided, the storage garage contains not more than five vehicles, the dwelling unit and the attached storage garage are sprinklered, the dwelling unit is separated from the remainder of the building in conformance with Sentences (1) to (3), there are no air duct systems connecting the storage garage and the dwelling unit, the construction between the storage garage and the dwelling unit provides an effective barrier to gas and exhaust fumes, and every door between the storage garage and the dwelling unit is, tight fitting and weather-stripped to provide an effective barrier against the passage of gas and exhaust fumes, fitted with a self-closing device, and not located in a room intended for sleeping. |  | Common Sentence | Yes | Retirement Homes
2015 | ON | NBC | Div B | 3.3.4.2.(5) | Fire Separations | The fire separation required by Sentence 3.3.5.6.(1) is not required between a dwelling unit and an attached storage garage, serving that dwelling unit only, provided (i) the dwelling unit and its attached storage garage are separated from the remainder of the building in conformance with Sentences 3.3.4.2.(1) , 3.3.4.2.(2) and 3.3.4.2.(3), (b) there are no air duct systems connecting the storage garage and the dwelling unit, (c) the construction between the storage garage and the dwelling unit provides an effective barrier to gas and exhaust fumes, and (d) every door between the storage garage and the dwelling unit is (i) tight fitting and weather-stripped to provide an effective barrier against the passage of gas and exhaust fumes, (ii) fitted with a self-closing device, and (iii) not located in a room intended for sleeping. | obc2019_divb | Div B | 3.3.4.2.(5) | 3.3.4.2. Fire Separations | Except in a retirement home, the fire separation required by Sentence 3.3.5.6.(1) is not required between a dwelling unit and an attached storage garage, serving that dwelling unit only, provided, (a) the dwelling unit and its attached storage garage are separated from the remainder of the building in conformance with Sentences (1) to (3), (b) there are no air duct systems connecting the storage garage and the dwelling unit, (c) the construction between the storage garage and the dwelling unit provides an effective barrier to gas and exhaust fumes, and (d) every door between the storage garage and the dwelling unit is, (i) tight fitting and weather-stripped to provide an effective barrier against the passage of gas and exhaust fumes, (ii) fitted with a self-closing device, and (iii) not located in a room intended for sleeping. |  | Common Sentence | Yes | Retirement Homes
2015 | ON | NBC | Div B | 3.3.4.3.(1) | Storage Rooms | Sprinklers shall be installed in a storage room provided for the use of tenants in a residential occupancy within a floor area but not contained within a suite. | obc2019_divb | Div B | 3.3.4.3.(1) | 3.3.4.3. Storage Rooms | Sprinklers shall be installed in a storage room provided for the use of tenants in a residential occupancy within a floor area but not contained within a suite. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.4.3.(2) | Storage Rooms | Except as permitted by Sentence 3.3.4.3.(3), a storage room referred to in Sentence 3.3.4.3.(1) shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h. | obc2019_divb | Div B | 3.3.4.3.(2) | 3.3.4.3. Storage Rooms | Except as permitted by Sentence (3), a storage room referred to in Sentence (1) shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.4.3.(3) | Storage Rooms | The fire-resistance rating of the fire separation required by Sentence 3.3.4.3.(2) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by part 3. is permitted to be less than 1 h for the floor assembly above the floor area, or the floor assembly below the floor area, if there is no floor assembly above. | obc2019_divb | Div B | 3.3.4.3.(3) | 3.3.4.3. Storage Rooms | The fire-resistance rating of the fire separation required by Sentence (2) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for, the floor assembly above the floor area, or the floor assembly below the floor area, if there is no floor assembly above. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.4.3.(4) | Storage Rooms | Except for the storage of flammable liquids and combustible liquids inside a single-family dwelling unit and garages or sheds attached to these dwelling units, where storage rooms are required by Part 4 of Division B of the NFC for the storage of flammable liquids or combustible liquids in residential occupancies ,such rooms shall not be located above or below the first storey. | obc2019_divb | Div B | 3.3.4.3.(4) | 3.3.4.3. Storage Rooms | Except where located within a dwelling unit, a room intended for the storage of flammable liquids or combustible liquids required by the Fire Code made under the Fire Protection and Prevention Act, 1997 shall not be located above or below the first storey of the building. |  | Common Sentence | Yes | Fire Hazards
2015 | ON | NBC | Div B | 3.3.4.4.(1) | Egress from Dwelling Units | Single storey dwelling units in an apartment building need not lead to a public corridor or exterior passageway on the same storey provided the dwelling units are served by private stairways leading directly to a public access to exit on the storey immediately above, and immediately below. | obc2019_divb | Div B | 3.3.4.4.(1) | 3.3.4.4. Egress from Dwelling Units | Except as required by Sentence (8), single storey dwelling units in an apartment building need not lead to a public corridor or exterior passageway on the same storey provided the dwelling units are served by private stairways leading directly to a public access to exit on the storey, immediately above, and immediately below. |  | Common Sentence | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.3.4.4.(2) | Egress from Dwelling Units | Except as permitted by Sentences 3.3.4.4.(3) and 3.3.4.4.(4), a dwelling unit containing more than one storey shall have an exit door or an egress door opening directly into a public access to exit from the uppermost storey and from the lowest storey of the dwelling unit so that each of these storeys is served by an exit or egress door located not more than 1.5 m above or below its floor level. | obc2019_divb | Div B | 3.3.4.4.(2) | 3.3.4.4. Egress from Dwelling Units | Except as required by Sentence (8) and as permitted by Sentences (3) and (4), a dwelling unit containing more than 1 storey shall have an exit door or an egress door opening directly into a public access to exit from the uppermost storey and from the lowest storey of the dwelling unit so that each storey is served by an exit or egress door located not more than 1.5 m above or below its floor level. |  | Common Sentence | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.3.4.4.(3) | Egress from Dwelling Units | A single exit is permitted from a dwelling unit provided the exit is an exterior doorway not more than 1.5 m above adjacent ground level and it is not necessary to travel up or down more than one storey to reach the exit door, or the uppermost floor level opens to a balcony not more than 6 m above adjacent ground level. | obc2019_divb | Div B | 3.3.4.4.(3) | 3.3.4.4. Egress from Dwelling Units | A single exit is permitted from a dwelling unit provided the exit is an exterior doorway not more than 1.5 m above adjacent ground level and, it is not necessary to travel up or down more than 1 storey to reach the exit door, or the uppermost floor level opens to a balcony not more than 6 m above adjacent ground level. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.4.4.(4) | Egress from Dwelling Units | An egress door from either the uppermost storey or the lowest storey of a dwelling unit, as required by Sentence (2), need not be provided if that storey is served by a stairway that (a) leads to a public access to exit, (b) has no direct access to any other storey in the dwelling unit, and (c) is separated from the other storeys in the dwelling unit by a fire separation having a fire-resistance rating not less than 45 min. | obc2019_divb | Div B | 3.3.4.4.(4) | 3.3.4.4. Egress from Dwelling Units | An egress door from either the uppermost storey or the lowest storey in a dwelling unit, as required in Sentence (2), need not be provided, (a) except as required by Sentence (8), if that storey is served by a stairway that, (i) leads to a public access to exit, (ii) has no direct access to any other storey in the dwelling unit, and (iii) is separated from the other storeys in the dwelling unit by a fire separation having a fire-resistance rating of not less than 45 min, (b) on the uppermost storey in the dwelling unit if the dwelling unit has not more than 2 storeys above the first storey of the building, (c) if it is not necessary to travel either more than 18 m or more than 1 storey up or down within the dwelling unit to reach the egress door, or (d) if that storey is, (i) provided with a balcony conforming to Sentence (7), (ii) not more than 2 storeys above or below the dwelling unit egress door, and (iii) in a building that is not more than 6 storeys in building height. |  | Common Sentence | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.3.4.4.(5) | Egress from Dwelling Units | In a building of residential occupancy not more than 3 storeys in building height, a doorway from a dwelling unit is permitted to open directly into an exit stairway provided the dwelling unit has a second and separate means of egress. | obc2019_divb | Div B | 3.3.4.4.(5) | 3.3.4.4. Egress from Dwelling Units | In a building of residential occupancy not more than 3 storeys in building height, a doorway from a dwelling unit is permitted to open directly into an exit stairway provided the dwelling unit has a second and separate means of egress. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.4.4.(6) | Egress from Dwelling Units | If a dwelling unit has a second and separate means of egress, one means of egress from a dwelling unit is permitted to pass through an interior corridor served by a single exit, an exterior balcony served by a single exit stairway, or an exterior passageway served by a single exit stairway. | obc2019_divb | Div B | 3.3.4.4.(6) | 3.3.4.4. Egress from Dwelling Units | If a dwelling unit has a second and separate means of egress, one means of egress from a dwelling unit is permitted to pass through, an interior corridor served by a single exit, an exterior balcony served by a single exit stairway, or an exterior passageway served by a single exit stairway. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.4.5.(1) | Automatic Locking Prohibition | Except for hotels and motels, a door opening onto a public corridor which provides access to exit from a suite shall be designed not to lock automatically. (See Note A-3.3.4.5.(1).) | obc2019_divb | Div B | 3.3.4.5.(1) | 3.3.4.5. Automatic Locking Prohibition | Except for hotels, a door opening onto a public corridor that provides access to exit from a suite shall be designed not to lock automatically. (See Appendix A.) |  | Common Sentence | Yes | Hotels
2015 | ON | NBC | Div B | 3.3.4.6.(1) | Sound Transmission | Occupants of dwelling units shall be protected from airborne noise in conformance with Section 5.8 | obc2019_divb | Div B | 3.3.4.6.(1) | 3.3.4.6. Sound Transmission | Buildings containing dwelling units shall be constructed so that airborne noise is controlled in conformance with Section 5.8. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.4.7.(1) | Stairs, Ramps, Landings, Handrails and Guards for Dwelling | Except as required in Article 3.3.4.8., stairs, ramps, landings, handrails and guards within a dwelling unit shall conform to the appropriate requirements in Section 9.8 | obc2019_divb | Div B | 3.3.4.7.(1) | 3.3.4.7. Stairs, Ramps, Landings, Handrails and Guards for | Except as required by Article 3.3.4.8., stairs, ramps, landings, handrails and interior guards within a dwelling unit shall conform to the applicable requirements in Section 9.8. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.4.7.(2) | Stairs, Ramps, Landings, Handrails and Guards for Dwelling | Exterior stairs, ramps, landings, handrails and guards serving a single dwelling unit, and loads on guards serving not more than two dwelling units, shall conform to the appropriate requirements in Section 9.8. | obc2019_divb | Div B | 3.3.4.7.(2) | 3.3.4.7. Stairs, Ramps, Landings, Handrails and Guards for | Except as provided in Sentence (3), exterior stairs, ramps, landings, handrails and guards serving a single dwelling unit shall conform to the applicable requirements in Section 9.8. and Sentence 3.1.20.1.(1). |  | Common Sentence | Yes | Dwelling Units
2015 | ON | NBC | Div B | 3.3.4.8.(1) | Protection of Openable Windows | Except as provided in Sentence 3.3.4.8.(2), openable windows in suites of residential occupancy shall be protected by a guard with a minimum height of 1?070 mm constructed in accordance with Article 3.3.1.18., or a mechanism capable of controlling the free swinging or sliding of the openable part of the window so as to limit any clear unobstructed opening to not more than 100 mm measured either vertically or horizontally where the other dimension is greater than 380 mm. | obc2019_divb | Div B | 3.3.4.8.(1) | 3.3.4.8. Protection of Openable Windows | Except as provided by Sentence (2), openable windows in suites of residential occupancy shall be protected by, a guard with a minimum height of 1 070 mm constructed in accordance with Article 3.3.1.17., or a mechanism capable of controlling the free swinging or sliding of the openable part of the window so as to limit any clear unobstructed opening to a size that will prevent the passage of a sphere having a diameter more than 100 mm. |  | Common Sentence | Yes | Dwelling Units
2015 | ON | NBC | Div B | 3.3.4.8.(2) | Protection of Openable Windows | Windows need not be protected in accordance with Sentence 3.3.4.8.(1) where the only opening having greater dimensions than those allowed by Sentence 3.3.4.8.(1) is located higher than 1?070 mm above the finished floor, or the bottom edge of the openable portion of the window is located less than 1?800 mm above the floor or ground on the other side of the window. | obc2019_divb | Div B | 3.3.4.8.(2) | 3.3.4.8. Protection of Openable Windows | Windows need not be protected in accordance with Sentence (1) where, the only opening having greater dimensions than those allowed by Clause (1)(b) is located higher than 1 070 mm above the finished floor, or the bottom edge of the openable portion of the window is located less than 1 800 mm above the floor or ground on the other side of the window. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.5.1.(1) | Scope | This Subsection applies to industrial occupancies. | obc2019_divb | Div B | 3.3.5.1.(1) | 3.3.5.1. Scope | This Subsection applies to industrial occupancies. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.5.10.(1) | Guards | Except where they serve storage garages, guards in industrial occupancies are permitted to consist of a top railing, and one or more intermediate rails spaced such that openings through the guard are of a size that prevents the passage of a spherical object whose diameter is 535 mm. | obc2019_divb | Div B | 3.3.5.9.(1) | 3.3.5.9. Guards | Guards in industrial occupancies, other than guards in storage garages, are permitted to consist of, (a) a top rail, and (b) one or more intermediate rails spaced such that the openings through the guard are of a size that prevents the passage of a spherical object having a diameter of 535 mm. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.5.2.(1) | Fire Extinguishing Systems | In addition to other requirements in this Code for the installation of automatic fire extinguishing systems, an appropriate fire extinguishing system shall be installed in every industrial occupancy floor area to provide protection if required by provincial or territorial regulations or municipal bylaws, or the NFC, in the absence of the regulations or bylaws referred to in Sentence 3.3.5.2.(1). | obc2019_divb | Div B | 3.3.5.2.(1) | 3.3.5.2. Fire Extinguishing Systems | In addition to other requirements in this Division for the installation of automatic fire extinguishing systems, an appropriate fire extinguishing system shall be installed in every industrial occupancy floor area to provide protection if required by, the Fire Code made under the Fire Protection and Prevention Act, 1997, or the CCBFC NRCC 56192, "National Fire Code of Canada", in the absence of provisions referred to in Clause (a). |  | Common Sentence | Yes | Fire Suppression
2015 | ON | NBC | Div B | 3.3.5.3.(1) | Basements | A basement shall not be used for the storage, manufacture or handling of volatile solids, liquids or gases that generate explosive air-vapour mixtures or for processes that involve explosive dusts. | obc2019_divb | Div B | 3.3.5.3.(1) | 3.3.5.3. Basements | A basement shall not be used for the storage, manufacture or handling of volatile solids, liquids or gases that generate explosive air-vapour mixtures or for processes that involve explosive dusts. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.5.3.(2) | Basements | Entrances and exits to a basement and to rooms containing building services shall be separate from the remainder of the building in a building in which the storage, manufacture or handling of volatile materials can generate explosive air-vapour mixtures, or processes occur that produce explosive dusts. | obc2019_divb | Div B | 3.3.5.3.(2) | 3.3.5.3. Basements | Entrances and exits to a basement and to rooms containing building services shall be separate from the remainder of the building in a building in which, the storage, manufacture or handling of volatile materials can generate explosive air-vapour mixtures, or processes occur that produce explosive dusts. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.5.3.(3) | Basements | Basements and rooms referred to in Sentence 3.3.5.3.(2) shall be separated from the remainder of the building with a vapour-tight separation. | obc2019_divb | Div B | 3.3.5.3.(3) | 3.3.5.3. Basements | Basements and rooms referred to in Sentence (2) shall be separated from the remainder of the building with a vapour-tight separation. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.5.4.(1) | Repair and Storage Garages | If access is provided from a storage garage to a stair tower or elevator serving occupancies above the level of the storage garage, the access shall be through a vestibule conforming to Sentence 3.3.5.7.(4). | obc2019_divb | Div B | 3.3.5.4.(1) | 3.3.5.4. Repair and Storage Garages (See Appendix A.) | If access is provided from a storage garage to a stair tower or elevator serving occupancies above the level of the storage garage, the access shall be through a vestibule conforming to Sentence 3.3.5.7.(3). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.5.4.(2) | Repair and Storage Garages | Treads and landings in interior stairs that extend to the roof of a storage garage shall be designed to be free of accumulations of ice and snow. | obc2019_divb | Div B | 3.3.5.4.(2) | 3.3.5.4. Repair and Storage Garages (See Appendix A.) | Treads and landings in interior stairs that extend to the roof of a storage garage shall be designed to be free of accumulations of ice and snow. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.5.4.(3) | Repair and Storage Garages | A mechanical storage garage not more than 4 storeys in building height, in which no persons other than parking attendants are permitted above the street floor level, need not have a fire separation between the exits and the remainder of the building. | obc2019_divb | Div B | 3.3.5.4.(3) | 3.3.5.4. Repair and Storage Garages (See Appendix A.) | A mechanical storage garage not more than 4 storeys in building height, in which no persons other than parking attendants are permitted above the street floor level, need not have a fire separation between the exits and the remainder of the building. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.5.4.(4) | Repair and Storage Garages | A garage shall be provided with natural or mechanical ventilation in conformance with the requirements of part 6. and Article 6.9.1.2. to prevent excessive accumulation of carbon monoxide, exhaust fumes or flammable and toxic vapours. | obc2019_divb | Div B | 3.3.5.4.(4) | 3.3.5.4. Repair and Storage Garages (See Appendix A.) | A garage shall be provided with natural or mechanical ventilation in conformance with the requirements of Subsection 6.2.2. to prevent excessive accumulation of carbon monoxide, exhaust fumes or flammable and toxic vapours. |  | Common Sentence | Yes | HVAC
2015 | ON | NBC | Div B | 3.3.5.4.(5) | Repair and Storage Garages | The clear height in a storage garage shall be not less than 2 m. | obc2019_divb | Div B | 3.3.5.4.(5) | 3.3.5.4. Repair and Storage Garages (See Appendix A.) | Except as required by Sentence 3.8.2.2.(2), the clear height in a storage garage shall be not less than 2 m |  | Common Sentence | Yes | Risk of Collision
2015 | ON | NBC | Div B | 3.3.5.4.(6) | Repair and Storage Garages | Vehicle guardrails and full-height walls required in Sentence (6) shall be designed and constructed to withstand the loading values stipulated in Sentence 4.1.5.15.(1). | obc2019_divb | Div B | 3.3.5.4.(6) | 3.3.5.4. Repair and Storage Garages (See Appendix A.) | Vehicle guardrails and full-height walls required by Sentence (6) shall be designed and constructed to withstand the loading values specified in Sentence 4.1.5.15.(1). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.5.4.(6) | Repair and Storage Garages | Where garage floors or ramps are 600 mm or more above the adjacent ground or floor level, every opening through such floors and the perimeter of floors and ramps shall be provided with (a) a continuous curb not less than 140 mm high, a guard not less than 1 070 mm high, and a vehicle guardrail not less than 500 mm high conforming to Sentence 3.3.5.4.(7), or (b) a full-height wall conforming to Sentence 3.3.5.4.(7). | obc2019_divb | Div B | 3.3.5.4.(6) | 3.3.5.4. Repair and Storage Garages (See Appendix A.) | Where storage garage or repair garage floors or ramps are 600 mm or more above the adjacent ground or floor level, every opening through such floors and the perimeter of such floors and ramps shall be provided with, (a) a continuous curb not less than 140 mm high, a guard not less than 1 070 mm high and a vehicle guardrail not less than 500 mm high conforming to Sentence (6.1), or (b) a full-height wall conforming to Sentence (6.1). |  | Common Sentence | Yes | Falling, Tripping, Slipping Protection
2015 | ON | NBC | Div B | 3.3.5.4.(7) | Repair and Storage Garages | Vehicle guardrails and full-height walls required in Sentence (6) shall be designed and constructed to withstand the loading values stipulated in Sentence 4.1.5.15.(1). | obc2019_divb | Div B | 3.3.5.4.(6) | 3.3.5.4. Repair and Storage Garages (See Appendix A.) | Where storage garage or repair garage floors or ramps are 600 mm or more above the adjacent ground or floor level, every opening through such floors and the perimeter of such floors and ramps shall be provided with, a continuous curb not less than 140 mm high, a guard not less than 1 070 mm high and a vehicle guardrail not less than 500 mm high conforming to Sentence (6.1), or a full-height wall conforming to Sentence (6.1).(6.1) Vehicle guardrails and full-height walls required by Sentence (6) shall be designed and constructed to withstand the loading values specified in Sentence 4.1.5.15.(1). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.5.4.(8) | Repair and Storage Garages | Except for open-air storeys, every storey of a storage garage or repair garage located below grade shall be sprinklered. | obc2019_divb | Div B | 3.3.5.4.(7) | 3.3.5.4. Repair and Storage Garages (See Appendix A.) | Except for open-air storeys, every storey of a storage garage or repair garage located below grade shall be sprinklered. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.5.5.(1) | Repair Garage Separation | A repair garage and any ancillary spaces serving it, including waiting rooms, reception rooms, tool and parts storage areas and supervisory office space, shall be separated from other occupancies by a fire separation having a fire-resistance rating not less than 2 h. | obc2019_divb | Div B | 3.3.5.5.(1) | 3.3.5.5. Repair Garage Separation | A repair garage and any ancillary spaces serving it, including waiting rooms, reception rooms, tool and parts storage areas and supervisory office space, shall be separated from other occupancies by a fire separation having a fire-resistance rating not less than 2 h. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.5.6.(1) | Storage Garage Separation | Except as permitted by Sentences 3.3.4.2.(4) and 3.3.4.2.(5), a storage garage shall be separated from other occupancies by a fire separation with a fire-resistance rating not less than 1.5 h. | obc2019_divb | Div B | 3.3.5.6.(1) | 3.3.5.6. Storage Garage Separation | Except as permitted by Sentences 3.3.4.2.(4) and (5), a storage garage shall be separated from other occupancies by a fire separation with a fire-resistance rating not less than 1.5 h. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.5.7.(1) | Vestibules | Except as provided in Sentence 3.3.5.7.(2), if access is provided through a fire separation between a storage garage and a Group A, Division 1 or Group B occupancy, the access shall be through a vestibule conforming to Sentence 3.3.5.7.(4). | obc2019_divb | Div B | 3.3.5.7.(1) | 3.3.5.7. Vestibules | If access is provided through a fire separation between a storage garage and a Group A, Division 1 or Group B occupancy or a retirement home, the access shall be through a vestibule conforming to Sentence (3). |  | Common Sentence | Yes | Retirement Homes
2015 | ON | NBC | Div B | 3.3.5.7.(3) | Vestibules | In a building more than 3 storeys in building height, access through a fire separation between a storage garage and a Group A, Division 2, 3 or 4, or a Group C occupancy, shall be through a vestibule conforming to Sentence 3.3.5.7.(4). | obc2019_divb | Div B | 3.3.5.7.(2) | 3.3.5.7. Vestibules | In a building more than 3 storeys in building height, access through a fire separation between a storage garage and a Group A, Division 2, 3 or 4, or a Group C occupancy, shall be through a vestibule conforming to Sentence (3). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.5.7.(4) | Vestibules | If access is provided through a vestibule, as required by Sentences 3.3.5.7.(1) , 3.3.5.7.(3) and 3.3.5.4.(1), the vestibule shall (a) be not less than 1.8 m long, (b) be ventilated (i) naturally to outside air by a vent that has an unobstructed area of not less than 0.1 m2 for each door that opens into the vestibule but not less than 0.4 m2 , or (ii) mechanically at a rate of 14 m3/h for each square metre of vestibule floor surface area, and (c) have openings between the vestibule and an adjoining occupancy provided with self-closing doors with no hold-open devices. | obc2019_divb | Div B | 3.3.5.7.(3) | 3.3.5.7. Vestibules | If access is provided through a vestibule, as required by Sentences (1), (2) and 3.3.5.4.(1), the vestibule shall, (a) be not less than 1.8 m long, (b) be ventilated, (i) naturally to outside air by a vent that has an unobstructed area of not less than 0.1 m2 for each door that opens into the vestibule but not less than 0.4 m², or (ii) mechanically at a rate of 14 m3/h for each square metre of vestibule floor surface area, and (c) have openings between the vestibule and an adjoining occupancy provided with self-closing doors with no hold-open devices. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.6.1.(1) | Application | This Subsection applies to design and fire protection requirements for buildings or parts thereof used for the storage, handling, use and processing of dangerous goods, including flammable liquids and combustible liquids, in quantities in excess of those identified in Table 3.2.7.1. of Division B of the NFC. (See Note A-3.3.6.1.(1).) | obc2019_divb | Div B | 3.3.6.1.(1) | 3.3.6.1. Application | This Subsection applies to design and fire protection requirements for buildings or parts of buildings intended for the storage, handling, use and processing of, dangerous goods, materials that involve a risk of explosion or high flammability, and materials that are highly reactive. |  | Common Sentence | Yes | Fire Hazards
2015 | ON | NBC | Div B | 3.3.6.2.(1) | Storage of Dangerous Goods | Solid and liquid dangerous goods classified as oxidizers or organic peroxides shall be separated from the remainder of the building by a fire separation having a fire-resistance rating of not less than 2 h. | obc2019_divb | Div B | 3.3.6.2.(1) | 3.3.6.2. Storage of Dangerous Goods | A room intended for the storage of solid and liquid dangerous goods classified as oxidizers or organic peroxides shall be separated from the remainder of the building by a fire separation having a fire-resistance rating of not less than 2 h. |  | Common Sentence | No | Fire Hazards
2015 | ON | NBC | Div B | 3.3.6.2.(2) | Storage of Dangerous Goods | Reactive materials shall be separated from the remainder of the building by a fire separation having a fire-resistance rating of not less than 2 h. (See Note A-3.3.6.2.(2).) | obc2019_divb | Div B | 3.3.6.2.(2) | 3.3.6.2. Storage of Dangerous Goods | A room intended for the storage of reactive materials shall be separated from the remainder of the building by a fire separation having a fire-resistance rating of not less than 2 h. (See Appendix A.) |  | Common Sentence | No | Fire Hazards
2015 | ON | NBC | Div B | 3.3.6.2.(3) | Storage of Dangerous Goods | The design of buildings or parts thereof used for the storage of dangerous goods classified as explosives shall conform to the NRCan R.S.C., 1985, c. E-17 Explosives Act and its Regulations, published by Natural Resources Canada. | obc2019_divb | Div B | 3.3.6.2.(3) | 3.3.6.2. Storage of Dangerous Goods | The design and construction of a building or part of a building intended for the storage of dangerous goods classified as explosives shall conform to the Explosives Act (Canada) and the regulations made under that Act. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.6.4.(1) | Storage and Dispensing Rooms for Flammable Liquids and Combustible | Fire separations for rooms where flammable liquids and combustible liquids are stored are required to be constructed with a fire-resistance rating in conformance with Subsection 4.2.9. of Division B of the NFC. | obc2019_divb | Div B | 3.3.6.4.(1) | 3.3.6.4. Storage and Dispensing Rooms for Flammable Liquids | A room intended for the storage of flammable liquids and combustible liquids shall be separated from the remainder of the building by a fire separation having a fire-resistance rating in conformance with the Fire Code made under the Fire Protection and Prevention Act, 1997. |  | Common Sentence | Yes | Fire Hazards
2015 | ON | NBC | Div B | 3.3.6.4.(2) | Storage and Dispensing Rooms for Flammable Liquids and Combustible | Where Class IA or IB liquids specified in Subsection 4.1.2. of Division B of the NFC are dispensed within a storage room, the room shall be designed to prevent critical structural and mechanical damage from an internal explosion in conformance with good engineering practice such as that described in NFPA 68-2013 Explosion Protection by Deflagration Venting (See Note A-3.3.6.4.(2).) | obc2019_divb | Div B | 3.3.6.4.(2) | 3.3.6.4. Storage and Dispensing Rooms for Flammable Liquids | Except as provided by Sentences (3) and (4), a room intended for the storage or dispensing of Class IA or Class IB liquids in open containers shall be designed to prevent critical structural and mechanical damage from an internal explosion in accordance with good engineering practice, such as that described in NFPA 68, "Explosion Protection by Deflagration Venting". (See Appendix A.) |  | Common Sentence | Yes | Fire Hazards
2015 | ON | NBC | Div B | 3.3.6.5.(1) | Tire Storage | A tire storage area designed to contain more than 375 m3 of rubber tires shall be separated from the remainder of the building by a fire separation having a fire-resistance rating of not less than 2 h. (See Note A-3.3.6.5.(1).) | obc2019_divb | Div B | 3.3.6.5.(1) | 3.3.6.5. Tire Storage | A tire storage area intended for the storage of more than 375 m3 of tires shall be separated from the remainder of the building by a fire separation having a fire-resistance rating of not less than 2 h. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.6.6.(1) | Ammonium Nitrate Storage | Where Article 3.2.9.1. of Division B of the NFC applies due to the quantity and nature of the stored product, and as stipulated in Sentences (2) to (6), buildings used for the storage of ammonium nitrate shall be classified as medium-hazard industrial occupancies (Group F, Division 2). Buildings intended for the storage of ammonium nitrate shall be not more than one storey in building height. Buildings intended for the storage of ammonium nitrate shall not (a) have basements or crawl spaces, or (b) contain open floor drains, tunnels, elevator pits or other pockets that might trap molten ammonium nitrate. Buildings intended for the storage of ammonium nitrate shall have not less than 0.007 m2 of vent area for each square metre of storage area, unless mechanical ventilation is provided. All flooring in storage areas described in Sentence (1) shall be constructed of noncombustible materials. Buildings intended for the storage of ammonium nitrate shall be designed to prevent the ammonium nitrate from coming into contact with building materials that (a) will cause the ammonium nitrate to become unstable, (b) may corrode or deteriorate by reason of contact with the ammonium nitrate, or (c) will become impregnated with the ammonium nitrate. (See Note A-3.3.6.6.(6).) | obc2019_divb | Div B | 3.3.6.6.(1) | 3.3.6.6. Ammonium Nitrate Storage | Where the Fire Code made under the Fire Protection and Prevention Act, 1997 applies due to the quantity and nature of the stored product, a building intended for the storage of ammonium nitrate shall, (a) be not more than one storey in building height,(b) not contain a basement or a crawl space, (c) not contain open floor drains, tunnels, elevator pits or other pockets that might trap molten ammonium nitrate, (d) have noncombustible flooring materials in storage areas, (e) be designed to prevent the ammonium nitrate from coming into contact with building materials that, (i) will cause the ammonium nitrate to become unstable, (ii) may corrode or deteriorate by reason of contact with the ammonium nitrate, or (iii) will become impregnated with the ammonium nitrate, and (f) have not less than 0.007 m2 of vent area for each square metre of storage area, unless mechanical ventilation is provided. |  | Common Sentence | Yes | Fire Hazards
2015 | ON | NBC | Div B | 3.3.6.7.(1) | Flooring Materials | Floors in areas where dangerous goods are stored shall be constructed of impermeable materials to prevent the absorption of chemicals. | obc2019_divb | Div B | 3.3.6.7.(1) | 3.3.6.7. Flooring Materials | The floor in an area intended for the storage of dangerous goods shall be constructed of impermeable materials to prevent the absorption of chemicals. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.6.8.(1) | Fire Separations in Process Plants | In process plants, areas where unstable liquids are handled or where small-scale unit chemical processes occur shall be separated from the remainder of the building by a fire separation having a fire-resistance rating of not less than 2 h. | obc2019_divb | Div B | 3.3.6.8.(1) | 3.3.6.8. Fire Separations in Process Plants | In a process plant, an area intended as a location where unstable liquids are handled or small scale unit chemical processes occur shall be separated from the remainder of the building by a fire separation having a fire-resistance rating of not less than 2 h. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.3.6.9.(1) | Basements and Pits | Process plants where Class I and II flammable liquids and combustible liquids are handled shall not be constructed with basements or covered pits. | obc2019_divb | Div B | 3.3.6.9.(1) | 3.3.6.9. Basements and Pits | A process plant intended as a location where Class I and Class II liquids are handled shall not contain a basement or a covered pit. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.1.1.(1) | Scope | Exit facilities complying with this Section shall be provided from every floor area that is intended for occupancy. (See Note A-3.4.1.1.(1).) | obc2019_divb | Div B | 3.4.1.1.(1) | 3.4.1.1. Scope | Exit facilities complying with this Section shall be provided from every floor area that is intended for occupancy. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.1.10.(1) | Combustible Glazing in Exits | Combustible glazing is not permitted in wall or ceiling assemblies or in closures used to construct an exit enclosure. | obc2019_divb | Div B | 3.4.1.10.(1) | Combustible Glazing in Exits | Combustible glazing is not permitted in wall or ceiling assemblies or in closures used to construct an exit enclosure. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.1.2.(1) | Separation of Exits | Except as permitted by Sentence 3.4.1.2.(2), if more than one exit is required from a floor area, each exit shall be separate from every other exit leading from that floor area. | obc2019_divb | Div B | 3.4.1.2.(1) | 3.4.1.2. Separation of Exits | Except as permitted by Sentence (2), if more than one exit is required from a floor area, each exit shall be separate from every other exit leading from that floor area. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.1.2.(2) | Separation of Exits | If more than 2 exits are provided from a floor area, exits are permitted to converge in conformance with Sentence 3.4.3.1.(2), provided the cumulative capacity of the converging exits does not contribute more than 50% of the total required exit width for the floor area. | obc2019_divb | Div B | 3.4.1.2.(2) | 3.4.1.2. Separation of Exits | If more than two exits are provided from a floor area, exits are permitted to converge in conformance with Sentence 3.4.3.1.(2), provided the cumulative capacity of the converging exits does not contribute more than 50% of the total required exit width for the floor area. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.1.3.(1) | Access to Exits | Access to exits shall conform to part 3. | obc2019_divb | Div B | 3.4.1.3.(1) | 3.4.1.3. Access to Exits | Access to exits shall conform to Section 3.3. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.1.4.(1) | Types of Exit | Subject to the requirements of this Section, an exit from any floor area shall be one of the following, used singly or in combination: an exterior doorway, an exterior passageway, an exterior ramp, an exterior stairway, a fire escape (conforming to part 3.), a horizontal exit, an interior passageway, an interior ramp, or an interior stairway. | obc2019_divb | Div B | 3.4.1.4.(1) | 3.4.1.4. Types of Exit | Subject to the requirements of this Section, an exit from any floor area shall be one of the following, used singly or in combination: an exterior doorway, an exterior passageway, an exterior ramp, an exterior stairway, a fire escape (conforming to Subsection 3.4.7.), a horizontal exit, an interior passageway, an interior ramp, or an interior stairway. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.1.5.(1) | Exterior Exit Passageways | Access to an exterior exit passageway from a floor area shall be through exit doors at the floor level. | obc2019_divb | Div B | 3.4.1.5.(1) | 3.4.1.5. Exterior Exit Passageways | Access to an exterior exit passageway from a floor area shall be through exit doors at the floor level. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.1.6.(1) | Restricted Use of Horizontal Exits | Except as permitted by Sentence (2), horizontal exits shall not comprise more than one half of the required number of exits from any floor area. | obc2019_divb | Div B | 3.4.1.6.(1) | 3.4.1.6. Restricted Use of Horizontal Exits | Except as permitted by Sentence (2), horizontal exits shall not comprise more than one-half of the required number of exits from any floor area. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.1.6.(2) | Restricted Use of Horizontal Exits | In a hospital or nursing home with treatment, horizontal exits serving patients' sleeping rooms shall comprise not more than two thirds of the required number of exits from any floor area. (See Note A-3.4.1.6.(2).) | obc2019_divb | Div B | 3.4.1.6.(2) | 3.4.1.6. Restricted Use of Horizontal Exits | In a hospital or long-term care home, horizontal exits serving patients' or residents' sleeping rooms shall comprise not more than two-thirds of the required number of exits from any floor area. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.1.8.(1) | Transparent Doors and Panels | Glass and transparent panels in an exit shall conform to the appropriate requirements of Article 3.3.1.19. for glass and transparent panels in an access to exit. | obc2019_divb | Div B | 3.4.1.8.(1) | 3.4.1.8. Transparent Doors and Panels | Glass and transparent panels in an exit shall conform to the appropriate requirements of Article 3.3.1.18. for glass and transparent panels in an access to exit. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.1.9.(1) | Mirrors Near Exits | No mirror shall be placed in or adjacent to any exit in a manner that would confuse the direction of exit. | obc2019_divb | Div B | 3.4.1.9.(1) | Mirrors Near Exits | No mirror shall be placed in or adjacent to any exit in a manner that would confuse the direction of exit. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.2.1.(1) | Minimum Number of Exits | Except as permitted by Sentences 3.4.2.1.(2) to 3.4.2.1.(4), every floor area intended for occupancy shall be served by at least 2 exits . | obc2019_divb | Div B | 3.4.2.1.(1) | 3.4.2.1. Minimum Number of Exits | Except as permitted by Sentences (2) to (4) and (6), every floor area intended for occupancy shall be served by at least two exits. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.2.1.(2) | Minimum Number of Exits | A floor area in a building not more than 2 storeys in building height, is permitted to be served by one exit provided the total occupant load served by the exit is not more than 60, and (a) in a floor area that is not sprinklered throughout, the floor area and the travel distance are not more than the values in Table 3.4.2.1.-A, or (b) in a floor area that is sprinklered throughout (i) the travel distance is not more than 25 m, and (ii) the floor area is not more than the value in Table 3.4.2.1.-B. | obc2019_divb | Div B | 3.4.2.1.(2) | 3.4.2.1. Minimum Number of Exits | A floor area in a building not more than 2 storeys in building height, is permitted to be served by one exit provided the total occupant load served by the exit is not more than 60 and, (a) in a floor area that is not sprinklered, the floor area and the travel distance are not more than the values in Table 3.4.2.1.A., or (b) in a floor area that is sprinklered, (i) the travel distance is not more than 25 m, and (ii) the floor area is not more than the value in Table 3.4.2.1.B. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.2.1.(3) | Minimum Number of Exits | Except as permitted by Sentence 3.4.2.1.(4), if Sentence 3.4.2.1.(2) permits a single exit from a floor area classified as Group B or Group C occupancy, the exit shall be an exterior doorway not more than 1.5 m above adjacent ground level. | obc2019_divb | Div B | 3.4.2.1.(3) | 3.4.2.1. Minimum Number of Exits | Except as permitted by Sentence (4), if Sentence (2) permits a single exit from a floor area classified as Group B or Group C occupancy, the exit shall be an exterior doorway not more than 1.5 m above adjacent ground level. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.2.1.(4) | Minimum Number of Exits | The requirements of Sentences 3.4.2.1.(1) and 3.4.2.1.(2) are permitted to be waived for dwelling units that have an access to exit conforming to Sentences 3.3.4.4.(1) to 3.3.4.4.(4). | obc2019_divb | Div B | 3.4.2.1.(4) | 3.4.2.1. Minimum Number of Exits | The requirements of Sentences (1) and (2) are permitted to be waived for dwelling units having access to exit conforming to Sentences 3.3.4.4.(1) to (4) and (8). |  | Common Sentence | Yes | Exits
2015 | ON | NBC | Div B | 3.4.2.1.(5) | Minimum Number of Exits | Exits are not required directly from rooftop enclosures that are provided with access to exits in conformance with Sentences 3.3.1.3.(5) and 3.3.1.3.(6). | obc2019_divb | Div B | 3.4.2.1.(5) | 3.4.2.1. Minimum Number of Exits | Exits are not required directly from rooftop enclosures that are provided with access to exits in conformance with Sentences 3.3.1.3.(5) and (6). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.2.2.(2) | Means of Egress from Mezzanines | The means of egress from a mezzanine need not conform to Sentence 3.4.2.2.(1), provided (a) the mezzanine is not required to terminate at a vertical fire separation, as permitted in Sentence 3.2.8.2.(1), (b) the occupant load of the mezzanine is not more than 60, (c) the area of the mezzanine does not exceed the area limits stated in Table 3.4.2.2., and (d) the distance limits stated in Table 3.4.2.2. measured along the path of travel are not exceeded from any point on the mezzanine to (i) an egress door serving the space that the mezzanine overlooks, if the space is served by a single egress door, or (ii) the egress stairway leading to an access to exit in the space below if that space is required to be served by 2 or more egress doorways in conformance with Sentence 3.3.1.5.(1). | obc2019_divb | Div B | 3.4.2.2.(2) | 3.4.2.2. Mezzanine Exiting | A mezzanine need not conform to Sentence (1) provided Article 3.2.8.2. does not require it to terminate at a vertical fire separation. |  | Common Sentence | Yes | Mezzanines
2015 | ON | NBC | Div B | 3.4.2.21(1) | Minimum Number of Exits Means of Egress from Mezzanines | Except as permitted by Sentences (2) and (3), the space above a mezzanine shall be served by means of egress leading to exits accessible at the mezzanine level on the same basis as floor areas. | obc2019_divb | Div B | 3.4.2.2.(1) | 3.4.2.2. Mezzanine Exiting | Except as permitted by Sentences (2) to (4), a mezzanine shall be provided with exits on the same basis as required for floor areas by this Section. |  | Common Sentence | Yes | Exits
2015 | ON | NBC | Div B | 3.4.2.3.(1) | Distance between Exits | Except as provided in Sentence 3.4.2.3.(2), the least distance between 2 exits from a floor area shall be (a) one half the maximum diagonal dimension of the floor area, but need not be more than 9 m for a floor area having a public corridor, or (b) one half the maximum diagonal dimension of the floor area, but not less than 9 m for all other floor areas. | obc2019_divb | Div B | 3.4.2.3.(1) | 3.4.2.3. Distance Between Exits | Except as provided in Sentence (2), the least distance between two required exits from a floor area shall be, (a) one-half the maximum diagonal dimension of the floor area, but need not be more than 9 m for a floor area having a public corridor, or (b) one-half the maximum diagonal dimension of the floor area, but not less than 9 m for all other floor areas. |  | Common Sentence | Yes | Exits
2015 | ON | NBC | Div B | 3.4.2.3.(2) | Distance between Exits | Exits need not comply with Sentence 3.4.2.3.(1) where (a) the floor area is divided so that not less than one third of the floor area is on each side of a fire separation, and (b) it is necessary to pass through the fire separation to travel from one exit to another exit. | obc2019_divb | Div B | 3.4.2.3.(2) | 3.4.2.3. Distance Between Exits | Exits need not comply with Sentence (1) where, the floor area is divided so that not less than one-third of the floor area is on each side of the fire separation, and it is necessary to pass through the fire separation to travel from one exit to another exit. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.2.3.(3) | Distance between Exits | The minimum distance between exits referred to in Sentence 3.4.2.3.(1) shall be the shortest distance that smoke would have to travel between the exits, assuming that the smoke will not penetrate an intervening fire separation. | obc2019_divb | Div B | 3.4.2.3.(3) | 3.4.2.3. Distance Between Exits | The minimum distance between exits referred to in Sentence (1) shall be the shortest distance that smoke would have to travel between the exits, assuming that the smoke will not penetrate an intervening fire separation. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.2.3.(3) | Distance between Exits | The minimum distance between exits referred to in Sentence 3.4.2.3.(1) shall be the shortest distance that smoke would have to travel between the exits, assuming that the smoke will not penetrate an intervening fire separation. | obc2019_divb | Div B | 3.4.2.5.(3) | 3.4.2.5. Location of Exits | Exits shall be located and arranged so that they are clearly visible or their locations are clearly indicated and they are accessible at all times. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.2.3.(4) | Distance between Exits | The distance between 2 exterior discharges of exit stairs serving the same floor area shall be (a) not less than 9 m, or (b) not less than 6 m, where (i) the building is sprinklered throughout, and (ii) the 2 exterior discharges are located within 15 m of a street. | obc2019_divb | Div B | 3.4.2.3.(4) | 3.4.2.3. Distance Between Exits | The distance between exterior doors leading from two or more exit stairs serving the same floor area shall be, (a) not less than 9 m, or (b) not less than 6 m, where, (i) the building is sprinklered, and (ii) the exterior doors are located within 15 m of a street. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.2.4.(1) | Travel Distance | Except as permitted by Sentence 3.4.2.4.(2), for the purposes of this Subsection, travel distance means the distance from any point in the floor area to an exit measured along the path of travel to the exit. | obc2019_divb | Div B | 3.4.2.4.(1) | 3.4.2.4. Travel Distance | Except as permitted by Sentence (2), for the purposes of this Subsection, travel distance means the distance from any point in the floor area to an exit measured along the path of travel to the exit. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.2.4.(2) | Travel Distance | The travel distance from a suite or a room not within a suite is permitted to be measured from an egress door of the suite or room to the nearest exit, provided (a) the suite or room is separated from the remainder of the floor area by a fire separation (i) having a fire-resistance rating not less than 45 min in a floor area that is not sprinklered throughout, or (ii) which is not required to have a fire-resistance rating, in a floor area that is sprinklered throughout, and (b) the egress door opens onto (i) an exterior passageway, (ii) a corridor used by the public that is separated from the remainder of the floor area in conformance with the requirements in Article 3.3.1.4. for the separation of public corridors, or (iii) a public corridor that is separated from the remainder of the floor area in conformance with Article 3.3.1.4. (see Note A-3.1.8.1.(1)(b)). | obc2019_divb | Div B | 3.4.2.4.(2) | 3.4.2.4. Travel Distance | The travel distance from a suite or a room not within a suite is permitted to be measured from an egress door of the suite or room to the nearest exit provided, (a) the suite or room is separated from the remainder of the floor area by a fire separation, (i) having a fire-resistance rating not less than 45 min in a floor area that is not sprinklered, or (ii) that is not required to have a fire-resistance rating, in a floor area that is sprinklered, and (b) the egress door opens onto, (i) an exterior passageway, (ii) a corridor used by the public that is separated from the remainder of the floor area in conformance with the requirements in Article 3.3.1.4. for the separation of public corridors, or (iii) a public corridor that is separated from the remainder of the floor area in conformance with Article 3.3.1.4. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.2.4.(3) | Travel Distance | Travel distance to an exit shall be not more than 50 m from any point in a service space referred to in Sentence 3.2.1.1.(8). | obc2019_divb | Div B | 3.4.2.4.(3) | 3.4.2.4. Travel Distance | Travel distance to an exit shall be not more than 50 m from any point in a service space referred to in Sentence 3.2.1.1.(9). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.2.5.(1) | Location of Exits | Except as permitted by Sentences 3.4.2.5.(2) and 3.3.2.5.(6), if more than one exit is required from a floor area, the exits shall be located so that the travel distance to at least one exit shall be not more than (a) 25 m in a high-hazard industrial occupancy, (b) 40 m in a business and personal services occupancy, (c) 45 m in a floor area that contains an occupancy other than a high-hazard industrial occupancy, provided it is sprinklered throughout, (d) 105 m in any floor area, served by a public corridor, in which rooms and suites are not separated from the remainder of the floor area by a fire separation, provided (i) the public corridor is not less than 9 m wide, (ii) the ceiling height in the public corridor is not less than 4 m above all floor surfaces, (iii) the building is sprinklered throughout, and (iv) not more than one half of the required egress doorways from a room or suite open into the public corridor if the room or suite is required to have more than one egress doorway, (e) 60 m in any storage garage that conforms to the requirements of Article 3.2.2.90., and (f) 30 m in any floor area other than those referred to in Clauses 3.4.2.5.(1) to 3.4.2.5.(1). | obc2019_divb | Div B | 3.4.2.5.(1) | 3.4.2.5. Location of Exits | Except as permitted by Sentences (2), 3.2.8.4.(4) and 3.3.2.4.(13) to (16), if more than one exit is required from a floor area, the exits shall be located so that the travel distance to at least one exit shall be not more than, (a) 25 m in a high hazard industrial occupancy, (b) 40 m in a business and personal services occupancy, (c) 45 m in a floor area that contains an occupancy other than a high hazard industrial occupancy, provided it is sprinklered, (d) 105 m in any floor area, served by a public corridor, in which rooms and suites are not separated from the remainder of the floor area by a fire separation, provided, (i) the public corridor is not less than 9 m wide, (ii) the ceiling height in the public corridor is not less than 4 m above all floor surfaces, (iii) the building is sprinklered, and (iv) not more than one-half of the required egress doorways from a room or suite open into the public corridor if the room or suite is required to have more than one egress doorway, (e) 60 m in any storage garage that conforms to the requirements of Article 3.2.2.83., and |  | Common Sentence | Yes | Exits
2015 | ON | NBC | Div B | 3.4.2.5.(2) | Location of Exits | Except for a high-hazard industrial occupancy, Sentence 3.4.2.5.(1) need not apply if exits are placed along the perimeter of the floor area and are not more than 60 m apart, measured along the perimeter, provided each main aisle in the floor area leads directly to an exit. | obc2019_divb | Div B | 3.4.2.5.(2) | 3.4.2.5. Location of Exits | Except for a high hazard industrial occupancy, Sentence (1) need not apply if exits are placed along the perimeter of the floor area and are not more than 60 m apart, measured along the perimeter, provided each main aisle in the floor area leads directly to an exit. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.2.6.(1) | Principal Entrances | For the purposes of this Section, at least one door at every principal entrance to a building providing access from the exterior at ground level shall be designed in accordance with the requirements for exits. | obc2019_divb | Div B | 3.4.2.6.(1) | 3.4.2.6. Principal Entrance | For the purposes of this Section, at least one door at every principal entrance from ground level shall be designed in accordance with the requirements for exits. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.2.6.(2) | Principal Entrances | In a building that is not sprinklered throughout in accordance with Sentence 3.2.5.12.(1), the principal entrance serving a dance hall or a licensed beverage establishment with an occupant load more than 250 shall provide at least one half of the required exit width. | obc2019_divb | Div B | 3.4.2.6.(2) | 3.4.2.6. Principal Entrance | In a building that is not sprinklered in accordance with Sentence 3.2.5.13.(1), the principal entrance serving a dance hall or a licensed beverage establishment with an occupant load more than 250 shall provide at least one-half of the required exit width. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.3.1.(1) | Exit Width Based on Occupant Load | For the purpose of determining the aggregate width of exits, the occupant load of every room or floor area shall be determined in conformance with Subsection 3.1.17. | obc2019_divb | Div B | 3.4.3.1.(1) | 3.4.3.1. Exit Width Based on Occupant Load | For the purpose of determining the aggregate width of exits, the occupant load of every room or floor area shall be determined in conformance with Subsection 3.1.17. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.3.1.(2) | Exit Width Based on Occupant Load | Except as permitted by Sentence 3.4.3.2.(4), the required exit width shall be cumulative if 2 or more exits converge. | obc2019_divb | Div B | 3.4.3.1.(2) | 3.4.3.1. Exit Width Based on Occupant Load | Except as permitted by Sentence 3.4.3.2.(4), the required exit width shall be cumulative if two or more exits converge. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.3.2.(1) | Exit Width | Except as permitted by Sentence 3.4.3.2.(3), the minimum aggregate required width of exits serving floor areas intended for assembly occupancies, residential occupancies, business and personal services occupancies, mercantile occupancies, and industrial occupancies shall be determined by multiplying the occupant load of the area served by (a) 6.1 mm per person for ramps with a slope of not more than 1 in 8, doorways, corridors and passageways, (b) 8 mm per person for a stair consisting of steps whose rise is not more than 180 mm and whose run is not less than 280 mm, or (c) 9.2 mm per person for (i) ramps with a slope of more than 1 in 8, or (ii) stairs, other than stairs conforming to Sentence 3.4.3.2.(1). | obc2019_divb | Div B | 3.4.3.2.(1) | 3.4.3.2. Exit Width | Except as permitted by Sentence (3), the minimum aggregate required width of exits serving floor areas intended for assembly occupancies, residential occupancies, business and personal services occupancies, mercantile occupancies, and industrial occupancies shall be determined by multiplying the occupant load of the area served by, 6.1 mm per person for ramps with a slope of not more than 1 in 8, doorways, corridors and passageways, 8 mm per person for a stair consisting of steps whose rise is not more than 180 mm and whose run is not less than 280 mm, or 9.2 mm per person for, ramps with a slope of more than 1 in 8, or stairs, other than stairs conforming to Clause (b). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.3.2.(2) | Exit Width | The minimum aggregate width of exits serving floor areas intended for a care, treatment or detention occupancy shall be determined by multiplying the occupant load of the area served by 18.4 mm per person. | obc2019_divb | Div B | 3.4.3.2.(2) | 3.4.3.2. Exit Width | The minimum aggregate width of exits serving floor areas intended for a care, care and treatment or detention occupancy shall be determined by multiplying the occupant load of the area served by 18.4 mm per person. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.3.2.(3) | Exit Width | The minimum aggregate width of means of egress serving a Group A, Division 4 occupancy shall be determined by multiplying the occupant load of the area served by 1.8 mm per person for aisles, stairs other than exit stairs, and ramps and passageways in vomitories and exits, and 2.4 mm per person for exit stairs. | obc2019_divb | Div B | 3.4.3.2.(3) | 3.4.3.2. Exit Width | The minimum aggregate width of means of egress serving a Group A, Division 4 occupancy shall be determined by multiplying the occupant load of the area served by, 1.8 mm per person for, aisles, stairs other than exit stairs, and ramps and passageways in vomitories and exits, and 2.4 mm per person for exit stairs. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.3.2.(4) | Exit Width | Except as required by Sentences 3.4.3.2.(5) and 3.4.3.2.(6), the required exit width need not be cumulative in an exit serving 2 or more floor areas located one above the other. | obc2019_divb | Div B | 3.4.3.2.(4) | 3.4.3.2. Exit Width | Except as required by Sentence (5), the required exit width need not be cumulative in an exit serving two or more floor areas located one above the other. |  | Common Sentence | Yes | Exits
2015 | ON | NBC | Div B | 3.4.3.2.(5) | Exit Width | The required exit width for an exit stair in an assembly hall or theatre serving more than one balcony level shall conform to Sentence 3.4.3.2.(6). | obc2019_divb | Div B | 3.4.3.2.(5) | 3.4.3.2. Exit Width | The required exit width for an exit stair in an assembly hall or theatre serving more than one balcony level shall conform to the appropriate requirements for stairs serving interconnected floor spaces in Article 3.2.8.4. |  | Common Sentence | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B | 3.4.3.2.(6) | Exit Width | The required exit width for exit stairs that serve interconnected floor space (a) the stairs provide not less than 0.3 m2 of area of treads and landings for each occupant of the interconnected floor space (see Note A-3.4.3.2.(6)(a)), or (b) protected floor spaces conforming to Article 3.2.8.5. are provided at each floor level and the protected floor space on a floor level has not less than 0.5 m2 of space for each occupant of that floor level of the interconnected floor space. (See Note A-3.4.3.2.(6).) | obc2019_divb | Div B | 3.2.8.4.(6) | 3.2.8.4. Exits | Except as provided in Sentences (7) and (8), portions of an interconnected floor space that have floor levels more than 18 m above grade shall be served by exits that provide at least 0.3 m2 of area of treads, landings and floor surface for each occupant of such portions of an interconnected floor space. (See Appendix A.) |  | Common Sentence | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B | 3.4.3.2.(6) | Exit Width | The required exit width for exit stairs that serve interconnected floor space designed in accordance with Articles 3.28.3. to 3.2.8.8. shall be cumulative, unless (a) the stairs provide not less than 0.3 m2 of area of treads and landings for each occupant of the interconnected floor space (see Note A-3.4.3.2.(6)(a)), or (b) protected floor spaces conforming to Article 3.2.8.5. are provided at each floor level and the protected floor space on a floor level has not less than 0.5 m2 of space for each occupant of that floor level of the interconnected floor space. (See Note A-3.4.3.2.(6).) | obc2019_divb | Div B | 3.2.8.4.(8) | 3.2.8.4. Exits | The requirements of Sentence (6) need not be applied where the exit stairs that serve interconnected floor spaces are designed so that the required width of each stair is cumulative. |  | Common Sentence | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B | 3.4.3.2.(7) | Exit Width | If more than one exit is required, every exit shall be considered as contributing not more than one half of the required exit width. | obc2019_divb | Div B | 3.4.3.2.(6) | 3.4.3.2. Exit Width | If more than one exit is required, every exit shall be considered as contributing not more than one-half of the required exit width. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.3.3.(1) | Exit Width Reduction | Except as permitted by Sentences 3.4.3.3.(2) and 3.4.3.3.(4), no fixture, turnstile or construction shall project into or be fixed within the required width of an exit. | obc2019_divb | Div B | 3.4.3.4.(1) | 3.4.3.4. Exit Width Reduction (See Appendix A.) | Except as permitted by Sentences (2) to (4), no fixture, turnstile or construction shall project into or be fixed within the required width of an exit. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.3.3.(2) | Exit Width Reduction | Swinging doors in their swing shall not reduce the required width of exit stairs or landings to less than 750 mm or reduce the width of an exit passageway to less than the minimum required width. | obc2019_divb | Div B | 3.4.3.2.(3) | 3.4.3.2. Exit Width | The minimum aggregate width of means of egress serving a Group A, Division 4 occupancy shall be determined by multiplying the occupant load of the area served by, 1.8 mm per person for, aisles, stairs other than exit stairs, and ramps and passageways in vomitories and exits, and 2.4 mm per person for exit stairs. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.3.3.(3) | Exit Width Reduction | Doors shall be installed so that, when open, they do not diminish nor obstruct the required width of the exit. | obc2019_divb | Div B | 3.4.3.4.(2) | 3.4.3.4. Exit Width Reduction (See Appendix A.) | Exit doors shall be hung so that, when open, they shall neither diminish nor obstruct the required width of the exit by more than 50 mm for each door leaf. |  | Common Sentence | Yes | Exits
2015 | ON | NBC | Div B | 3.4.3.3.(4) | Exit Width Reduction | Handrails and construction below handrails, including handrail supports and stair stringers, shall not project more than 100 mm into the required width of a means of egress. | obc2019_divb | Div B | 3.4.3.4.(4) | 3.4.3.4. Exit Width Reduction (See Appendix A.) | Handrails and construction below handrails, including handrail supports and stair stringers, are permitted to project into the required width of means of egress but the projections shall be not more than 100 mm on each side of the required width. |  | Common Sentence | Yes | Exits
2015 | ON | NBC | Div B | 3.4.3.4.(1) | Headroom Clearance | Except as permitted by Sentences 3.4.3.4.(4) and 3.4.3.4.(5), every exit shall have a clear height over the clear width of the exit of not less than 2050 mm. | obc2019_divb | Div B | 3.4.3.5.(1) | 3.4.3.5. Headroom Clearance (See Appendix A.) | Except as provided by Sentences (2), (4) and (5), every exit shall have a clear height over the clear width of the exit of not less than 2 100 mm. |  | Common Sentence | Yes | Exits
2015 | ON | NBC | Div B | 3.4.3.4.(2) | Headroom Clearance | The clear height of stairways shall be measured vertically over the clear width of the stairway, from the straight line tangent to the tread and landing nosings to the lowest element above. (See Note A-9.8.7.4.) | obc2019_divb | Div B | 3.4.3.5.(2) | 3.4.3.5. Headroom Clearance (See Appendix A.) | The clear height of stairways shall be measured vertically, over the clear width of the stairway, from a straight line tangent to the tread and landing nosings to the lowest point above, and shall not be less than 2 050 mm. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.3.4.(3) | Headroom Clearance | The clear height of landings shall be measured within the clear width of the landing vertically to the lowest element above. | obc2019_divb | Div B | 3.4.3.5.(3) | 3.4.3.5. Headroom Clearance (See Appendix A.) | The clear height of landings shall be measured vertically, over the clear width of the landing, to the lowest point above. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.3.4.(4) | Headroom Clearance | Except as permitted bySentence (5), the headroom clearance for doorways shall be not less than 2 030 mm. | obc2019_divb | Div B | 3.4.3.5.(4) | 3.4.3.5. Headroom Clearance (See Appendix A.) | Except as permitted by Sentence (5), the clear height of doorways shall not be less than 2 030 mm. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.3.4.(5) | Headroom Clearance | No door closer or other device shall be installed so as to reduce the headroom clearance of a doorway to less than 1980 mm. | obc2019_divb | Div B | 3.4.3.5.(5) | 3.4.3.5. Headroom Clearance (See Appendix A.) | No door closer or other device shall be installed so as to reduce the clear height of a doorway to less than 1 980 mm. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.4.1.(1) | Fire-Resistance Rating of Exit Separations | Except as permitted by Sentences 3.4.4.1.(2), Sentence 3.3.5.4.(3), Sentence 3.4.4.2.(2) and 3.4.4.3.(1), every exit shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than that required by part 3., but not less than 45 min, (a) for the floor assembly above the storey, or (b) the floor assembly below the storey, if there is no floor assembly above. | obc2019_divb | Div B | 3.4.4.1.(1) | 3.4.4.1. Fire-Resistance Rating of Exit Separations | Except as provided by Sentences (2), (3) and (5) and Sentences 3.3.5.4.(3), 3.4.4.2.(2), 3.4.4.3.(1) and 3.13.3.1.(3), every exit shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than that required by Subsection 3.2.2., but not less than 45 min, for, (a) the floor assembly above the storey, or (b) the floor assembly below the storey, if there is no floor assembly above. |  | Common Sentence | Yes | Exits
2015 | ON | NBC | Div B | 3.4.4.1.(2) | Fire-Resistance Rating of Exit Separations | The fire-resistance rating of the fire separation referred to in Sentence 3.4.4.1.(1) need not be more than 2 h. | obc2019_divb | Div B | 3.4.4.1.(2) | 3.4.4.1. Fire-Resistance Rating of Exit Separations | The fire-resistance rating of the fire separation referred to in Sentence (1) need not be more than 2 h. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.4.1.(3) | Fire-Resistance Rating of Exit Separations | If an exit stair in an assembly hall or theatre serves more than one balcony level, the exit stair shall be separated from the remainder of the building in conformance with Sentence 3.4.4.1.(1). | obc2019_divb | Div B | 3.4.4.1.(4) | 3.4.4.1. Fire-Resistance Rating of Exit Separations | If an exit stair in an assembly hall or theatre serves more than one balcony level, the exit stair shall be separated from the remainder of the building in conformance with Sentence (1). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.4.2.(1) | Exits through Lobbies | Except as permitted by Sentence 3.4.4.2.(2), no exit from a floor area above or below the first storey shall lead through a lobby. | obc2019_divb | Div B | 3.4.4.2.(1) | 3.4.4.2. Exits Through Lobbies | Except as permitted by Sentence (2), no exit from a floor area above or below the first storey shall lead through a lobby. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.4.2.(2) | Exits through Lobbies | Not more than one exit from a floor area is permitted to lead through a lobby, provided (a) the lobby floor is not more than 4.5 m above grade, (b) the path of travel through the lobby to the outdoors is not more than 15 m, (c) the adjacent rooms or premises having direct access to the lobby do not contain a care, residential or industrial occupancy, (d) the lobby is not located within an interconnected floor space other than as described in Sentence 3.2.8.2.(6), (e) the lobby conforms to the requirements for exits, except that (i) rooms other than service rooms and storage rooms are permitted to open onto the lobby, (ii) the fire separation between the lobby and a room used for the sole purpose of control and supervision of the building need not have a fire-resistance rating, (iii) the fire separation between the lobby and adjacent occupancies that are permitted to open onto the lobby need not have a fire-resistance rating provided the lobby and adjacent occupancies are sprinklered, and (iv) passenger elevators are permitted to open onto the lobby, provided the elevator doors are designed to remain closed except while loading and unloading passengers, and (f) a fire separation, constructed in accordance with Sentence 3.4.4.1.(1), is maintained between the lobby and any exit permitted by this Sentence to lead through the lobby. | obc2019_divb | Div B | 3.4.4.2.(2) | 3.4.4.2. Exits Through Lobbies | Not more than one exit from a floor area is permitted to lead through a lobby provided, (a) the lobby floor is not more than 4.5 m above grade, (b) the path of travel through the lobby to the outdoors is not more than 15 m, (c) the adjacent rooms or premises having direct access to the lobby do not contain a residential occupancy or an industrial occupancy, except that dwelling units may open directly onto the lobby where, (i) from the interior of the exit stair that opens onto the lobby there is alternate means of egress not leading through the lobby and such means of egress is entirely within the same storey as the lobby, or (ii) the floor area is sprinklered, (d) except as required by Clause (g), the lobby is not located within an interconnected floor space other than as described in Sentence 3.2.8.2.(6), (e) the lobby conforms to the requirements for exits, except that, (i) rooms other than service rooms and storage rooms are permitted to open onto the lobby, (ii) the fire separation between the lobby and a room used for the sole purpose of control and supervision of the building need not have a fire-resistance rating, (iii) the fire separation between the lobby and adjacent occupancies that are permitted to open onto the lobby need not have a fire-resistance rating provided the lobby and adjacent occupancies are sprinklered, and (iv) passenger elevator entrances are permitted to open onto the lobby provided the elevator entrance doors are designed to remain closed except while loading and unloading, (f) a fire separation, constructed in accordance with Sentence 3.4.4.1.(1), is maintained between the lobby and any exit permitted by this Sentence to lead through the lobby, and (g) that if the exit serves a hotel, the lobby is not located within an interconnected floor space. |  | Common Sentence | Yes | Exits
2015 | ON | NBC | Div B | 3.4.4.3.(1) | Exterior Passageway Exceptions | The requirements of Sentences 3.4.4.1.(1) and 3.2.3.13.(1) and 3.2.3.13.(3) do not apply to an exterior exit passageway provided not less than 50% of the exterior side is open to the outdoors, and an exit stair is provided at each end of the passageway. | obc2019_divb | Div B | 3.4.4.3.(1) | 3.4.4.3. Exterior Passageway Exceptions | The requirements of Sentences 3.4.4.1.(1) and 3.2.3.13.(1) and (3) do not apply to an exterior exit passageway provided, not less than 50% of the exterior side is open to the outdoors, and an exit stair is provided at each end of the passageway. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.4.4.(1) | Integrity of Exits | A fire separation that separates an exit from the remainder of the building shall have no openings except for (a) standpipe and sprinkler piping, (b) electrical wires and cables, totally enclosed noncombustible raceways and noncombustible piping that serve only the exit, (c) openings required by the provisions of Subsection 3.2.6, (d) exit doorways, and (e) wired glass and glass block permitted by Article 3.1.8.16. | obc2019_divb | Div B | 3.4.4.4.(1) | 3.4.4.4. Integrity of Exits | A fire separation that separates an exit from the remainder of the building shall have no openings except for, (a) standpipe and sprinkler piping, (b) electrical wires and cables, totally enclosed noncombustible raceways and noncombustible piping that serve only the exit, (c) openings required by the provisions of Subsection 3.2.6., (d) exit doorways, (e) wired glass and glass block permitted by Article 3.1.8.14., and (f) a sprinkler protected glazed wall assembly conforming to Article 3.1.8.18. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.4.4.4.(2) | Integrity of Exits | Exits within scissors stairs and other contiguous exit stairways shall be separated from each other by a smoke-tight fire separation having a fire-resistance rating not less than that required for the floor assembly through which they pass. | obc2019_divb | Div B | 3.4.4.4.(2) | 3.4.4.4. Integrity of Exits | Exits within scissors stairs and other contiguous exit stairways shall be separated from each other by a smoke-tight fire separation having a fire-resistance rating not less than that required for the floor assembly through which they pass. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.4.4.(3) | Integrity of Exits | Fire separations separating contiguous stairs described in Sentence 3.4.4.4.(2) shall not be pierced by doorways, ductwork, piping or any other openings that affect the continuity of the separation. | obc2019_divb | Div B | 3.4.4.4.(3) | 3.4.4.4. Integrity of Exits | Fire separations separating contiguous stairs described in Sentence (2) shall not be pierced by doorways, ductwork, piping or any other openings that affect the continuity of the separation. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.4.4.(4) | Integrity of Exits | A fuel-fired appliance shall not be installed in an exit. | obc2019_divb | Div B | 3.4.4.4.(4) | 3.4.4.4. Integrity of Exits | A fuel-fired appliance shall not be installed in an exit. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.4.4.(5) | Integrity of Exits | An exit shall not be used as a plenum for a heating, ventilating or air-conditioning system. | obc2019_divb | Div B | 3.4.4.4.(5) | 3.4.4.4. Integrity of Exits | An exit shall not be used as a plenum for a heating, ventilating or air-conditioning system. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.4.4.(6) | Integrity of Exits | An exit shall be designed for no purpose other than for exiting, except that an exit is permitted also to be designed to serve as an access to a floor area. | obc2019_divb | Div B | 3.4.4.4.(6) | 3.4.4.4. Integrity of Exits | An exit shall be designed for no purpose other than for exiting, except that an exit is permitted also to be designed to serve as an access to a floor area. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.4.4.(7) | Integrity of Exits | A service room shall not open directly into an exit. | obc2019_divb | Div B | 3.4.4.4.(7) | 3.4.4.4. Integrity of Exits | A service room shall not open directly into an exit. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.4.4.(8) | Integrity of Exits | Storage rooms, washrooms, toilet rooms, laundry rooms and similar ancillary rooms shall not open directly into an exit. | obc2019_divb | Div B | 3.4.4.4.(8) | 3.4.4.4. Integrity of Exits | Storage rooms, washrooms, toilet rooms, laundry rooms and similar ancillary rooms shall not open directly into an exit. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.4.4.(9) | Integrity of Exits | Service spaces referred to in Sentence 3.2.1.1.(8) shall not open directly into an exit. | obc2019_divb | Div B | 3.4.4.4.(9) | 3.4.4.4. Integrity of Exits | Service spaces referred to in Sentence 3.2.1.1.(9) shall not open directly into an exit. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.5.1.(1) | Exit Signs | Every exit door shall have an exit sign placed over or adjacent to it if the exit serves (a) a building more than 2 storeys in building height, (b) a building having an occupant load of more than 150, or (c) a room or floor area that has a fire escape as part of a required means of egress. | obc2019_divb | Div B | 3.4.5.1.(1) | 3.4.5.1. Exit Signage | Except as provided by Sentences (9) and (10), every exit door shall have an exit sign placed over or adjacent to it if the exit serves, (a) a building more than 2 storeys in building height, (b) a building having an occupant load of more than 150, or (c) a room or floor area that has a fire escape as part of a required means of egress. |  | Common Sentence | Yes | Exits
2015 | ON | NBC | Div B | 3.4.5.1.(2) | Exit Signs | Every exit sign shall (a) be visible on approach to the exit, (b) consist of a green and white or lightly tinted graphical symbol meeting the colour specifications referred to in ISO 3864-1:2011 Graphical symbols “ Safety colours and safety signs “ Part 1: Design principles for safety signs and safety markings and (c) conform to ISO 7010:2011 Graphical symbols “ Safety colours and safety signs “ Registered safety signs for the following symbols (see Note A-3.4.5.1.(2)(c)): (i) E001 emergency exit left, (ii) E002 emergency exit right, (iii) E005 90-degree directional arrow, and (iv) E006 45-degree directional arrow. | obc2019_divb | Div B | 3.4.5.1.(2) | 3.4.5.1. Exit Signage | Except as provided by Sentence (7), every exit sign shall, (a) be visible on approach to the exit, (b) consist of a green pictogram and white graphic symbol meeting the visibility specifications referred to in ISO 3864 1, "Graphical Symbols ‚" Safety Colours and Safety Signs â‚¬" Part 1: Design Principles for Safety Signs and Safety Markings", and (c) conform to ISO 7010, "Graphical Symbols - Safety Colours and Safety Signs - Registered Safety Signs" for the following symbols: (i) E001 emergency exit left, (ii) E002 emergency exit right, (iii) E005 90-degree directional arrow, and (iv) E006 45-degree directional arrow. |  | Common Sentence | Yes | Exits
2015 | ON | NBC | Div B | 3.4.5.1.(3) | Exit Signs | Internally illuminated exit signs shall be continuously illuminated and (a) where illumination of the sign is powered by an electrical circuit, be constructed in conformance with CSA C22.2 No. 141-10 Emergency Lighting Equipment or (b) where illumination of the sign is not powered by an electrical circuit, be constructed in conformance with ULC CAN/ULC-S572-17 Photoluminescent and Self-Luminous Exit Signs and Path Marking Systems | obc2019_divb | Div B | 3.4.5.1.(3) | 3.4.5.1. Exit Signage | Internally illuminated exit signs shall, (a) be continuously illuminated, and (b) where illumination of the sign is powered by an electrical circuit, be constructed in conformance with CSA C22.2 No. 141, "Emergency Lighting Equipment". |  | Common Sentence | Yes | Exits
2015 | ON | NBC | Div B | 3.4.5.1.(3) | Exit Signs | Internally illuminated exit signs shall be continuously illuminated and (a) where illumination of the sign is powered by an electrical circuit, be constructed in conformance with CSA C22.2 No. 141-10 Emergency Lighting Equipment or (b) where illumination of the sign is not powered by an electrical circuit, be constructed in conformance with ULC CAN/ULC-S572-17 Photoluminescent and Self-Luminous Exit Signs and Path Marking Systems | obc2019_divb | Div B | 3.4.5.1.(5) | 3.4.5.1. Exit Signage | Photoluminescent and self-luminous exit signs shall, (a) conform to CAN/ULC-S572, “Photoluminescent and Self-Luminous Signs and Path Marking Systems”, (b) be labelled in accordance with the time duration for which they have been tested and listed, (c) be so installed that upon failure of the regular power they will continue to be illuminated for the applicable time duration specified in Clause 3.2.7.4.(1)(b), and (d) be continuously illuminated if reliant on an external energy source to energize the reflective coating of the sign. |  | Common Sentence | Yes | Exits
2015 | ON | NBC | Div B | 3.4.5.1.(4) | Exit Signs | Externally illuminated exit signs shall be continuously illuminated and be constructed in conformance with ULC CAN/ULC-S572-17 Photoluminescent and Self-Luminous Exit Signs and Path Marking Systems (See Note A-3.4.5.1.(4).) The circuitry serving lighting for externally and internally illuminated exit signs shall serve no equipment other than emergency equipment, and be connected to an emergency power supply as described in Article 3.2.7.4. | obc2019_divb | Div B | 3.4.5.1.(4) | 3.4.5.1. Exit Signage | Externally illuminated exit signs shall be continuously illuminated by a light fixture supplied by an electrical circuit. |  | Common Sentence | Yes | Exits
2015 | ON | NBC | Div B | 3.4.5.1.(5) | Exit Signs | The circuitry serving lighting for externally and internally illuminated exit signs shall (a) serve no equipment other than emergency equipment, and (b) be connected to an emergency power supply as described in Article 3.2.7.4. | obc2019_divb | Div B | 3.4.5.1.(6) | 3.4.5.1. Exit Signage | If illumination of an exit sign is provided from an electrical circuit, that circuit shall, (a) serve no equipment other than emergency lighting in the area where exit signs are installed, and (b) be connected to an emergency power supply as described in Sentence 3.2.7.4.(1). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.5.1.(6) | Exit Signs | Where no exit is visible from a public corridor, from a corridor used by the public in a Group A or B major occupancy, or from principal routes serving an open floor area having an occupant load of more than 150, an exit sign conforming to Clauses 3.4.5.1.(2)(b) and 3.4.5.1.(2)(c) with an arrow or pointer indicating the direction of egress shall be provided. | obc2019_divb | Div B | 3.4.5.1.(7) | 3.4.5.1. Exit Signage | Where no exit is visible from a public corridor, from a corridor used by the public in a Group A or B major occupancy or from principal routes serving an open floor area having an occupant load of more than 150, an exit sign conforming to Clauses (2)(b) and (c) with an arrow or other indicator pointing at the direction of egress shall be provided. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.5.1.(7) | Exit Signs | Except for egress doorways described in Sentence 3.3.2.4.(4), an exit sign conforming to Sentences 3.4.5.1.(2) to 3.4.5.1.(5) shall be placed over or adjacent to every egress doorway from rooms with an occupant load of more than 60 in Group A, Division 1 occupancies, dance halls, licensed beverage establishments, and other similar occupancies that, when occupied, have lighting levels below that which would provide easy identification of the egress doorway. | obc2019_divb | Div B | 3.4.5.1.(8) | 3.4.5.1. Exit Signage | Except for egress doorways described in Sentence 3.3.2.3.(4), an exit sign conforming to Sentences (2) to (6) shall be placed over or adjacent to every egress doorway from rooms with an occupant load more than 60 in Group A, Division 1 occupancies, dance halls, licensed beverage establishments and other similar occupancies that, when occupied, have lighting levels below the level that would provide easy identification of the egress doorway. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.5.2.(1) | Signs for Stairs and Ramps at Exit Level | In a building more than 2 storeys in building height, any part of an exit ramp or stairway that continues up or down past the lowest exit level shall have a posted sign clearly indicating that it does not lead to an exit. | obc2019_divb | Div B | 3.4.5.2.(1) | 3.4.5.2. Signs Within Exit Facilities | In a building more than 2 storeys in building height, any part of an exit ramp or stair that continues up or down past the lowest exit level shall be clearly marked by a sign indicating that it does not lead to an exit. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.1.(1) | Slip Resistance of Ramps and Stairs | The surfaces of ramps, and landings and treads shall have a finish that is slip resistant, and if accessible to the public, shall have either a colour contrast or a distinctive pattern to demarcate the leading edge of the tread and the leading edge of the landing, as well as the beginning and end of a ramp. | obc2019_divb | Div B | 3.4.6.1.(1) | 3.4.6.1. Surface Finish of Ramps and Stairs | The surfaces of ramps, landings and treads shall, have a finish that is slip-resistant, and if accessible to the public, have a colour contrast or a distinctive visual pattern to demarcate, the leading edge of the tread, the leading edge of the landing, and the beginning and end of a ramp. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.1.(2) | Slip Resistance of Ramps and Stairs | Treads and landings of exterior exit stairs more than 10 m high shall be designed to be free of ice and snow accumulations. | obc2019_divb | Div B | 3.4.6.1.(3) | 3.4.6.1. Surface Finish of Ramps and Stairs | Treads and landings of exterior exit stairs shall be designed to be free of ice and snow accumulations if the stairs, (a) are more than 10 m high, or (b) serve a hotel. |  | Common Sentence | Yes | Hotels
2015 | ON | NBC | Div B | 3.4.6.10.(1) | Horizontal Exits | The floor area on each side of a horizontal exit shall be sufficient to accommodate the occupants of both floor areas, allowing not less than 0.5 m2 of clear floor space per person, except that 1.5 m2 shall be provided for each person in a wheelchair and 2.5 m2 for each bedridden patient. | obc2019_divb | Div B | 3.4.6.10.(1) | 3.4.6.10. Horizontal Exits | Except in an elementary or secondary school that is subdivided by a firewall, the floor area on each side of a horizontal exit shall be sufficient to accommodate the occupants of both floor areas, allowing not less than 0.5 m2 of clear floor space per person, except that 1.5 m2 shall be provided for each person in a wheelchair and 2.5 m2 for each patient in bed. |  | Common Sentence | Yes | Schools
2015 | ON | NBC | Div B | 3.4.6.10.(2) | Horizontal Exits | If vestibules, enclosed balconies or bridges are used as parts of a horizontal exit, their clear width shall be not less than that of the exit doorways opening into them, except that handrails are not permitted to project into this clear width more than 100 mm. | obc2019_divb | Div B | 3.4.6.10.(2) | 3.4.6.10. Horizontal Exits | If vestibules, enclosed balconies or bridges are used as parts of a horizontal exit, their clear width shall be not less than that of the exit doorways opening into them, except that handrails are not permitted to project into this clear width more than 100 mm. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.10.(3) | Horizontal Exits | In a horizontal exit where there is a difference in level between the connected floor areas, slopes not more than those specified for ramps in Article 3.4.6.7. are permitted to be used. | obc2019_divb | Div B | 3.4.6.10.(3) | 3.4.6.10. Horizontal Exits | In a horizontal exit where there is a difference in level between the connected floor areas, slopes not more than those specified for ramps in Article 3.4.6.7. are permitted to be used. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.10.(4) | Horizontal Exits | No stairs or steps shall be used in a horizontal exit. | obc2019_divb | Div B | 3.4.6.10.(4) | 3.4.6.10. Horizontal Exits | No stairs or steps shall be used at a horizontal exit. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.10.(5) | Horizontal Exits | If 2 doors are provided in a horizontal exit that comprises a part of the required number of exits from the floor areas on both sides of the exit (a) the doors shall be mounted adjacent to each other with the door on the right side in the direction of travel through the horizontal exit swinging in the direction of travel through the horizontal exit, and (b) signs shall be provided on each side of the horizontal exit to indicate the door that swings in the direction of travel from that side. | obc2019_divb | Div B | 3.4.6.10.(5) | 3.4.6.10. Horizontal Exits | If two doors are provided in a horizontal exit that comprises a part of the required number of exits from the floor areas on both sides of the exit, (a) the doors shall be mounted adjacent to each other with the door on the right side in the direction of travel through the horizontal exit swinging in the direction of travel through the horizontal exit, and (b) signs shall be provided on each side of the horizontal exit to indicate the door that swings in the direction of travel from that side. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.10.(6) | Horizontal Exits | If a horizontal exit utilizes bridges between buildings or outside balconies, the bridges or balconies shall conform to Article 3.2.3.19. | obc2019_divb | Div B | 3.4.6.10.(6) | 3.4.6.10. Horizontal Exits | If a horizontal exit utilizes bridges between buildings or outside balconies, the bridges or balconies shall conform to Article 3.2.3.19. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.11.(2) | Doors | Except as provided in Sentence (3) and where doorways are used to confine the spillage of flammable liquids within a service room or within a room in an industrial occupancy, a threshold for a doorway in an exit shall be not more than 13 mm higher than the surrounding finished floor surface. | obc2019_divb | Div B | 3.4.6.11.(1) | 3.4.6.11. Doors | Except as provided in Sentence (2) and where a threshold is used to contain spillage, a threshold for a doorway in an exit shall be not more than 13 mm higher than the surrounding finished floor surface. |  | Common Sentence | Yes | Exits
2015 | ON | NBC | Div B | 3.4.6.11.(3) | Doors | Except for doors providing access to ground level as required by Sentence 3.3.1.7.(1) and 3.3.1.7.(1), an exit door is permitted to open onto not more than one step which shall be not more than 150 mm high where there is a risk of blockage by ice or snow. | obc2019_divb | Div B | 3.4.6.11.(2) | 3.4.6.11. Doors | No exit door shall open directly onto a step except that, if there is danger of blockage from ice or snow, an exit door is permitted to open onto not more than one step which shall be not more than 150 mm high. |  | Common Sentence | Yes | Exits
2015 | ON | NBC | Div B | 3.4.6.11.(4) | Doors | Exit doors shall be clearly identifiable. (See Note A-3.4.6.11.(4).) | obc2019_divb | Div B | 3.4.6.11.(3) | 3.4.6.11. Doors | Exit doors shall be clearly identifiable. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.11.(5) | Doors | No door leaf in an exit doorway with more than one leaf shall be less than 610 mm wide. | obc2019_divb | Div B | 3.4.6.11.(4) | 3.4.6.11. Doors | No door leaf in an exit doorway with more than one leaf shall be less than 600 mm wide. |  | Common Sentence | Yes | Exits
2015 | ON | NBC | Div B | 3.4.6.11.(6) | Doors | Where an exit door leading directly to the outside is subject to being obstructed by parked vehicles or storage because of its location, a visible sign or a physical barrier prohibiting such obstructions shall be installed on the exterior side of the door. | obc2019_divb | Div B | 3.4.6.11.(5) | 3.4.6.11. Doors | Where an exit door leading directly to the outside is subject to being obstructed by a parked vehicle or storage because of its location, a visible sign prohibiting such obstructions shall be permanently mounted on the exterior side of the door. |  | Common Sentence | Yes | Exits
2015 | ON | NBC | Div B | 3.4.6.12.(1) | Direction of Door Swing | Except for doors serving a single dwelling unit and except as permitted by Sentence 3.4.6.12.(2) and Article 3.4.6.14., every exit door shall (a) open in the direction of exit travel, and (b) swing on its vertical axis. | obc2019_divb | Div B | 3.4.6.12.(1) | 3.4.6.12. Direction of Door Swing | Except as permitted by Sentences (2) to (4) and Article 3.4.6.14., every exit door shall, (a) open in the direction of exit travel, and (b) swing on its vertical axis. |  | Common Sentence | Yes | Exits
2015 | ON | NBC | Div B | 3.4.6.12.(2) | Direction of Door Swing | Exit doors need not conform to Sentence 3.4.6.12.(1), where (a) they serve storage garages serving not more than one dwelling unit, (b) they serve accessory buildings serving not more than one dwelling unit, (c) they (i) serve storage suites not more than 28 m2 in area that are on the first storey in warehousing buildings, and (ii) open directly outdoors at ground level, or (d) they serve individual self-service storage units referred to in part 3. | obc2019_divb | Div B | 3.4.6.12.(4) | 3.4.6.12. Direction of Door Swing | Exit doors need not conform to Sentence (1) where they serve, (a) storage garages serving not more than one dwelling unit, (b) accessory buildings serving not more than one dwelling unit, or (c) storage suites not more than 28 m2 in area that are on the first storey of a warehouse and open directly outdoors at ground level. |  | Common Sentence | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B | 3.4.6.13.(1) | Self-closing Devices | An exit door that is normally required to be kept closed (a) shall be provided with a self-closing mechanism, and (b) shall never be secured in an open position except as permitted by Sentence 3.1.8.14.(1). | obc2019_divb | Div B | 3.4.6.13.(1) | 3.4.6.13. Self-Closing Devices | An exit door that is normally required to be kept closed, (a) shall be provided with a self-closing mechanism, and (b) shall not be secured in an open position except as permitted by Sentence 3.1.8.12.(1). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.14.(1) | Sliding Doors | Except as permitted by Sentences 3.4.6.14.(2) and 3.4.6.12.(2), an exit door leading directly to outdoors at ground level is permitted to be a sliding door provided it conforms to Sentence 3.3.1.12.(1). | obc2019_divb | Div B | 3.4.6.14.(1) | 3.4.6.14. Sliding Doors | Except as permitted by Sentences (2) and 3.4.6.12.(4), an exit door leading directly to outdoors at ground level is permitted to be a sliding door provided it is released in conformance with Sentence 3.3.1.11.(1). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.14.(2) | Sliding Doors | An exit door serving a Group B, Division 1 occupancy, or an impeded egress zone in other occupancies, is permitted to be a sliding door that does not conform to Sentence 3.3.1.12.(1) provided it is designed to be released in conformance with Article 3.3.1.13. | obc2019_divb | Div B | 3.4.6.14.(2) | 3.4.6.14. Sliding Doors | An exit door serving a Group B, Division 1 occupancy, or an impeded egress zone in other occupancies, is permitted to be a sliding door that does not conform to Sentence 3.3.1.11.(1) provided it is designed to be released in conformance with Article 3.3.1.12. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.15.(1) | Revolving Doors | Except as permitted by Sentence 3.4.6.15.(3), a revolving door, if used, shall (a) be collapsible, (b) have hinged doors providing equivalent exiting capacity located adjacent to it, (c) be used as an exit from the ground floor level only, (d) not be used at the foot of any stairway, and (e) have all glass in door leaves and enclosure panels conforming to (i) CAN/CGSB-12.1-M90 Tempered or Laminated Safety Glass or (ii) CAN/CGSB-12.11-M90 Wired Safety Glass | obc2019_divb | Div B | 3.4.6.15.(1) | 3.4.6.15. Revolving Doors | Except as permitted by Sentence (3), a revolving door, if used, shall, (a) be collapsible, (b) have hinged doors providing equivalent exiting capacity located adjacent to it, (c) be used as an exit from the ground floor level only, (d) be not less than 3 m from the foot of any stairway, and (e) have all glass in door leaves and enclosure panels conforming to, (i) CAN/CGSB-12.1-M, “Tempered or Laminated Safety Glass”, or (ii) CAN/CGSB-12.11-M, “Wired Safety Glass”. |  | Common Sentence | Yes | Exits
2015 | ON | NBC | Div B | 3.4.6.15.(2) | Revolving Doors | Except as permitted by Sentence 3.4.6.15.(3), a revolving door shall not be considered to have an exiting capacity for more than 45 persons. | obc2019_divb | Div B | 3.4.6.15.(2) | 3.4.6.15. Revolving Doors | Except as permitted by Sentence (3), a revolving door shall not be considered to have an exiting capacity for more than 45 persons. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.15.(3) | Revolving Doors | An electrically powered revolving door is not required to conform to Sentences 3.4.6.15.(1) and 3.4.6.15.(2) provided (a) the door leaves will collapse and stop automatic rotation of the door system and not obstruct the doorway if a force not more than that specified in Sentence 3.4.6.16.(2) is applied at the centre of a door leaf, (b) the door leaves are capable of being opened from inside the building without requiring keys, special devices, or specialized knowledge of the door opening mechanism, (c) the allowable exiting capacity is based on the clear width of passage through the door enclosure when the doors are fully collapsed, (d) a permanent sign, whose centre line is between 1?000 mm and 1?500 mm above the floor, is placed on each face of each door leaf indicating the method for collapsing the door leaf in an emergency, and (e) glass used for door leaves and enclosure panels is safety glass conforming to (i) CAN/CGSB-12.1-M90 Tempered or Laminated Safety Glass or (ii) CAN/CGSB-12.11-M90 Wired Safety Glass | obc2019_divb | Div B | 3.4.6.15.(3) | 3.4.6.15. Revolving Doors | An electrically powered revolving door is not required to conform to Sentences (1) and (2) provided, (a) the door leaves will collapse and stop automatic rotation of the door system and not obstruct the doorway if a force not more than that specified in Sentence 3.4.6.16.(2) is applied at the centre of a door leaf, (b) the door leaves are capable of being opened from inside the building without requiring keys, special devices, or specialized knowledge of the door opening mechanism, (c) the allowable exiting capacity is based on the clear width of passage through the door enclosure when the doors are fully collapsed, (d) a permanent sign, whose centreline is between 1 000 mm and 1 500 mm above the floor, is placed on each face of each door leaf indicating the method for collapsing the door leaf in an emergency, and (e) glass used for door leaves and enclosure panels is safety glass conforming to, (i) CAN/CGSB-12.1-M, “Tempered or Laminated Safety Glass”, or (ii) CAN/CGSB-12.11-M, “Wired Safety Glass”. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.16.(1) | Door Release Hardware | Except for devices on doors serving a contained use area or an impeded egress zone designed to be remotely released in conformance with Article 3.3.1.13., and except as permitted by Sentences 3.4.6.16.(4) and 3.4.6.16.(5) and Article 3.4.6.17., locking, latching and other fastening devices on a principal entrance door to a building as well as those on every exit door shall include release hardware complying with Sentence 3.8.3.8.(1) to permit the door to be readily opened from the inside with not more than one releasing operation and without requiring keys, special devices or specialized knowledge of the door-opening mechanism. (See Note A-3.4.6.16.(1).) | obc2019_divb | Div B | 3.4.6.16.(1) | 3.4.6.16. Door Release Hardware | Except for dwelling units, except for devices on doors serving a contained use area or an impeded egress zone designed to be released in conformance with Article 3.3.1.12., and except as permitted by Sentence (4), locking, latching and other fastening devices on every exit door shall permit the door to be readily opened from the inside with not more than one releasing operation and without requiring keys, special devices or specialized knowledge of the door opening mechanism. (See Appendix A.) |  | Common Sentence | Yes | Exits
2015 | ON | NBC | Div B | 3.4.6.16.(2) | Door Release Hardware | If a door is equipped with a latching mechanism, a device that will release the latch and allow the door to swing wide open when a force of not more than 90 N is applied to the device in the direction of travel to the exit shall be installed on every exit door from a floor area containing an assembly occupancy having an occupant load more than 100, every door leading to an exit lobby from an exit stair shaft, and every exterior door leading from an exit stair shaft in a building having an occupant load more than 100, and every exit door from a floor area containing a high-hazard industrial occupancy. | obc2019_divb | Div B | 3.4.6.16.(2) | 3.4.6.16. Door Release Hardware | If a door is equipped with a latching mechanism, a device that will release the latch and allow the door to swing wide open when a force of not more than 90 N is applied to the device in the direction of travel to the exit shall be installed on, every exit door from a floor area containing an assembly occupancy having an occupant load more than 100, every door leading to an exit lobby from an exit stair shaft, and every exterior door leading from an exit stair shaft in a building having an occupant load more than 100, and every exit door from a floor area containing a high hazard industrial occupancy. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.16.(3) | Door Release Hardware | Except as required by Sentence 3.8.3.6.(8), every exit door shall be designed and installed so that, when the latch is released, the door will open under a force of not more than 90 N, applied at the knob or other latch releasing device. | obc2019_divb | Div B | 3.4.6.16.(3) | 3.4.6.16. Door Release Hardware | Except as required by Sentence 3.8.3.3.(7), every exit door shall be designed and installed so that, when the latch is released, the door will open under a force of not more than 90 N, applied at the knob or other latch releasing device. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.16.(4) | Door Release Hardware | Electromagnetic locks that do not incorporate latches, pins or other similar devices to keep the door in the closed position are permitted to be installed on doors, other than those leading directly from a high-hazard industrial occupancy, provided (a) the building is equipped with a fire alarm system, (b) the locking device releases upon actuation of the alarm signal from the buildings fire alarm system, (c) the locking device releases immediately upon loss of power controlling the electromagnetic locking mechanism and its associated auxiliary controls, (d) except for locking devices installed in conformance with Sentence 3.4.6.16.(5), the locking device releases immediately upon actuation of a manually operated switch readily accessible only to authorized personnel, (e) except as provided in Sentence 3.4.6.16.(4), a force of not more than 90 N applied to the door opening hardware initiates an irreversible process that will release the locking device within 15 s and not re-lock until the door has been opened, (f) upon release, the locking device must be reset manually by the actuation of the switch referred to in Sentence 3.4.6.16.(4), (g) a legible sign is permanently mounted on the door to indicate that the locking device will release within 15 s of applying pressure to the door-opening hardware, (h) the total time delay for all electromagnetic locks in any path of egress to release is not more than 15 s, (i) where a bypass switch is installed to allow testing of the fire alarm system, actuation of the switch (i) can prevent the release of the locking device by the fire alarm system, as stated in Sentence 3.4.6.16.(4), during the test, and (ii) causes an audible and visual signal to be indicated at the fire alarm annunciator panel required by Article 3.2.4.9. and at the monitoring station specified in Sentence 3.2.4.8.(4), (j) emergency lighting is provided at each door, and (k) where they are installed on doors providing emergency crossover access to floor areas from exit stairs in accordance with Article 3.4.6.18., (i) the locking device releases immediately upon the operation of a manual station for the fire alarm system located on the wall on the exit stair side not more than 600 mm from the door, and (ii) a legible sign with the words "re-entry door unlocked by fire alarm" written in letters at least 25 mm high with a stroke of at least 5 mm is permanently mounted on the door on the exit stair side. | obc2019_divb | Div B | 3.4.6.16.(4) | 3.4.6.16. Door Release Hardware | Except as permitted by Sentence 3.3.1.12.(6), electromagnetic locks that do not incorporate latches, pins or other similar devices to keep the door in the closed position are permitted to be installed on exit doors other than doors described in Sentence (5) provided, (a) the building is equipped with a fire alarm system conforming to Subsection 3.2.4., (b) the locking device, and all similar devices in the access to exit leading to the exit door, are installed as ancillary devices to the fire alarm system and release immediately upon activation of, (i) the alarm signal where a single stage fire alarm system is installed, (ii) except as provided in Subclause (iii), the alert signal where a two stage fire alarm system is installed, or (iii) the alarm signal of a two stage fire alarm system installed in a care, care and treatment or detention occupancy or in a retirement home, (c) the locking device releases immediately upon loss of power to the fire alarm control panel or loss of power controlling the electromagnetic locking mechanism and its associated auxiliary controls, (d) the locking device releases immediately upon actuation of a manually operated switch readily accessible only to authorized personnel and located near the main entrance of the building or in the central alarm and control facility of Sentence 3.2.6.7.(1), (e) the locking device releases immediately upon a fault being detected in the electrical circuit between the fire alarm control panel and the controller of the locking device, (f) the locking device releases immediately upon the operation of a manual pull station for the fire alarm system located on the wall not more than 600 mm from the door, (g) a legible sign having the words EMERGENCY EXIT UNLOCKED BY FIRE ALARM is permanently mounted on the door, (h) the lettering on the sign required in Clause (g) is at least 25 mm high with a 5 mm stroke, (i) upon release, the locking device must be reset manually by the actuation of the switch referred to in Clause (d), (j) the operation of any by-pass switch, where provided for testing of the fire alarm system, causes an audible signal and a visual signal to be indicated at the fire alarm annunciator panel and at the monitoring station referred to in Clause 3.2.4.8.(4) (a), and (k) emergency lighting is provided at the doors. |  | Common Sentence | Yes | Electromagnetic Locks
2015 | ON | NBC | Div B | 3.4.6.16.(6) | Door Release Hardware | Door hardware for the operation of the doors referred to in this Section shall be installed at a height not more than 1?200 mm above the finished floor. | obc2019_divb | Div B | 3.4.6.16.(8) | 3.4.6.16. Door Release Hardware | Door hardware for the operation of the doors referred to in this Section shall be installed at a height not more than 1 200 mm above the finished floor. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.18.(1) | Emergency Crossover Access to Floor | Except as permitted in Sentence 3.4.6.18.(2), doors providing access to floor areas from exit stairs shall not have locking devices to prevent entry into any floor area from which the travel distance up or down to an unlocked door is more than 2 storeys. | obc2019_divb | Div B | 3.4.6.18.(1) | 3.4.6.18. Emergency Crossover Access to Floor Areas | Except as permitted in Sentence (2), doors providing access to floor areas from exit stairs shall not have locking devices to prevent entry into any floor area from which the travel distance up or down to an unlocked door is more than 2 storeys. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.18.(2) | Emergency Crossover Access to Floor | Doors referred to in Sentence 3.4.6.18.(1) are permitted to be equipped with electromagnetic locks, provided they comply with Sentences 3.4.6.16.(4) and 3.4.6.16.(5). | obc2019_divb | Div B | 3.4.6.18.(2) | 3.4.6.18. Emergency Crossover Access to Floor Areas | Doors referred to in Sentence (1) are permitted to be equipped with electromagnetic locks provided they comply with Sentences 3.4.6.16.(4) and (5). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.18.(3) | Emergency Crossover Access to Floor | Doors referred to in Sentence (1) shall be identified by a sign on the stairway side to indicate that they are openable from that side. | obc2019_divb | Div B | 3.4.6.18.(3) | 3.4.6.18. Emergency Crossover Access to Floor Areas | Doors referred to in Sentence (1) shall be identified by a permanently mounted sign on the stair side to indicate that they are openable from that side. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.18.(4) | Emergency Crossover Access to Floor | Locked doors intended to prevent entry into a floor area from an exit stair shall be identified by a sign on the stairway side to indicate the location of the nearest unlocked door in each direction of travel, and be openable with a master key that fits all locking devices and is kept in a designated location accessible to firefighters or be provided with a wired glass panel not less than 0.0645 m2 in area and located not more than 300 mm from the door opening hardware. | obc2019_divb | Div B | 3.4.6.18.(4) | 3.4.6.18. Emergency Crossover Access to Floor Areas | Locked doors intended to prevent entry into a floor area from an exit stair shall, be identified by a permanently mounted sign on the stair side to indicate the location of the nearest unlocked door in each direction of travel, and be openable with a master key that fits all locking devices and is kept in a designated location accessible to firefighters or be provided with a wired glass panel not less than 0.0645 m2 in area and located not more than 300 mm from the door opening hardware. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.18.(5) | Emergency Crossover Access to Floor | Where access to floor areas through unlocked doors is required by Sentence (1) , it shall be possible for a person entering the floor area to have access through unlocked doors within the floor area to at least one other exit. | obc2019_divb | Div B | 3.4.6.18.(5) | 3.4.6.18. Emergency Crossover Access to Floor Areas | Where access to a floor area is required by Sentence (1), access through unlocked doors to the floor area from at least one other exit shall also be provided. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.19.(1) | Floor Numbering | Arabic numerals indicating the assigned floor number shall (a) be mounted permanently on the stair side of the wall at the latch side of doors to exit stair shafts, (b) be not less than 60 mm high, raised approximately 0.7 mm above the surface, (c) be located 1?500 mm from the finished floor and not more than 300 mm from the door, and (d) be contrasting in colour with the surface to which they are applied (see Note A-3.4.6.19.(1)(d)). | obc2019_divb | Div B | 3.4.6.19.(1) | 3.4.6.19. Floor Numbering | Arabic numerals indicating the assigned floor number shall (a) be mounted permanently on each side of doors to exit stair shafts, (b) be not less than 60 mm high, raised approximately 0.7 mm above the surface, (c) be located 1 500 mm from the finished floor, and (d) be contrasting in colour with the surface to which they are applied. |  | Common Sentence | Yes | Exits
2015 | ON | NBC | Div B | 3.4.6.2.(1) | Minimum Number of Risers | Except as permitted by Sentence 3.3.2.15.(1), every flight of interior stairs shall have not less than 3 risers. | obc2019_divb | Div B | 3.4.6.2.(1) | 3.4.6.2. Minimum Number of Risers | Except as permitted by Sentence 3.3.2.13.(1), every flight of interior stairs shall have no fewer than 3 risers. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.3.(1) | Maximum Vertical Rise of Stair Flights and Required Landings | No flight of stairs shall have a vertical rise of more than 3.7 m between floors or landings, except that a flight of stairs serving as an exit in a Group B, Division 2 occupancy shall have a vertical rise not more than 2.4 m between floors or landings. | obc2019_divb | Div B | 3.4.6.3.(1) | 3.4.6.3. Maximum Vertical Rise of Stair Flights and Required Landings | No flight shall have a vertical rise of more than 3.7 m between floors or landings, except that a flight serving as an exit in a Group B, Division 2 or 3 occupancy shall have a vertical rise not more than 2.4 m between floors or landings. |  | Common Sentence | Yes | Care Occupancy
2015 | ON | NBC | Div B | 3.4.6.3.(2) | Maximum Vertical Rise of Stair Flights and Required Landings | Except as provided in Sentence 3.4.6.3.(3), a landing shall be provided at the top and bottom of each flight of interior and exterior stairs, at the top and bottom of every section of ramp, where a doorway opens onto a stair or ramp, where a ramp opens onto a stair, and where a stair opens onto a ramp. | obc2019_divb | Div B | 3.4.6.3.(2) | 3.4.6.3. Maximum Vertical Rise of Stair Flights and Required | Except as provided by Sentence (3), a landing shall be provided, at the top and bottom of each flight of interior and exterior stairs, at the top and bottom of every section of ramp, where a doorway opens onto a stair or ramp, where a ramp opens onto a stair, and where a stair opens onto a ramp. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.3.(3) | Maximum Vertical Rise of Stair Flights and Required Landings | A landing may be omitted at the bottom of an exterior stair or ramp, provided there is no gate, door or fixed obstruction within the lesser of the width of the stair or ramp, or 1?100 mm. (See Note A-3.4.6.4.) | obc2019_divb | Div B | 3.4.6.3.(3) | 3.4.6.3. Maximum Vertical Rise of Stair Flights and Required | A landing may be omitted at the bottom of an exterior stair or ramp, provided there is no gate, door or fixed obstruction within the lesser of, the width of the stair or ramp, or 1 100 mm. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.4.(1) | Dimensions of Landings | Except as provided in Sentence 3.4.6.4.(2), a landing shall be at least as wide and as long as the width of the stairway in which it occurs. | obc2019_divb | Div B | 3.4.6.4.(1) | 3.4.6.4. Dimensions of Landings (See Appendix A.) | Except as permitted in Sentences (2) and (6), a landing shall be, at least as wide as the width of the stair or ramp in which it occurs, and at least as long as the width of the stair or ramp in which it occurs. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.4.(2) | Dimensions of Landings | In a straight stairway and in a stairway that turns less than 90°, the length of the landing need not be more than the lesser of the required width of stair, or 1 100 mm. | obc2019_divb | Div B | 3.4.6.4.(2) | 3.4.6.4. Dimensions of Landings (See Appendix A.) | Where a landing in a stair or ramp does not turn or turns less than 90o, the length of the landing need not be more than the lesser of, the required width of the stair or ramp, or 1 100 mm. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.4.(3) | Dimensions of Landings | The length of a landing shall be measured perpendicular to the nosing of adjacent steps, at a distance equal to half the length required in Sentence 3.4.6.4.(2), from the narrow edge of the landing. | obc2019_divb | Div B | 3.4.6.4.(3) | 3.4.6.4. Dimensions of Landings (See Appendix A.) | Where a landing in a stair or ramp turns less than 90o, the length of the landing shall be measured perpendicular to the nosings of adjacent steps or to the end of the ramp, at a distance equal to half the length required by Sentence (2) from the narrow edge of the landing. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.4.(4) | Dimensions of Landings | Where a doorway or stairway empties onto a ramp through a side wall, there shall be a level area extending across the full width of the ramp, and for a distance of 300 mm on either side of the wall opening, except one side if it abuts on an end wall. | obc2019_divb | Div B | 3.4.6.4.(4) | 3.4.6.4. Dimensions of Landings (See Appendix A.) | Where a doorway or stair empties onto a ramp through a side wall, there shall be a level area extending across the full width of the ramp, and for a distance of 300 mm on either side of the wall opening, except one side if it abuts on an end wall. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.4.(5) | Dimensions of Landings | Where a doorway or stairway empties onto a ramp through an end wall, there shall be a level area extending across the full width of the ramp and along its length for not less than 900 mm. | obc2019_divb | Div B | 3.4.6.4.(5) | 3.4.6.4. Dimensions of Landings (See Appendix A.) | Where a doorway or stair empties onto a ramp through an end wall, there shall be a level area extending across the full width of the ramp and along its length for not less than 900 mm. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.5.(1) | Handrails | One handrail shall be provided on stairs that are less than 1 100 mm in width. | obc2019_divb | Div B | 3.4.6.5.(1) | 3.4.6.5. Handrails | At least one handrail shall be provided on straight flights that are less than 1 100 mm in width. |  | Common Sentence | Yes | Exits
2015 | ON | NBC | Div B | 3.4.6.5.(10) | Handrails | Except where interrupted by doorways, at least one handrail shall be continuous throughout the length of a stairway or ramp, including at landings. (See Note A-3.4.6.5.(10).) | obc2019_divb | Div B | 3.4.6.5.(10) | 3.4.6.5. Handrails | Except as required by Sentence (16) and except where interrupted by doorways or newels at changes in direction, at least one handrail shall be continuous throughout the length of a stair or ramp, including at landings. (See Appendix A.) |  | Common Sentence | Yes | Exits
2015 | ON | NBC | Div B | 3.4.6.5.(11) | Handrails | Handrails shall be terminated in a manner that will not obstruct pedestrian travel or create a hazard. (See Note A-3.4.6.5.(10).) | obc2019_divb | Div B | 3.4.6.5.(11) | 3.4.6.5. Handrails | Handrails shall be terminated in a manner that will not obstruct pedestrian travel or create a hazard. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.5.(12) | Handrails | At least one handrail at the side of a stairway or ramp shall extend horizontally not less than 300 mm beyond the top and bottom of the stairway or ramp. (See Note A-3.4.6.5.(10).) | obc2019_divb | Div B | 3.4.6.5.(12) | 3.4.6.5. Handrails | At least one handrail shall, in the case of a stair, extend horizontally at the required height, not less than 300 mm beyond the top riser, and continue to slope for a depth of one tread beyond the bottom riser followed by a 300 mm horizontal extension, and in the case of a ramp, extend horizontally at the required height, not less than 300 mm beyond the top and bottom edges of the incline. |  | Common Sentence | Yes | Exits
2015 | ON | NBC | Div B | 3.4.6.5.(13) | Handrails | The clearance between a handrail and any surface behind it shall be not less than 50 mm, or 60 mm if the surface behind the handrail is rough or abrasive. | obc2019_divb | Div B | 3.4.6.5.(13) | 3.4.6.5. Handrails | The clearance between a handrail and any surface behind it shall be not less than, 60 mm, if the surface behind the handrail is rough or abrasive, or 50 mm, in all other cases. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.5.(14) | Handrails | Handrails and their supports shall be designed and constructed to withstand the loading values specified in Sentence 4.1.5.14.(7). | obc2019_divb | Div B | 3.4.6.5.(14) | 3.4.6.5. Handrails | Handrails and their supports shall be designed and constructed to withstand the loading values specified in Sentence 4.1.5.14.(7). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.5.(15) | Handrails | A ramp shall have handrails on both sides. | obc2019_divb | Div B | 3.4.6.5.(15) | 3.4.6.5. Handrails | (15) A ramp shall have handrails on both sides. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.5.(2) | Handrails | One handrail shall be provided on each side of stairs that are 1 100 mm or more in width, curved flights of any width, and ramps. | obc2019_divb | Div B | 3.4.6.5.(2) | 3.4.6.5. Handrails | One handrail shall be provided on each side of, straight flights that are 1 100 mm or more in width, curved flights, and ramps. |  | Common Sentence | Yes | Exits
2015 | ON | NBC | Div B | 3.4.6.5.(3) | Handrails | In addition to Sentence 3.4.6.5.(2), intermediate handrails shall be provided so that (a) a handrail is reachable within 750 mm of all portions of the required exit width,(b) at least one portion of the stair or ramp between two handrails is the minimum width required for stairways or ramps (see Sentences 3.4.3.2.(8) and 3.4.3.3.(4)), and (c) all other portions of the stair or ramp between two handrails have a clear width of 510 mm or more. | obc2019_divb | Div B | 3.4.6.5.(3) | 3.4.6.5. Handrails | In addition to Sentence (2), intermediate handrails shall be provided so that, a handrail is reachable within 825 mm of all portions of the required exit width, and at least one portion of the stair or ramp between two handrails is the required exit width for stairs or ramps as described in Sentences 3.4.3.2.(7) and 3.4.3.4.(4). |  | Common Sentence | Yes | Exits
2015 | ON | NBC | Div B | 3.4.6.5.(4) | Handrails | Where a stair or ramp is wider than its required exit width, handrails shall be located along the most direct path of travel. (See Note A-3.4.6.5.(4).) | obc2019_divb | Div B | 3.4.6.5.(4) | 3.4.6.5. Handrails | Where a stair or ramp is wider than its required exit width, handrails shall be located along the most direct path of travel. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.5.(5) | Handrails | Handrails shall be continuously graspable along their entire length, be free of any sharp or abrasive elements, and have a circular cross-section with an outside diameter not less than 30 mm and not more than 43 mm, or a non-circular cross-section with a perimeter not less than 100 mm and not more than 125 mm and whose largest cross-sectional dimension is not more than 45 mm. | obc2019_divb | Div B | 3.4.6.5.(5) | 3.4.6.5. Handrails | Handrails shall be continuously graspable along their entire length, shall be free of any sharp or abrasive elements, and shall have, a circular cross-section with an outside diameter not less than 30 mm and not more than 43 mm, or any non-circular cross-section with a perimeter not less than 100 mm and not more than 125 mm and whose largest cross-sectional dimension is not more than 45 mm. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.5.(6) | Handrails | The height of handrails on stairs, on aisles with steps and on ramps shall be measured vertically from the top of the handrail to a straight line drawn tangent to the tread nosings of the stair or aisle step served by the handrail (see Note A-9.8.7.4.), or the surface of the ramp, floor or landing served by the handrail. | obc2019_divb | Div B | 3.4.6.5.(6) | 3.4.6.5. Handrails | The height of handrails on stairs, on aisles with steps and on ramps shall be measured vertically from the top of the handrail to, a straight line drawn tangent to the tread nosings of the stair served by the handrail, or the surface of the ramp, floor or landing served by the handrail. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.5.(7) | Handrails | Except as provided in Sentence 3.4.6.5.(8) and Sentence 3.8.3.5.(1), the height of handrails on stairs, on aisles with steps and on ramps shall be not less than 865 mm, and not more than 1 070 mm . | obc2019_divb | Div B | 3.4.6.5.(7) | 3.4.6.5. Handrails | Except as provided by Sentence (8) and Clause 3.8.3.4.(1)(e), the height of handrails on stairs, on aisles with steps and on ramps shall be, not less than 865 mm, and not more than 1070 mm. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.5.(8) | Handrails | Handrails installed in addition to required handrails need not comply with Sentence 3.4.6.5.(7). | obc2019_divb | Div B | 3.4.6.5.(8) | 3.4.6.5. Handrails | Handrails installed in addition to required handrails need not comply with Sentence (7). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.5.(9) | Handrails | Required handrails shall be continuously graspable throughout the length of a ramp, and a flight of stairs, from the bottom riser to the top riser. | obc2019_divb | Div B | 3.4.6.5.(9) | 3.4.6.5. Handrails | Required handrails shall be continuous throughout the length of, a ramp, and a flight, from the bottom riser to the top riser. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.6.(1) | Guards | Every exit shall have a wall or a well-secured guard on each side, where (a) there is a difference in elevation of more than 600 mm between the walking surface and (b) the adjacent surface, or the adjacent surface within 1.2 m of the walking surface has a slope of more than 1 in 2. | obc2019_divb | Div B | 3.4.6.6.(1) | 3.4.6.6. Guards | Every exit shall have a wall or a well-secured guard on each side where, (a) the difference in level is more than 600 mm between the walking surface and the adjacent surface, or (b) the adjacent surface within 1 200 mm of the walking surface has a slope of more than 1 in 2 away from the walking surface. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.6.(2) | Guards | Except as required by Sentence 3.4.6.6.(4), the height of guards for exit stairs and exit ramps as well as their landings shall be not less than 1?070 mm. | obc2019_divb | Div B | 3.4.6.6.(2) | 3.4.6.6. Guards | Except as required by Sentence (4), the height of guards for exit stairs and exit ramps, as well as their landings, shall be not less than 1 070 mm. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.6.(3) | Guards | The height of guards shall be measured vertically to the top of the guard from a line drawn through the outside edges of the stair nosings, or the surface of the ramp or landing. | obc2019_divb | Div B | 3.4.6.6.(3) | 3.4.6.6. Guards | The height of guards shall be measured vertically to the top of the guard from, a line drawn through the outside edges of the tread nosings, or the surface of the ramp or landing. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.6.(4) | Guards | The height of guards for exterior stairs and landings more than 10 m above adjacent ground level shall be not less than 1500 mm measured vertically to the top of the guard from the surface of the landing or from a line drawn through the outside edges of the stair nosings. | obc2019_divb | Div B | 3.4.6.6.(4) | 3.4.6.6. Guards | The height of guards for exterior stairs and landings more than 10 m above adjacent ground level shall be not less than 1 500 mm measured vertically to the top of the guard from the surface of the landing or a line drawn through the outside edges of the tread nosings. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.6.(5) | Guards | Except as provided in Sentence 3.3.1.18.(3) and Articles 3.3.4.7. and 3.3.5.10., guards in exits shall not have any openings that permit the passage of a spherical object whose diameter is more than 100 mm | obc2019_divb | Div B | 3.4.6.6.(5) | 3.4.6.6. Guards | Except as provided in Sentence (6), openings through any guard that is required by Sentence (1) shall be of a size that will prevent the passage of a sphere having a diameter more than 100 mm unless it can be shown that the location and size of openings that exceed this limit do not represent a hazard. |  | Common Sentence | Yes | Exits
2015 | ON | NBC | Div B | 3.4.6.6.(6) | Guards | In a stairway, a window for which the distance measured vertically between the bottom of the window and a line drawn through the outside edges of the stair nosings is less than 900 mm, or a window that extends to less than 1 070 mm above the landing, shall (a) be protected by a guard that is (i) located approximately 900 mm above a line drawn through the outside edges of the stair nosings, or (ii) not less than 1 070 mm high measured to the top of the guard from the surface of the landing, or (b) be fixed in position and designed to resist the lateral design loads specified for guards and walls in Articles 4.1.5.14. and 4.1.5.16. | obc2019_divb | Div B | 3.4.6.6.(7) | 3.4.6.6. Guards | In a stairway, a window for which the distance measured vertically between the bottom of the window and a line drawn through the outside edges of the tread nosings is less than 900 mm, or a window that extends to less than 1 070 mm above the landing, shall, (a) be protected by a guard that is, (i) located approximately 900 mm above a line drawn through the outside edges of the tread nosings, or (ii) not less than 1 070 mm high measured to the top of the guard from the surface of the landing, or (b) be fixed in position and designed to resist the lateral design loads specified for guards and walls in Articles 4.1.5.14. and 4.1.5.16. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.7.(1) | Ramp Slope | Except as required for aisles by Article 3.3.2.5., the maximum slope of a ramp shall be 1 in 10 in any assembly, care, treatment, detention or residential occupancy, 1 in 6 in an industrial occupancy, 1 in 8 in all other occupancies , and 1 in 10 for an exterior ramp. | obc2019_divb | Div B | 3.4.6.7.(1) | 3.4.6.7. Ramp Slope | Except as required for aisles by Article 3.3.2.4., the maximum slope of a ramp shall be, 1 in 10 in any assembly, care, care and treatment, detention or residential occupancy, 1 in 6 in an industrial occupancy, 1 in 8 in all other occupancies, and 1 in 10 for an exterior ramp. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.8.(1) | Treads and Risers | Except as permitted for dwelling units and by Sentence 3.4.7.5.(1) for fire escapes, steps for stairs shall have a run of not less than 280 mm between successive steps. | obc2019_divb | Div B | 3.4.6.8.(1) | 3.4.6.8. Treads and Risers | Except as permitted for dwelling units and by Sentence 3.4.7.5.(1) for fire escapes, steps in flights shall have a run of not less than 280 mm and not more than 355 mm between successive steps. |  | Common Sentence | Yes | Exits
2015 | ON | NBC | Div B | 3.4.6.8.(10) | Treads and Risers | If resilient material is used to cover the nosing of a stair tread, the minimum rounded or beveled edge required by Sentence (8) is permitted to be reduced to 3 mm. | obc2019_divb | Div B | 3.4.6.8.(10) | 3.4.6.8. Treads and Risers | If resilient material is used to cover the nosing of a stair tread, the minimum radius or bevel required by Sentence (8) is permitted to be reduced to 3 mm. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.8.(3) | Treads and Risers | Except as provided in Article 3.3.4.7. and except for fire escape stairs, stairs that are principally used for maintenance and service, and stairs that serve industrial occupancies other than storage garages, steps for stairs shall have no open risers. | obc2019_divb | Div B | 3.4.6.8.(2) | 3.4.6.8. Treads and Risers | Steps in flights shall have no open risers, (a) except as provided in Article 3.3.4.7., and (b) except for the following stairs: (i) fire escape stairs, (ii) stairs that are principally used for maintenance and service, and (iii) stairs that serve industrial occupancies other than storage garages. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.8.(3) | Treads and Risers | Steps for stairs referred to in Sentence (1) shall have a rise between successive treads not less than 125 mm and not more than 180 mm. | obc2019_divb | Div B | 3.4.6.8.(2) | 3.4.6.8. Treads and Risers | Steps referred to in Sentence (1) shall have a rise between successive treads not less than 125 mm and not more than 180 mm. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.8.(4) | Treads and Risers | Except in fire escape stairs and where an exterior stair adjoins a walkway as permitted in Sentence 3.4.6.3.(3), risers, measured as the vertical nosing-to-nosing distance, shall be of uniform height in any one flight, with a maximum tolerance of (a) 5 mm between adjacent treads or landings, and (b) 10 mm between the tallest and shortest risers in a flight. | obc2019_divb | Div B | 3.4.6.8.(3) | 3.4.6.8. Treads and Risers | Except in fire escape stairs and where an exterior stair adjoins a walkway as permitted by Sentence 3.4.6.3.(3), risers, measured as the vertical nosing-to-nosing distance, shall be of uniform height in any one flight, with a maximum tolerance of, (a) 5 mm between adjacent treads or landings, and (b) 10 mm between the tallest and shortest risers in a flight. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.8.(5) | Treads and Risers | Except in fire escape stairs, treads shall have a uniform run with a maximum tolerance of (a) 5 mm between adjacent treads, and (b) 10 mm between the deepest and shallowest treads in a flight. | obc2019_divb | Div B | 3.4.6.8.(4) | 3.4.6.8. Treads and Risers | Except in fire escape stairs, treads, measured as the horizontal nosing-to-nosing distance, shall have a uniform run with a maximum tolerance of, (a) 5 mm between adjacent treads, and (b) 10 mm between the deepest and shallowest treads in a flight. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.8.(6) | Treads and Risers | Treads and risers shall not differ significantly in run and rise in successive flights in any stair system. | obc2019_divb | Div B | 3.4.6.8.(5) | 3.4.6.8. Treads and Risers | Treads and risers shall not differ significantly in run and rise in successive flights in any stair system. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.8.(7) | Treads and Risers | The slope of treads or landings shall not exceed 1 in 50. | obc2019_divb | Div B | 3.4.6.8.(7) | 3.4.6.8. Treads and Risers | The slope on treads or landings shall not exceed 1 in 50. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.8.(8) | Treads and Risers | Except as permitted by Sentence 3.4.6.8.(10), the top of the nosing of stair treads shall have a rounded or beveled edge extending not less than 6 mm and not more than 13 mm measured horizontally from the front of the nosing. | obc2019_divb | Div B | 3.4.6.8.(8) | 3.4.6.8. Treads and Risers | Except as permitted by Sentence (10), the top of the nosing of a stair tread shall have a rounded or bevelled edge extending not less than 6 mm and not more than 13 mm measured horizontally from the front of the nosing. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.8.(9) | Treads and Risers | The front edge of stair treads in exits and public access to exits shall be at right angles to the direction of exit travel. | obc2019_divb | Div B | 3.4.6.8.(9) | 3.4.6.8. Treads and Risers | The front edge of stair treads in exits and public access to exits shall be at right angles to the direction of exit travel. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.9.(2) | Curved Flights in Exits | A curved flight used as an exit shall have (a) a handrail on each side, (b) a minimum run of 240 mm, (c) a run that conforms to Article 3.4.6.8. when measured at a point 300 mm from the centre line of the handrail at the narrow end of the tread, and (d) an inside radius that is not less than twice the stair width. | obc2019_divb | Div B | 3.4.6.9.(2) | 3.4.6.9. Curved Flights in Exits | A curved flight used as an exit shall have, (a) a handrail on each side, (b) treads with a minimum run of 240 mm, (c) treads with a run that conforms to Article 3.4.6.8. when measured at a point 300 mm from the centre line of the inside handrail, and (d) an inside radius that is not less than twice the stair width. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.9.(3) | Curved Flights in Exits | Tapered treads shall have a consistent angle and uniform run and rise dimensions in accordance with the construction tolerances stipulated in Article 3.4.6.8. when measured at a point 300 mm from the centre line of the handrail at the narrow end of the tread | obc2019_divb | Div B | 3.4.6.9.(3) | 3.4.6.9. Curved Flights in Exits | Tapered treads shall have a consistent angle and uniform run and rise dimensions in accordance with the construction tolerances described in Article 3.4.6.8. when measured at a point 300 mm from the centre line of the inside handrail. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.6.9.(4) | Curved Flights in Exits | All tapered treads within a flight shall turn in the same direction. | obc2019_divb | Div B | 3.4.6.9.(4) | 3.4.6.9. Curved Flights in Exits | All tapered treads within a flight shall turn in the same direction. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.7.1.(1) | Scope | Except as permitted by Sentence 3.4.7.1.(2), fire escapes shall not be erected on a building. | obc2019_divb | Div B | 3.4.7.1.(1) | 3.4.7.1. Scope | Except as permitted by Sentence (2), fire escapes shall not be erected on a building. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.7.1.(2) | Scope | If it is impracticable to provide one or more of the exit facilities listed in Article 3.4.1.4., fire escapes conforming to Articles 3.4.7.2. to 3.4.7.7. are permitted to serve floor areas in an existing building provided the floor areas served are not more than (a) 2 storeys above ground level in care, treatment or detention occupancies, and (b) 5 storeys above ground level in other occupancies. | obc2019_divb | Div B | 3.4.7.1.(2) | 3.4.7.1. Scope | If it is impracticable to provide one or more of the exit facilities listed in Article 3.4.1.4., fire escapes conforming to Articles 3.4.7.2. to 3.4.7.7. are permitted to serve floor areas in an existing building provided the floor areas served are, (a) not in an elementary or secondary school or a retirement home, (b) not more than 2 storeys above ground level in care, care and treatment or detention occupancies, and (c) not more than 5 storeys above ground level in other occupancies. |  | Common Sentence | Yes | Retirement Homes
2015 | ON | NBC | Div B | 3.4.7.2.(1) | Fire Escape Construction | Fire escapes shall be of metal or concrete, of the stair type extending to ground level, constructed throughout in a strong substantial manner and securely fixed to the building, except that wooden fire escapes are permitted to be used on buildings of combustible construction if all posts and brackets are not less than 89 mm in their least dimension and all other woodwork is not less than 38 mm in its least dimension. | obc2019_divb | Div B | 3.4.7.2.(1) | 3.4.7.2. Fire Escape Construction | Fire escapes shall be of metal or concrete, of the stair type extending to ground level, constructed throughout in a strong substantial manner and securely fixed to the building, except that wooden fire escapes are permitted to be used on buildings of combustible construction if all posts and brackets are not less than 89 mm in their least dimension and all other woodwork is not less than 38 mm in its least dimension. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.7.3.(1) | Access to Fire Escapes | Access to fire escapes shall be from corridors through doors at floor level, except that access from a dwelling unit is permitted to be through a casement window having an unobstructed opening not less than 1?100 mm high by 550 mm wide with a sill height of not more than 900 mm above the inside floor. | obc2019_divb | Div B | 3.4.7.3.(1) | 3.4.7.3. Access to Fire Escapes | Access to fire escapes shall be from corridors through doors at floor level, except that access from a dwelling unit is permitted to be through a casement window having an unobstructed opening not less than 1 100 mm high by 550 mm wide with a sill height of not more than 900 mm above the inside floor. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.7.3.(2) | Access to Fire Escapes | The clear area of a fire escape balcony onto which a door opens, shall be not less than 1 m2. | obc2019_divb | Div B | 3.4.7.3.(2) | 3.4.7.3. Access to Fire Escapes | The clear area of a fire escape balcony onto which a door opens, shall be not less than 1 m2. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.7.4.(1) | Protection of Fire Escapes | If a fire escape serves any storey above the second, openings located in a zone described in Sentence 3.4.7.4.(2), including access doorways in the exterior walls of the building to which the fire escape is attached, shall be protected by closures conforming to Subsection 3.1.8. | obc2019_divb | Div B | 3.4.7.4.(1) | 3.4.7.4. Protection of Fire Escapes | If a fire escape serves any storey above the second, openings located in a zone described in Sentence (2), including access doorways in the exterior walls of the building to which the fire escape is attached, shall be protected by closures conforming to Subsection 3.1.8. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.7.4.(2) | Protection of Fire Escapes | The zone referred to in Sentence 3.4.7.4.(1) extends from any balcony, platform or stairway of a fire escape to a distance (a) 3 m horizontally, (b) 10 m below, or (c) 1.8 m above. | obc2019_divb | Div B | 3.4.7.4.(2) | 3.4.7.4. Protection of Fire Escapes | The zone referred to in Sentence (1) extends from any balcony, platform or stairway of a fire escape to a distance, (a) 3 m horizontally, (b) 10 m below, and (c) 1 800 mm above. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.7.5.(1) | Stairs | Stairs shall be inclined at an angle of not more than 45° with the horizontal, and their steps shall have risers not more than 210 mm high and treads not less than 220 mm wide exclusive of nosing. | obc2019_divb | Div B | 3.4.7.5.(1) | 3.4.7.5. Stairs | Stairs shall be inclined at an angle of not more than 45? with the horizontal, and their steps shall have risers not more than 210 mm high and treads not less than 220 mm wide exclusive of nosing. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.7.5.(2) | Stairs | Stairway headroom shall be not less than 1?950 mm plus the height of one riser measured vertically above the nosing of any tread or platform. | obc2019_divb | Div B | 3.4.7.5.(2) | 3.4.7.5. Stairs | Stairway headroom shall be not less than 1 950 mm plus the height of one riser measured vertically above the nosing of any tread or platform. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.7.5.(3) | Stairs | The width of a fire escape shall conform to Articles 3.4.3.1. to 3.4.3.3., except that the width is permitted to be reduced to 550 mm provided the fire escape serves (a) not more than 3 storeys, and (b) not more than 15 persons. | obc2019_divb | Div B | 3.4.7.5.(3) | 3.4.7.5. Stairs | The width of a fire escape shall conform to Articles 3.4.3.1., 3.4.3.2. and 3.4.3.4., except that the width is permitted to be reduced to 550 mm provided the fire escape serves, (a) not more than 3 storeys, and (b) not more than 15 persons. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.7.5.(4) | Stairs | If a flight of stairs leading to the ground at the foot of a fire escape is not fixed in position, it shall be held in the raised position without a latch or locking device, and shall be fitted with a counterbalancing device that will permit it to be easily and quickly brought into position for use. | obc2019_divb | Div B | 3.4.7.5.(4) | 3.4.7.5. Stairs | If a flight leading to the ground at the foot of a fire escape is not fixed in position, it shall, (a) be held in the raised position without a latch or locking device, (b) be fitted with a counterbalancing device, (c) be easily and quickly brought into position for use, and (d) reach the ground in the lowered position. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.7.6.(1) | Guards and Railings | The open sides of every platform, balcony and stairway forming part of a fire escape shall be protected by guards not less than 920 mm high measured vertically above the nosing of any tread or platform. | obc2019_divb | Div B | 3.4.7.6.(1) | 3.4.7.6. Guards and Railings | The open sides of every platform, balcony and stairway forming part of a fire escape shall be protected by guards not less than 920 mm high measured vertically above the nosing of any tread or platform. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.7.6.(2) | Guards and Railings | The top rail of a guard is permitted to serve as a handrail if it is free from obstructions which could break a handhold. | obc2019_divb | Div B | 3.4.7.6.(2) | 3.4.7.6. Guards and Railings | The top rail of a guard is permitted to serve as a handrail if it is free from obstructions that could break a handhold. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.7.6.(3) | Guards and Railings | A wall handrail shall be installed if the fire escape is more than 550 mm wide. | obc2019_divb | Div B | 3.4.7.6.(3) | 3.4.7.6. Guards and Railings | A wall handrail shall be installed if the fire escape is more than 550 mm wide. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.7.6.(4) | Guards and Railings | Unless it can be shown that the size of openings that exceed this limit does not present a hazard, there shall be no opening that permits the passage of a sphere whose diameter is more than 100 mm through a guard for a fire escape. | obc2019_divb | Div B | 3.4.7.6.(4) | 3.4.7.6. Guards and Railings | Openings through any guard that is required by Sentence (1) shall be of a size that will prevent the passage of a sphere having a diameter more than 100 mm unless it can be shown that the location and size of openings that exceed this limit do not represent a hazard. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.4.7.6.(5) | Guards and Railings | Unless it can be shown that the location and size of an opening do not present a hazard, a guard for a fire escape shall be designed so that no member, attachment or opening located between 140 mm and 900 mm above a platform or the nosing of any tread will facilitate climbing. Except for guards conforming to Article 3.3.5.10., guards that protect a level located more than one storey or 4.2 m above the adjacent level shall be designed so that no member, attachment or opening located between 140 mm and 900 mm above the level being protected by the guard facilitates climbing. (See Note A- 9.8.8.6.(1).) | obc2019_divb | Div B | 3.4.6.6.(8) | 3.4.6.6. Guards | Unless it can be shown that the location and size of openings do not present a hazard, a guard shall be designed so that no member, attachment or opening located between 140 mm and 900 mm above the level being protected by the guard will facilitate climbing. |  | Common Sentence | Yes | Exits
2015 | ON | NBC | Div B | 3.4.7.6.(5) | Guards and Railings | Unless it can be shown that the location and size of an opening do not present a hazard, a guard for a fire escape shall be designed so that no member, attachment or opening located between 140 mm and 900 mm above a platform or the nosing of any tread will facilitate climbing. | obc2019_divb | Div B | 3.4.7.6.(5) | 3.4.7.6. Guards and Railings | Unless it can be shown that the location and size of openings do not present a hazard, a guard for a fire escape shall be designed so that no member, attachment or opening located between 140 mm and 900 mm above a platform or the nosing of any tread will facilitate climbing. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.5.1.1.(1) | Scope | This Section applies to vertical transportation facilities installed in a building, including elevators, escalators and dumbwaiters. | obc2019_divb | Div B | 3.5.1.1.(1) | 3.5.1.1. Scope | This Section applies to vertical transportation facilities installed in a building, including elevators, escalators and dumbwaiters. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.5.1.1.(2) | Scope | Elevators in a building within the scope of Subsection 3.2.6. shall conform to Articles 3.2.6.4. , 3.2.6.5. and 3.2.6.6. | obc2019_divb | Div B | 3.5.1.1.(2) | 3.5.1.1. Scope | Elevators in a building within the scope of Subsection 3.2.6. shall conform to Articles 3.2.6.4. and 3.2.6.5. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.5.2.1.(3) | Elevators, Escalators and Dumbwaiters | Passenger elevators shall conform to Appendix E of ASME/CSA ASME A17.1/CSA B44 "Safety Code for Elevators and Escalators" | obc2019_divb | Div B | 3.5.2.2.(1) | 3.5.2.2. Barrier-Free Design | Passenger elevators shall conform to Appendix E of ASME A17.1 / CSA B44, "Safety Code for Elevators and Escalators". |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.5.3.1.(1) | Fire Separations for Elevator Hoistways | Except as permitted by Sentence (2), a vertical service space used as an elevator hoistway shall be separated from all other portions of each adjacent storey by a fire separation having a fire-resistance rating conforming to Table 3.5.3.1. for the fire-resistance rating required by Subsection 3.2.2. for (a) the floor assembly above the storey, or (b) the floor assembly below the storey, if there is no floor assembly above. | obc2019_divb | Div B | 3.5.3.1.(1) | 3.5.3.1. Fire Separations for Elevator Hoistways | Except as permitted by Sentence (2), a vertical service space used as an elevator hoistway shall be separated from all other portions of each adjacent storey by a fire separation having a fire-resistance rating conforming to Table 3.5.3.1. for the fire-resistance rating required by Subsection 3.2.2. for, (a) the floor assembly above the storey, or (b) the floor assembly below the storey, if there is no floor assembly above. |  | Common Sentence | Yes | Vertical Transportation
2015 | ON | NBC | Div B | 3.5.3.1.(2) | Fire Separations for Elevator Hoistways | Passenger elevators, other than those provided for firefighters in accordance with Article 3.2.6.5., are permitted to be located within interconnected floor space without being enclosed in a hoistway separated from the remainder of the building, provided the elevator machinery is located in a room separated from the remainder of the building by a fire separation having a fire-resistance rating not less than that required for hoistways by Sentence 3.5.3.1.(1). | obc2019_divb | Div B | 3.5.3.1.(2) | 3.5.3.1. Fire Separations for Elevator Hoistways | Passenger elevators, other than those provided for firefighters in accordance with Article 3.2.6.5., are permitted to be located within or adjacent to the opening of an interconnected floor space protected in conformance with the requirements of Articles 3.2.8.3. to 3.2.8.11., Sentences 3.2.8.2.(4) and (6) without being enclosed in a hoistway separated from the remainder of the interconnected floor space provided the elevator machinery is located in a room separated from the remainder of the building by a fire separation whose fire-resistance rating is not less than that required for hoistways by Sentence (1). |  | Common Sentence | Yes | Vertical Transportation
2015 | ON | NBC | Div B | 3.5.3.2.(1) | Vertical Service Spaces for Dumbwaiters | A vertical service space containing a dumbwaiter shall be separated from all other portions of each adjacent storey by a fire separation having a fire-resistance rating conforming to Table 3.5.3.1. for the fire-resistance rating required by Sunsection 3.2.2, for (a) the floor assembly above the storey or (b)the floor assembly below the storey, if there is no floor assembly above. | obc2019_divb | Div B | 3.5.3.2.(1) | 3.5.3.2. Vertical Service Spaces for Dumbwaiters | A vertical service space containing a dumbwaiter shall be separated from all other portions of each adjacent storey by a fire separation having a fire-resistance rating conforming to Table 3.5.3.1. for the fire-resistance rating required by Subsection 3.2.2. for, (a) the floor assembly above the storey, or (b) the floor assembly below the storey, if there is no floor assembly above. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.5.3.3.(1) | Fire Separations for Elevator Machine Rooms | Except as permitted by Sentence (2), a room containing elevator machinery shall be separated from all other parts of the building by a fire separation having a fire-resistance rating not less than that required for the vertical service space containing the elevator hoistway. | obc2019_divb | Div B | 3.5.3.3.(1) | 3.5.3.3. Fire Separations for Elevator Machine Rooms | Except as permitted by Sentence (2), a room containing elevator machinery shall be separated from all other parts of the building by a fire separation having a fire-resistance rating not less than that required for the vertical service space containing the elevator hoistway. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.5.3.3.(2) | Fire Separations for Elevator Machine Rooms | A room containing elevator machinery need not be separated from the elevator hoistway that it serves provided the room and the hoistway are separated from all other parts of the building by a fire separation having a fire-resistance rating not less than that required for the vertical service space containing the elevator hoistway. | obc2019_divb | Div B | 3.5.3.3.(2) | 3.5.3.3. Fire Separations for Elevator Machine Rooms | A room containing elevator machinery need not be separated from the elevator hoistway that it serves provided the room and the hoistway are separated from all other parts of the building by a fire separation having a fire-resistance rating not less than that required for the vertical service space containing the elevator hoistway. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.5.4.1.(1) | Elevator Car Dimensions | If one or more elevators are provided in a building, all storeys shall be served by at least one elevator which has inside dimensions that will accommodate and provide adequate access for a patient stretcher 2 010 mm long and 610 mm wide in the prone position. (See Note A-3.5.4.1.(1).) | obc2019_divb | Div B | 3.5.4.1.(1) | 3.5.4.1. Elevator Car Dimensions | If an elevator is installed to conform to the requirements of Article 3.3.1.7., or if one or more elevators are provided in a building more than three storeys in building height, each storey having elevator service shall be served by at least one elevator that has inside dimensions that will accommodate and provide adequate access for a patient stretcher 2 010 mm long and 610 mm wide in the prone position. (See Appendix A.) |  | Common Sentence | Yes | Vertical Transportation
2015 | ON | NBC | Div B | 3.5.4.1.(2) | Elevator Car Dimensions | An elevator satisfying the requirements of Sentence (1) shall be clearly identified on the main entrance level of the building. | obc2019_divb | Div B | 3.5.4.1.(2) | 3.5.4.1. Elevator Car Dimensions | An elevator satisfying the requirements of Sentence (1) shall be clearly identified on the main entrance level of the building. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.1.1.(1) | Scope | The provisions of this Section apply to horizontal service spaces, vertical service spaces, attic or roof spaces, ducts, crawl spaces, shaft spaces, service rooms, and mechanical penthouses, and facilities contained therein. | obc2019_divb | Div B | 3.6.1.1.(1) | 3.6.1.1. Scope | The provisions of this Section apply to horizontal service spaces, vertical service spaces, attic or roof spaces, ducts, crawl spaces, shaft spaces, service rooms, and mechanical penthouses, and facilities contained in any of them. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.1.4.(1) | Storage Use Prohibition | Service spaces shall not be designed to facilitate subsequent use as storage space. | obc2019_divb | Div B | 3.6.1.3.(1) | 3.6.1.3. Storage Use Prohibition | Service spaces shall not be designed to facilitate subsequent use as storage space. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.2.1.(1) | Fire Separations around Service Rooms | Except as permitted by Sentences (2) , (8) , (9) and (10), fuel-fired appliances shall be installed in service rooms separated from the remainder of the building by fire separations having a fire-resistance rating not less than 1 h. | obc2019_divb | Div B | 3.6.2.1.(1) | 3.6.2.1. Fire Separations around Service Rooms | Except as permitted by Sentences (2) and (8) to (10), fuel-fired appliances shall be installed in service rooms separated from the remainder of the building by fire separations having a fire-resistance rating not less than 1 h. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.2.1.(10) | Fire Separations around Service Rooms | A fire separation is not required between a roof-top appliance and the building it serves. | obc2019_divb | Div B | 3.6.2.1.(10) | 3.6.2.1. Fire Separations around Service Rooms | A fire separation is not required between a rooftop appliance and the building it serves. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.2.1.(2) | Fire Separations around Service Rooms | Except as required by Sentence (3), a fuel-fired appliance that serves only one room or suite is not required to be installed in a service room separated from the remainder of the building. | obc2019_divb | Div B | 3.6.2.1.(2) | 3.6.2.1. Fire Separations around Service Rooms | Except as required by Sentence (3), a fuel-fired appliance that serves only one room or suite is not required to be installed in a service room separated from the remainder of the building. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.2.1.(3) | Fire Separations around Service Rooms | A solid-fuel-burning appliance shall not be located in a repair garage, a storage garage, or any other location where it could be exposed to flammable vapours or gases, unless (a) it is enclosed in a service room that is separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h, (b) it is supplied with combustion air directly from outside the building, and (c) the heat that it generates is supplied indirectly to the space served by means of ducts or piping. | obc2019_divb | Div B | 3.6.2.1.(3) | 3.6.2.1. Fire Separations around Service Rooms | A solid fuel fired appliance shall not be located in a repair garage, a storage garage, or any other location where it could be exposed to flammable vapours or gases unless, (a) it is enclosed in a service room that is separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h, (b) it is supplied with combustion air directly from outside the building, and (c) the heat that it generates is supplied indirectly to the space served by means of ducts or piping. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.2.1.(4) | Fire Separations around Service Rooms | A service room containing an incinerator shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 2 h. | obc2019_divb | Div B | 3.6.2.1.(4) | 3.6.2.1. Fire Separations around Service Rooms | A service room containing an incinerator shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 2 h. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.2.1.(5) | Fire Separations around Service Rooms | Equipment that uses a liquid having a flash point below 93.3°C shall be installed in a service room separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h. | obc2019_divb | Div B | 3.6.2.1.(5) | 3.6.2.1. Fire Separations around Service Rooms | Equipment that uses a liquid having a flash point below 93.3°C shall be installed in a service room separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.2.1.(6) | Fire Separations around Service Rooms | Electrical equipment that is required to be located in a service room according to CSA C22.1-12 Canadian Electrical Code, Part I shall be installed in a service room separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h. | obc2019_divb | Div B | 3.6.2.1.(6) | 3.6.2.1. Fire Separations around Service Rooms | Electrical equipment that is required to be located in a service room by a regulation made under the Electricity Act, 1998, shall be installed in a service room separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h. |  | Common Sentence | Yes | Referenced Standard
2015 | ON | NBC | Div B | 3.6.2.1.(7) | Fire Separations around Service Rooms | Except as permitted by Sentence (8), in a storey that is not sprinklered throughout, a service room that contains service equipment other than that addressed by Sentences (1) to (6) shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h. | obc2019_divb | Div B | 3.6.2.1.(7) | 3.6.2.1. Fire Separations around Service Rooms | Except as permitted by Sentence (8), in a storey that is not sprinklered, a service room that contains service equipment other than that addressed by Sentences (1) to (6), shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.2.1.(8) | Fire Separations around Service Rooms | Where a service room contains a limited quantity of service equipment, and the service equipment neither constitutes a fire hazard nor is essential to the operation of fire safety systems in the building, the requirements for a fire separation shall not apply. | obc2019_divb | Div B | 3.6.2.1.(8) | 3.6.2.1. Fire Separations around Service Rooms | If a service room referred to in Sentence (7) contains a limited quantity of service equipment, and the service equipment neither constitutes a fire hazard nor is essential to the operation of fire safety systems in the building, the requirements for a fire separation shall not apply. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.6.2.1.(9) | Fire Separations around Service Rooms | A fire separation is not required between a fireplace and the space it serves. | obc2019_divb | Div B | 3.6.2.1.(9) | 3.6.2.1. Fire Separations around Service Rooms | A fire separation is not required between a fireplace and the space it serves. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.2.2.(1) | Service Rooms under Exits | A service room containing service equipment subject to possible explosion, such as boilers operating in excess of 100 kPa (gauge) and some types of refrigerating machinery and transformers, shall not be located directly under a required exit. | obc2019_divb | Div B | 3.6.2.2.(1) | 3.6.2.2. Service Rooms Under Exits | A service room containing service equipment subject to possible explosion, such as boilers operating in excess of 100 kPa (gauge) and some types of refrigerating machinery and transformers, shall not be located directly under a required exit. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.2.3.(1) | Service Equipment | A service room containing space heating, space cooling and service water heating appliances is permitted to contain other service equipment such as electrical service equipment. | obc2019_divb | Div B | 3.6.2.3.(1) | 3.6.2.3. Service Equipment | A service room containing space heating, space cooling and service water heating appliances is permitted to contain other service equipment such as electrical service equipment. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.2.4.(1) | Incinerator Rooms | A service room containing an incinerator shall not contain other fuel-fired appliances. | obc2019_divb | Div B | 3.6.2.4.(1) | 3.6.2.4. Incinerator Rooms | A service room containing an incinerator shall not contain other fuel-fired appliances. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.2.5.(1) | Combustible Refuse Storage | Except as required by Sentence 3.6.3.3.(9), a room for the storage of combustible refuse shall be separated from the remainder of the building by a fire separation with a fire-resistance rating not less than 1 h, and sprinklered. (See Note A-3.6.2.5.(1).) | obc2019_divb | Div B | 3.6.2.5.(1) | 3.6.2.5. Combustible Refuse Storage | Except as required by Sentence 3.6.3.3.(9), a room for the storage of combustible refuse shall be, separated from the remainder of the building by a fire separation with a fire-resistance rating not less than 1 h, and sprinklered. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.2.6.(1) | Door Swing for Service Rooms | A swing-type door from a service room containing a boiler or incinerator shall swing outward from the room, except that the door shall swing inward if the door opens onto a corridor or any room used for an assembly occupancy. (See also Sentence 3.4.4.4.(7).) | obc2019_divb | Div B | 3.6.2.6.(1) | 3.6.2.6. Door Swing for Service Rooms | A swing-type door from a service room containing a boiler or incinerator shall swing outward from the room, except that the door shall swing inward if the door opens onto a corridor or any room used for an assembly occupancy. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.2.7.(2) | Electrical Equipment Vaults | An electrical equipment vault referred to in Sentence (1) shall be separated from the remainder of the building by a fire separation of solid masonry or concrete construction having a fire-resistance rating not less than (a) 3 h if the vault is not protected by an automatic fire extinguishing system, or (b) 2 h if the vault is protected by an automatic fire extinguishing system. | obc2019_divb | Div B | 3.6.2.7.(1) | 3.6.2.7. Electrical Equipment Vaults | Where an electrical equipment vault is required by the Electrical Safety Code adopted under Ontario Regulation 164/99 (Electrical Safety Code) made under the Electricity Act, 1998, the electrical equipment vault shall be totally enclosed by a fire separation of solid masonry or concrete construction having a fire-resistance rating of not less than 3 h if the vault is not provided with an automatic fire extinguishing system and not less than 2 h if the vault is so protected. |  | Common Sentence | Yes | Referenced Standard
2015 | ON | NBC | Div B | 3.6.2.7.(3) | Electrical Equipment Vaults | If a building is sprinklered throughout, an electrical equipment vault referred to in Sentence 3.6.2.7.(1) need not be sprinklered provided the vault is designed for no purpose other than to contain the electrical equipment, and the vault contains a smoke detector which will actuate the building fire alarm system in the event of a fire in the vault. | obc2019_divb | Div B | 3.6.2.7.(2) | 3.6.2.7. Electrical Equipment Vaults | Where a building is required to be sprinklered, the electrical equipment vault described in Sentence (1) need not be sprinklered provided, the vault is designed for no purpose other than to contain the electrical equipment, and a smoke detector is provided in the vault that will actuate the building fire alarm system in the event of a fire in the vault. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.2.7.(4) | Electrical Equipment Vaults | Only pipes or ducts necessary for fire protection or the proper operation of the electrical installation shall penetrate the fire separation referred to in Sentence (2). | obc2019_divb | Div B | 3.6.2.7.(5) | 3.6.2.7. Electrical Equipment Vaults | Only pipes or ducts necessary for fire protection or the proper operation of the electrical installation shall penetrate the fire separations surrounding the electrical equipment vault. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.2.7.(5) | Electrical Equipment Vaults | Explosion-relief devices and vents or other protective measures conforming to Sentence 3.3.1.20.(3) shall be provided for an electrical equipment vault referred to in Sentence 3.6.2.7.(1) that contains dielectric-liquid-filled electrical equipment. (See Note A-3.6.2.7.(5).) | obc2019_divb | Div B | 3.6.2.7.(8) | 3.6.2.7. Electrical Equipment Vaults | Explosion-relief devices and vents or other protective measures shall be provided for every electrical equipment vault containing dielectric liquid filled electrical equipment in conformance with Sentence 3.3.1.19.(4). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.2.7.(6) | Electrical Equipment Vaults | An electrical equipment vault referred to in Sentence (1) shall be provided with a ventilation system designed in conformance with part 6. to prevent the ambient temperature in the vault from exceeding 40Â°C. | obc2019_divb | Div B | 3.6.2.7.(9) | 3.6.2.7. Electrical Equipment Vaults | Every electrical equipment vault shall be provided with a ventilation system designed in conformance with Part 6 to prevent the ambient temperature in the vault from exceeding 40Ã‚Â°C. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.2.7.(8) | Electrical Equipment Vaults | The floor of an electrical equipment vault referred to in Sentence (1) shall be liquid tight and surrounded by liquid tight walls and sills of sufficient height to confine within the vault all of the liquid from the largest item of electrical equipment, but to a height of not less than 100 mm. | obc2019_divb | Div B | 3.6.2.7.(14) | 3.6.2.7. Electrical Equipment Vaults | Except as permitted in Sentence (15), the floor of the electrical equipment vault described in Sentences (1) and (2) shall be liquid tight and surrounded by liquid tight walls and sills of sufficient height to confine within the vault all of the liquid from the largest item of electrical equipment, but to a height of not less than 100 mm. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.2.7.(9) | Electrical Equipment Vaults | Electrical equipment vaults shall be secured against unauthoroized entry. | obc2019_divb | Div B | 3.6.2.7.(7) | 3.6.2.7. Electrical Equipment Vaults | Each door to an electrical equipment vault shall be provided with a substantial lock or padlock. |  | Common Sentence | Yes | Building services and utilities
2015 | ON | NBC | Div B | 3.6.2.8.(1) | Emergency Power Installations | Where a generator intended to supply emergency power for lighting, fire safety and life safety systems is located in a building, except where such building is used solely for the purpose of housing the generator and its ancillary equipment, it shall be located in a room that (a) is separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 2 h, and (b) contains only the generating set and equipment related to the emergency power supply system. | obc2019_divb | Div B | 3.6.2.8.(1) | 3.6.2.8. Emergency Power Installations | Where a generator intended to supply emergency power for lighting, fire safety and life safety systems is located in a building, it shall be located in a room that, (a) is separated from the remainder of the building by a fire separation with a fire-resistance rating not less than, (i) 2 h for buildings within the scope of Subsection 3.2.6., and (ii) 1 h for other buildings, and (b) contains only the generating set and equipment that is related to the emergency power supply system. |  | Common Sentence | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.6.3.1.(1) | Fire Separations for Vertical Service Spaces | Except as provided in Articles 3.6.3.3. and 3.6.3.5. and Section 3.5., a vertical service space shall be separated from all other portions of each adjacent storey by a fire separation having a fire-resistance rating conforming to Table 3.6.3.1. for the fire-resistance rating required bySubsection 3.2.2. for (a) the floor assembly above the storey, or (b) the floor assembly below the storey, if there is no floor assembly above. | obc2019_divb | Div B | 3.6.3.1.(1) | 3.6.3.1. Fire Separations for Vertical Service Spaces | Except as provided in Section 3.5. and Articles 3.6.3.3. and 3.6.3.5., a vertical service space shall be separated from all other portions of each adjacent storey by a fire separation having a fire-resistance rating conforming to Table 3.6.3.1. for the fire-resistance rating required by Subsection 3.2.2. for, (a) the floor assembly above the storey, or(b) the floor assembly below the storey, if there is no floor assembly above. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.3.1.(2) | Fire Separations for Vertical Service Spaces | A vertical service space that does not extend through the roof of a building shall be enclosed at the top with construction having a fire-resistance rating not less than that required for the vertical service space walls. | obc2019_divb | Div B | 3.6.3.1.(2) | 3.6.3.1. Fire Separations for Vertical Service Spaces | A vertical service space that does not extend through the roof of a building shall be enclosed at the top with construction having a fire-resistance rating not less than that required for the vertical service space walls. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.3.1.(3) | Fire Separations for Vertical Service Spaces | A vertical service space that does not extend to the bottom of a building shall be enclosed at the lowest level with construction having a fire-resistance rating not less than that required for the vertical service space walls. | obc2019_divb | Div B | 3.6.3.1.(3) | 3.6.3.1. Fire Separations for Vertical Service Spaces | A vertical service space that does not extend to the bottom of a building shall be enclosed at the lowest level with construction having a fire-resistance rating not less than that required for the vertical service space walls. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.3.1.(4) | Fire Separations for Vertical Service Spaces | A vent from a vertical service space not extending to the roof shall be enclosed within the building with construction having a fire-resistance rating not less than that required for the vertical service space walls. | obc2019_divb | Div B | 3.6.3.1.(4) | 3.6.3.1. Fire Separations for Vertical Service Spaces | A vent from a vertical service space not extending to the roof shall be enclosed within the building with construction having a fire-resistance rating not less than that required for the vertical service space walls. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.3.1.(5) | Fire Separations for Vertical Service Spaces | Only openings that are necessary for the use of the vertical service space shall be permitted through a vertical service space enclosure. | obc2019_divb | Div B | 3.6.3.1.(5) | 3.6.3.1. Fire Separations for Vertical Service Spaces | Only openings that are necessary for the use of the vertical service space shall be permitted through a vertical service space enclosure. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.3.2.(1) | Foamed Plastic Protection | Foamed plastic insulation in a vertical service space shall be protected in conformance with Article 3.1.5.14. | obc2019_divb | Div B | 3.6.3.2.(1) | 3.6.3.2. Foamed Plastic Protection | Foamed plastic insulation in a vertical service space shall be protected in conformance with Article 3.1.5.12A. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.3.3.(1) | Linen and Refuse Chutes | A linen chute or refuse chute shall be impervious to moisture, have a smooth internal surface, be corrosion-resistant, be constructed of noncombustible material, and be located in a shaft in which there are no services other than noncombustible drain, waste and vent piping or noncombustible water piping. | obc2019_divb | Div B | 3.6.3.3.(1) | 3.6.3.3. Linen and Refuse Chutes | A linen chute or refuse chute shall, be impervious to moisture, have a smooth internal surface, be corrosion-resistant, be constructed of noncombustible material, and be located in a shaft in which there are no services other than noncombustible drain, waste and vent piping or noncombustible water piping. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.3.3.(10) | Linen and Refuse Chutes | The room or bin into which a refuse chute discharges shall be of sufficient size to contain the refuse between normal intervals of emptying, be impervious to moisture and be equipped with a water connection and floor drain for washing-down purposes. | obc2019_divb | Div B | 3.6.3.3.(10) | 3.6.3.3. Linen and Refuse Chutes | The room or bin into which a refuse chute discharges shall be of sufficient size to contain the refuse between normal intervals of emptying, be impervious to moisture and be equipped with a water connection and floor drain for washing-down purposes. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.3.3.(11) | Linen and Refuse Chutes | A room into which a refuse chute discharges shall contain no service equipment that is not related to refuse handling and disposal. | obc2019_divb | Div B | 3.6.3.3.(11) | 3.6.3.3. Linen and Refuse Chutes | A room into which a refuse chute discharges shall contain no service equipment that is not related to refuse handling and disposal. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.3.3.(2) | Linen and Refuse Chutes | A shaft containing a linen chute or refuse chute shall have a fire-resistance rating conforming to Sentence 3.6.3.1.(1), but not less than 1 h if the chute outlet for the discharge room is protected by an automatic, self-latching closure held open by a fusible link, or 2 h if no closure is provided at the chute outlet into the discharge room. | obc2019_divb | Div B | 3.6.3.3.(2) | 3.6.3.3. Linen and Refuse Chutes | A shaft containing a linen chute or refuse chute shall have a fire-resistance rating conforming to Sentence 3.6.3.1.(1), but not less than, 1 h if the chute outlet for the discharge room is protected by an automatic, self-latching closure held open by a fusible link, or 2 h if no closure is provided at the chute outlet into the discharge room. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.3.3.(3) | Linen and Refuse Chutes | An interior linen chute or refuse chute shall extend not less than 1 m above the roof and shall be vented above the roof with a vent which has an unobstructed area not less than the cross-sectional area of the chute, and is equipped with a cover that will open automatically, or that can be opened manually, in the event of a fire in the chute. | obc2019_divb | Div B | 3.6.3.3.(3) | 3.6.3.3. Linen and Refuse Chutes | An interior linen chute or refuse chute shall extend not less than 1 m above the roof and shall be vented above the roof with a vent that, has an unobstructed area not less than the cross-sectional area of the chute, and is equipped with a cover that will open automatically, or that can be opened manually, in the event of a fire in the chute. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.3.3.(4) | Linen and Refuse Chutes | Intake openings for a linen chute or a refuse chute shall have an area not more than 60% of the cross-sectional area of the chute, and be fitted with closures designed to close automatically and latch after use. | obc2019_divb | Div B | 3.6.3.3.(4) | 3.6.3.3. Linen and Refuse Chutes | Intake openings for a linen chute or a refuse chute shall, have an area not more than 60% of the cross-sectional area of the chute, and be fitted with closures designed to close automatically and latch after use. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.3.3.(5) | Linen and Refuse Chutes | Intake openings for a linen chute or a refuse chute shall be located in rooms or compartments that have no dimension less than 750 mm, are separated from the remainder of the building by a fire separation with a fire-resistance rating not less than 45 min, are designed for no other purpose, and do not open directly into an exit. | obc2019_divb | Div B | 3.6.3.3.(5) | 3.6.3.3. Linen and Refuse Chutes | Intake openings for a linen chute or a refuse chute shall be located in rooms or compartments that, have no dimension less than 750 mm, are separated from the remainder of the building by a fire separation with a fire-resistance rating not less than 45 min, are designed for no other purpose, and do not open directly into an exit. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.3.3.(6) | Linen and Refuse Chutes | Sprinklers shall be installed at the top of each linen chute or refuse chute, at alternate floor levels and in the room or bin into which the chute discharges. | obc2019_divb | Div B | 3.6.3.3.(6) | 3.6.3.3. Linen and Refuse Chutes | Sprinklers shall be installed at the top of each linen chute or refuse chute, at alternate floor levels and in the room or bin into which the chute discharges. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.3.3.(7) | Linen and Refuse Chutes | The room into which a linen chute discharges shall be separated from the remainder of the building by a fire separation with a fire-resistance rating not less than 1 h. | obc2019_divb | Div B | 3.6.3.3.(7) | 3.6.3.3. Linen and Refuse Chutes | The room into which a linen chute discharges shall be separated from the remainder of the building by a fire separation with a fire-resistance rating not less than 1 h. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.3.3.(8) | Linen and Refuse Chutes | A refuse chute shall be equipped at the top with spray equipment for washing-down purposes. | obc2019_divb | Div B | 3.6.3.3.(8) | 3.6.3.3. Linen and Refuse Chutes | A refuse chute shall be equipped at the top with spray equipment for washing-down purposes. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.3.3.(9) | Linen and Refuse Chutes | A refuse chute shall discharge only into a room or bin separated from the remainder of the building by a fire separation with a fire-resistance rating not less than 2 h. | obc2019_divb | Div B | 3.6.3.3.(9) | 3.6.3.3. Linen and Refuse Chutes | A refuse chute shall discharge only into a room or bin separated from the remainder of the building by a fire separation with a fire-resistance rating not less than 2 h. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.3.4.(1) | Exhaust Duct Negative Pressure | If a vertical service space contains an exhaust duct that serves more than one fire compartment, (a) the duct shall have a fan located at or near the exhaust outlet to ensure that the duct is under negative pressure, and (b) theindividual fire compartments shall not have individual fans that exhaust directly into the duct in the vertical service space. | obc2019_divb | Div B | 3.6.3.4.(1) | Exhaust Duct Negative Pressure | If a vertical service space contains an exhaust duct that serves more than one fire compartment, the duct shall have a fan located at or near the exhaust outlet to ensure that the duct is under negative pressure |  | Common Sentence | Yes | HVAC
2015 | ON | NBC | Div B | 3.6.3.5.(1) | Grease Duct Enclosures | Except as provided in Sentence (2), fire separations enclosing grease ducts for commercial cooking operations shall conform to NFPA 96-2014 Ventilation Control and Fire Protection of Commercial Cooking Operations | obc2019_divb | Div B | 3.6.3.5.(1) | 3.6.3.5. Grease Duct Enclosures (See Appendix A.) | Except as provided in Sentence (2), fire separations enclosing grease ducts for commercial cooking operations shall conform to NFPA 96, "Ventilation Control and Fire Protection of Commercial Cooking Operations". |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.3.5.(2) | Grease Duct Enclosures | The fire-resistance rating of field-applied and factory-built grease duct enclosure assemblies shall be determined in conformance with ULC CAN/ULC-S144 Fire Resistance Test â€“ Grease Duct Assemblies | obc2019_divb | Div B | 3.6.3.5.(2) | 3.6.3.5. Grease Duct Enclosures (See Appendix A.) | The fire-resistance rating of field-applied and factory-built grease duct enclosure assemblies shall be determined in conformance with CAN/ULC-S144, "Fire Resistance Test - Grease Duct Assemblies". |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.4.1.(1) | Scope | This Subsection applies to horizontal service spaces and service facilities, including ceiling spaces, duct spaces, crawl spaces and attic or roof spaces. | obc2019_divb | Div B | 3.6.4.1.(1) | 3.6.4.1. Scope | This Subsection applies to horizontal service spaces and service facilities, including ceiling spaces, duct spaces, crawl spaces and attic or roof spaces. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.4.2.(1) | Fire Separations for Horizontal Service Spaces | Except as provided in Article 3.6.3.5., a horizontal service space that penetrates a required vertical fire separation shall be separated from the remainder of the building it serves in conformance with Sentence (2). | obc2019_divb | Div B | 3.6.4.2.(1) | 3.6.4.2. Fire Separations for Horizontal Service Spaces | Except as provided in Article 3.6.3.5., a horizontal service space that penetrates a required vertical fire separation shall be separated from the remainder of the building it serves in conformance with Sentence (2). |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.4.2.(2) | Fire Separations for Horizontal Service Spaces | If a horizontal service space or other concealed space is located above a required vertical fire separation other than a vertical shaft, this space need not be divided at the fire separation as required by Article 3.1.8.3. provided the construction between this space and the space below is a fire separation with a fire-resistance rating equivalent to that required for the vertical fire separation, except that the fire-resistance rating is permitted to be not less than 30 min if the vertical fire separation is not required to have a fire-resistance rating more than 45 min. (See Note A-3.6.4.2.(2).) | obc2019_divb | Div B | 3.6.4.2.(2) | 3.6.4.2. Fire Separations for Horizontal Service Spaces | If a horizontal service space or other concealed space is located above a required vertical fire separation other than a vertical shaft, this space need not be divided at the fire separation as required by Article 3.1.8.3. provided the construction between this space and the space below is a fire separation with a fire-resistance rating equivalent to that required for the vertical fire separation, except that the fire-resistance rating is permitted to be not less than 30 min if the vertical fire separation is not required to have a fire-resistance rating more than 45 min. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.4.3.(1) | 3.6.4.3. Plenum Requirements | Aconcealedspaceusedasaplenum within afloor assembly or within a roof assembly need not conformto Sentence 3.1.5.18.(1 )and Article 3.6.5.1., provided (a) all materials within the concealed space have a flame-spreadrating not more than 25 and a smoke developed classification not more than 50, except for (i) tubing for pneumatic controls, (ii) optical fibre cables and electrical wires and cables with combustible insulation, jackets or sheathes that are used for the transmission of voice, sound or data and conform to Sentences 3.1.4.3.(2) and 3.1.5.21.(2), (iii) totally enclosed non-metallic raceways with an FT6 rating, when tested in accordance with Clause 3.1.5.23.(1)(a), in buildings required to be of noncombustible construction ,and (iv) totally enclosed non-metallic raceways with an FT4 rating, when tested in accordance with Clause 3.1.5.23.(1)(a), in buildings permitted to be of combustible construction, and (b) the supports for the ceiling membrane are of noncombustible material having a melting point not below 760°C. | obc2019_divb | Div B | 3.6.4.3.(1) | 3.6.4.3. Plenum Requirements | A concealed space used as a plenum within a floor assembly or within a roof assembly need not conform to Sentence 3.1.5.15.(1) and Article 6.2.3.2. provided, (a) all materials within the concealed space have a flame-spread rating not more than 25 and a smoke developed classification not more than 50, except for, (i) tubing for pneumatic controls, (ii) optical fibre cables and electrical wires and cables that exhibit a flame spread not more than 1.5 m, a smoke density not more than 0.5 at peak optical density and a smoke density not more than 0.15 at average optical density when tested in conformance with the Flame and Smoke Test in the Appendix to CSA C22.2 No. 0.3, "Test Methods for Electrical Wires and Cables", (FT6 Rating), (iii) optical fibre cables and electrical wires and cables that are located in totally enclosed noncombustible raceways, (iv) totally enclosed nonmetallic raceways that exhibit a horizontal flame distance of not more than 1.5 m, an average optical smoke density of not more than 0.15 and a peak optical smoke density of not more than 0.5 when tested in conformance with CAN/ULC-S102.4, "Fire and Smoke Characteristics of Electrical Wiring, Cables and Non-Metallic Raceways", (FT6 Rating), and (v) single conductor electrical wires and cables that exhibit a vertical char of not more than 1.5 m when tested in conformance with the Vertical Flame Test Ã¢â‚¬"Cables in Cabletrough in Clause 4.11.4. of CSA C22.2 No. 0.3, "Test Methods for Electrical Wires and Cables", (FT4 Rating), and (b) the supports for the ceiling membrane are of noncombustible material having a melting point not below 760Ã‚Â°C. |  | Common Sentence | Yes | Construction Materials
2015 | ON | NBC | Div B | 3.6.4.3.(2) | Plenum Requirements | If a concealed space referred to in Sentence (1) is used as a return-air plenum and incorporates a ceiling membrane that forms part of the required fire-resistance rating of the assembly, every opening through the membrane shall be protected by a fire stop flap that (a) stops the flow of air into the concealed space in the event of a fire, (b) is supported in a manner that will maintain the integrity of the ceiling membrane for the duration of time required to provide the required fire-resistance rating, (c) conforms to ULC CAN/ULC-S112.2 Fire Test of Ceiling Firestop Flap Assemblies and (d) activates at a temperature approximately 30Â°C above the normal maximum temperature that occurs in the return-air plenum, whether the air duct system is operating or shut down. | obc2019_divb | Div B | 3.6.4.3.(2) | 3.6.4.3. Plenum Requirements | If a concealed space referred to in Sentence (1) is used as a return-air plenum and incorporates a ceiling membrane that forms part of the required fire-resistance rating of the assembly, every opening through the membrane shall be protected by a fire stop flap that shall, (a) stop the flow of air into the concealed space in the event of a fire, (b) be supported in a manner that will maintain the integrity of the ceiling membrane for the duration of time required to provide the required fire-resistance rating, (c) conform to CAN/ULC-S112.2, "Fire Test of Ceiling Firestop Flap Assemblies", and (d) activate at a temperature approximately 30Ã‚Â°C above the normal maximum temperature that occurs in the return-air plenum, whether the air duct system is operating or shut down. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.4.4.(1) | Attic or Roof Space Access | An attic or roof space more than 600 mm high shall be provided with access from the floor immediately below by a hatchway not less than 550 mm by 900 mm or by a stairway. | obc2019_divb | Div B | 3.6.4.4.(1) | 3.6.4.4. Attic or Roof Space Access | An attic or roof space more than 600 mm high shall be provided with access from the floor immediately below by a hatchway not less than 550 mm by 900 mm or by a stairway. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.4.5.(1) | Horizontal Service Space Access | A horizontal service space, consisting of ceiling and duct spaces, which is more than 1?200 mm high and 600 mm wide shall have inspection doors not less than 300 mm in both horizontal and vertical dimensions placed so that the entire interior of the duct or space can be viewed. | obc2019_divb | Div B | 3.6.4.5.(1) | 3.6.4.5. Horizontal Service Space Access | A horizontal service space, consisting of ceiling and duct spaces, that is more than 1 200 mm high and 600 mm wide shall have inspection doors not less than 300 mm in both horizontal and vertical dimensions placed so that the entire interior of the duct or space can be viewed. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.6.4.6.(1) | Crawl Space Access | A crawl space shall have at least one access opening not less than 550 mm by 900 mm. | obc2019_divb | Div B | 3.6.4.6.(1) | 3.6.4.6. Crawl Space Access | A crawl space shall have at least one access opening not less than 550 mm by 900 mm. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.7.1.1.(1) | Room and Space Height | The height of every room and space shall be sufficient so that the ceiling or ceiling fixtures do not obstruct movement or activities below. | obc2019_divb | Div B | 3.7.1.1.(1) | 3.7.1.1. Room and Space Height | The height of every room and space shall be sufficient so that the ceiling or ceiling fixtures do not obstruct movement or activities below. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.7.1.1.(2) | Room and Space Height | The unobstructed height in dwelling units shall conform to Subsection 9.5.3. | obc2019_divb | Div B | 3.7.1.1.(2) | 3.7.1.1. Room and Space Height | The unobstructed height in dwelling units and sleeping rooms in Group C occupancies shall conform to Subsection 9.5.3. |  | Common Sentence | Yes | Risk of Collision
2015 | ON | NBC | Div B | 3.7.2.1.(1) | Plumbing and Drainage Systems | Except as permitted in Sentence 3.7.2.1.(2), if the installation of a sanitary drainage system is not possible because of the absence of a water supply, sanitary privies, chemical closets or other means for the disposal of human waste shall be provided. | obc2019_divb | Div B | 3.7.4.1.(2) | 3.7.4.1. Plumbing and Drainage Systems | When the installation of a sanitary drainage system is not possible because of the absence of a water supply, sanitary privies, chemical closets or other means for the disposal of human waste shall be provided. |  | Common Sentence | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B | 3.7.2.2.(1) | Water Closets | Except as permitted by Sentence 3.7.2.2.(4), water closets shall be provided for each sex assuming that the occupant load is equally divided between males and females, unless the proportion of each sex expected in the building can be determined with reasonable accuracy. (See Note A-3.7.2.2.(1).) | obc2019_divb | Div B | 3.7.4.2.(2) | 3.7.4.2. Plumbing Fixtures, General | Except as provided in this Subsection, water closets shall be provided for each sex assuming that the occupant load is equally divided between males and females, unless the proportion of each sex expected in the building can be determined with reasonable accuracy. |  | Common Sentence | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B | 3.7.2.2.(10) | Water Closets | Except as permitted by Sentences (4) and (7), the number of water closets required for a care or residential occupancy shall be at least one for each 10 persons of each sex. | obc2019_divb | Div B | 3.7.4.6.(1) | 3.7.4.6. Plumbing Fixtures for Other Residential Occupancies | Except for dwelling units and as provided in Sentence (2), the number of water closets required for residential occupancies shall conform to Table 3.7.4.6. |  | Common Sentence | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B | 3.7.2.2.(11) | Water Closets | At least one water closet shall be provided for each dwelling unit. | obc2019_divb | Div B | 3.7.4.5.(1) | 3.7.4.5. Plumbing Facilities for Dwelling Units | A dwelling unit where a piped water supply is available shall be provided with a, (a) kitchen sink, (b) lavatory, (c) water closet or drainless composting water closet, and (d) bathtub or shower stall. |  | Common Sentence | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B | 3.7.2.2.(12) | Water Closets | Except as permitted by Sentence 3.7.2.2.(4), the number of water closets required for a business and personal services occupancy shall conform to Table 3.7.2.2.-B. | obc2019_divb | Div B | 3.7.4.7.(1) | 3.7.4.7. Plumbing Fixtures for Business and Personal Services | Except as provided in Sentence (2), the number of water closets required for business and personal services occupancies shall conform to Table 3.7.4.7. |  | Common Sentence | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B | 3.7.2.2.(13) | Plumbing Facilities | Except as permitted by Sentences (4) and (16), the number of water closets required for a mercantile occupancy shall be atleast one for each 300 males and one for each 150 females. | obc2019_divb | Div B | 3.7.4.8.(2) | 3.7.4.8. Plumbing Fixtures for Mercantile Occupancies | Except as provided in Sentence (4), the number of water closets required for the public in mercantile occupancies shall be at least one fixture for each 300 males and one fixture for each 150 females, except that, (a) water closets provided for employees are permitted to be counted as part of those required for the public when these water closets are made accessible to the public, and (b) where the total area of the mercantile occupancy, excluding basements, is not more than 600 m2, not more than one water closet for each sex need be provided. |  | Common Sentence | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B | 3.7.2.2.(14) | Water Closets | Except as permitted by Sentence 3.7.2.2.(4), the number of water closets required for an industrial occupancy shall conform to Table 3.7.2.2.-C. | obc2019_divb | Div B | 3.7.4.9.(1) | 3.7.4.9. Plumbing Fixtures for Industrial Occupancies | Except as provided in Sentence (2), the number of water closets and lavatories required for industrial occupancies shall conform to Table 3.7.4.9. |  | Common Sentence | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B | 3.7.2.2.(2) | Water Closets | If a single universal washroom is provided in accordance with the requirements of Section 3.8., the total number of persons in the building used to determine the number of water closets to be provided, is permitted to be reduced by 10 before applying Sentence (6), (7), (8), (12), (13) or (14). | obc2019_divb | Div B | 3.7.4.2.(7) | 3.7.4.2. Plumbing Fixtures, General | The water closet and lavatory provided in the universal washroom described in Sentence 3.8.3.12.(1) may be counted as part of the plumbing fixtures required for males and females in this Subsection if, more than one water closet is required for males, and more than one water closet is required for females. |  | Common Sentence | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B | 3.7.2.2.(4) | Water Closets | Both sexes are permitted to be served by a single water closet if the occupant load in an occupancy referred to in Sentence 3.7.2.2.(6) , 3.7.2.2.(10) , 3.7.2.2.(12) , 3.7.2.2.(13) , 3.7.2.2.(14) or 3.7.2.2.(16) is not more than 10. | obc2019_divb | Div B | 3.7.4.2.(9) | 3.7.4.2. Plumbing Fixtures, General | Both sexes are permitted to be served by a single water closet if the occupant load is not more than 10 persons in an assembly occupancy referred to in Article 3.7.4.3. except for, elementary and secondary schools, child care facilities, places of worship, and undertaking premises. |  | Common Sentence | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B | 3.7.2.2.(4) | Water Closets | Both sexes are permitted to be served by a single water closet if the occupant load in an occupancy referred to in Sentence 3.7.2.2.(6) , 3.7.2.2.(10) , 3.7.2.2.(12) , 3.7.2.2.(13) , 3.7.2.2.(14) or 3.7.2.2.(16) is not more than 10. | obc2019_divb | Div B | 3.7.4.8.(3) | 3.7.4.8. Plumbing Fixtures for Mercantile Occupancies | Not more than one water closet to serve both sexes need be provided in a Group E occupancy where, (a) the occupant load is not more than nine persons, or (b) where the total area of the occupancy, excluding basements, is not more than 300 m2. |  | Common Sentence | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B | 3.7.2.2.(4) | Water Closets | Both sexes are permitted to be served by a single water closet if the occupant load in an occupancy referred to in Sentence 3.7.2.2.(6) , 3.7.2.2.(10) , 3.7.2.2.(12) , 3.7.2.2.(13) , 3.7.2.2.(14) or 3.7.2.2.(16) is not more than 10. | obc2019_divb | Div B | 3.7.4.9.(2) | 3.7.4.9. Plumbing Fixtures for Industrial Occupancies | Not more than one water closet to serve both sexes need be provided in a Group F occupancy where, (a) the occupant load is not more than 10 persons, or (b) the total area of the occupancy, excluding basements, is not more than 300 m2. |  | Common Sentence | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B | 3.7.2.2.(4) | Water Closets | Both sexes are permitted to be served by a single water closetif the occupant load inan occupancy referred to in Sentence (6), (10), (12), (13), (14) or (16) is not more than 10. | obc2019_divb | Div B | 3.7.4.7.(2) | 3.7.4.7. Plumbing Fixtures for Business and Personal Services | Not more than one water closet to serve both sexes need be provided in a Group D occupancy having an occupant load of not more than 10 persons. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.7.2.2.(5) | Water Closets | Urinals are permitted to be substituted for two thirds of the number of water closets required by this Article for males, except that if only 2 water closets are required for males, one urinal is permitted to be substituted for one of the water closets. | obc2019_divb | Div B | 3.7.4.2.(3) | 3.7.4.2. Plumbing Fixtures, General | Except as provided in Sentence (4), urinals are permitted to be substituted for water closets required by this Subsection for males and may be counted as water closets provided the number of urinals is not more than, (a) one-fifth of the required number of water closets in hospitals and long-term care homes, and (b) two-thirds of the required number of water closets in any other occupancy. |  | Common Sentence | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B | 3.7.2.2.(5) | Water Closets | Urinals are permitted to be substituted for two thirds of the number of water closets required by this Article for males, except that if only 2 water closets are required for males, one urinal is permitted to be substituted for one of the water closets. | obc2019_divb | Div B | 3.7.4.2.(4) | 3.7.4.2. Plumbing Fixtures, General | If only two water closets are required for males, one urinal is permitted to be substituted for one of the water closets. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.7.2.2.(6) | Water Closets | Except as permitted by Sentences 3.7.2.2.(4) , 3.7.2.2.(7) and 3.7.2.2.(8), the number of water closets required for assembly occupancies shall conform to Table 3.7.2.2.-A. | obc2019_divb | Div B | 3.7.4.3.(1) | 3.7.4.3. Plumbing Fixtures for Assembly Occupancies | Except as provided by Sentences (2) to (16) and Sentence 3.7.4.2.(9), the number of water closets required for assembly occupancies shall conform to Table 3.7.4.3.A. |  | Common Sentence | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B | 3.7.2.2.(7) | Water Closets | The number of water closets required for primary schools and daycare centres shall be at least one for each 30 males and one for each 25 females. | obc2019_divb | Div B | 3.7.4.3.(13) | 3.7.4.3. Plumbing Fixtures for Assembly Occupancies | In a child care facility the maximum number of children per water closet and lavatory shall conform to Table 3.7.4.3.I. |  | Common Sentence | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B | 3.7.2.2.(7) | Water Closets | The number of water closets required for primary schools and daycare centres shall be at least one for each 30 males and one for each 25 females. | obc2019_divb | Div B | 3.7.4.3.(14) | 3.7.4.3. Plumbing Fixtures for Assembly Occupancies | The number of water closets required for elementary and secondary schools shall be at least one fixture for each 30 males and one fixture for each 26 females. |  | Common Sentence | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B | 3.7.2.2.(8) | Water Closets | The number of water closets required for places of worship and undertaking premises shall be at least one for each 150 persons of each sex. | obc2019_divb | Div B | 3.7.4.3.(16) | 3.7.4.3. Plumbing Fixtures for Assembly Occupancies | The number of water closets required for places of worship and undertaking premises shall be at least one fixture for each 150 persons of each sex. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.7.2.2.(9) | Water Closets | The number of water closets required for a treatment or detention occupancy shall be determined on the basis of the special needs of the occupancy. | obc2019_divb | Div B | 3.7.4.4.(1) | 3.7.4.4. Plumbing Fixtures for Care, Care and Treatment or | The number of water closets and lavatories required for Group B, Division 1 occupancies shall be determined on the basis of the special needs of these occupancies. |  | Common Sentence | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B | 3.7.2.2.(9) | Water Closets | The number of water closets required for a treatment or detention occupancy shall be determined on the basis of the special needs of the occupancy. Except as permitted by Sentences (4) and (7), the number of water closets required for a care or residential occupancy shall be at least one for each 10 persons of each sex. | obc2019_divb | Div B | 3.7.4.4.(2) | 3.7.4.4. Plumbing Fixtures for Care, Care and Treatment or | In a Group B, Division 2 or 3 occupancy, washrooms shall be provided so that each washroom, (a) serves not more than four patients or residents, (b) is accessible from patients’ or residents’ sleeping rooms, (c) contains one water closet, and (d) contains one lavatory. |  | Common Sentence | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B | 3.7.2.3.(1) | Lavatories | Except as permitted by Sentence 3.7.2.3.(2), at least one lavatory shall be provided in a room containing one or 2 water closets or urinals, and at least one additional lavatory shall be provided for each additional 2 water closets or urinals. | obc2019_divb | Div B | 3.7.4.2.(5) | 3.7.4.2. Plumbing Fixtures, General | Except as required in this Subsection, at least one lavatory shall be provided in a room containing one or two water closets or urinals, and at least one additional lavatory shall be provided for each additional two water closets or urinals. |  | Common Sentence | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B | 3.7.2.3.(2) | Lavatories | Wash fountains in circular form are permitted to be provided in lieu of lavatories required by Sentence 3.7.2.3.(1) provided each 500 mm of circumference is considered to be the equivalent of one lavatory. | obc2019_divb | Div B | 3.7.4.2.(6) | 3.7.4.2. Plumbing Fixtures, General | Wash fountains in circular or straight trough form are permitted to be provided in lieu of required lavatories provided each 500 mm of circumference or trough length is considered to be the equivalent of one lavatory. |  | Common Sentence | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B | 3.7.2.3.(3) | Lavatories | Any shelf or projection above a lavatory shall be located so that it will not be a hazard. | obc2019_divb | Div B | 3.8.3.11.(4) | 3.8.3.11. Lavatories, Mirrors and Washroom Accessories (See | Where a shelf is installed above a lavatory required by Sentence (1), it shall, be located not more than 200 mm above the top of the lavatory and not more than 1 100 mm above the finished floor, and project not more than 100 mm from the wall. |  | Common Sentence | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B | 3.7.2.3.(3) | Lavatories | Any shelf or projection above a lavatory shall be located so that it will not be a hazard. | obc2019_divb | Div B | 3.7.4.2.(10) | 3.7.4.2. Plumbing Fixtures, General | Any shelf or projection above a lavatory shall be located so that it will not be a hazard. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.7.2.3.(4) | Lavatories | Lavatories required by Sentence 3.7.2.3.(1) shall be equipped with faucets that operate automatically, or have a manual control that complies with Sentence 3.8.3.8.(1), does not require the application of continuous force to maintain water flow, and where metered, provides at least 10 s of water flow. | obc2019_divb | Div B | 3.7.4.2.(11) | 3.7.4.2. Plumbing Fixtures, General | Except for dwelling units, lavatories required by Sentence (5) shall be equipped with faucets that, operate automatically, or have a manual control that, has a lever type handle or is otherwise operable with a closed fist, does not require the application of continuous force to maintain water flow, and where metered, provides at least 10 s of water flow. |  | Common Sentence | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B | 3.7.2.4.(1) | Mobile Home Facilities | If mobile homes do not have individual sanitary facilities connected to a central water supply and drainage system, a service building shall be provided for public use. | obc2019_divb | Div B | 3.7.4.10.(1) | 3.7.4.10. Plumbing Fixtures for Mobile Home Facilities | If mobile homes do not have individual plumbing facilities connected to a central water supply and drainage system, a service building shall be provided for public use. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.7.2.4.(2) | Mobile Home Facilities | The service building required by Sentence 3.7.2.4.(1) shall contain at least one water closet for each sex if the service building facilities serve not more than 10 mobile homes, and an additional water closet for each sex for each additional 10 mobile homes. | obc2019_divb | Div B | 3.7.4.10.(2) | 3.7.4.10. Plumbing Fixtures for Mobile Home Facilities | The service building required by Sentence (1) shall contain, (a) at least one water closet for each sex if the service building facilities serve not more than 10 mobile homes, and (b) an additional water closet for each sex for each additional 10 mobile homes. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.7.2.4.(3) | Mobile Home Facilities | If a service building is required by Sentence 3.7.2.4.(1), it shall contain lavatories as required by Sentence 3.7.2.3.(1) and at least one laundry tray or similar facility, and one bathtub or shower for each sex. | obc2019_divb | Div B | 3.7.4.10.(3) | 3.7.4.10. Plumbing Fixtures for Mobile Home Facilities | If a service building is required by Sentence (1) it shall contain lavatories as required by Sentence 3.7.4.2.(5) and at least, one laundry tray or similar facility, and one bathtub or shower for each sex. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.7.2.5.(1) | Safety Glass | Glass, other than safety glass, shall not be used for a shower or bathtub enclosure. | obc2019_divb | Div B | 3.7.4.11.(1) | 3.7.4.11. Safety Glass | Glass, other than safety glass, shall not be used for a shower or bathtub enclosure. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.7.2.6.(1) | Surface Protection | Wall and floor surfaces below the uppermost surfaces of a urinal shall be protected from deterioration by impervious and durable material for a distance from the urinal to a point not less than 900 mm from the projected outline of the urinal on to the wall or floor. | obc2019_divb | Div B | 3.7.4.12.(1) | 3.7.4.12. Surface Protection | Wall and floor surfaces below the uppermost surfaces of urinals shall be protected from deterioration by impervious and durable material for a distance from the urinal to a point not less than 900 mm from the projected outline of the urinal on to the wall or floor. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.7.2.6.(2) | Surface Protection | Floor surfaces around a water closet shall be protected from deterioration by an impervious and durable material for a distance not less than 900 mm from the projected outline of the water closet on the floor. | obc2019_divb | Div B | 3.7.4.12.(2) | 3.7.4.12. Surface Protection | Floor surfaces around a water closet shall be protected from deterioration by impervious and durable material for a distance not less than 900 mm from the projected outline of the water closet on to the floor. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.7.2.7.(1) | Floor Drain | A floor drain shall be installed in a washroom containing a urinal equipped with an automatic flushing device. | obc2019_divb | Div B | 3.7.4.13.(1) | 3.7.4.13. Floor Drains | A floor drain shall be installed in a washroom for public use that contains a urinal or a water closet equipped with an automatic flushing device. (See Appendix A.) |  | Common Sentence | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B | 3.7.2.8.(1) | Grab Bars | 1 ) Grab bars shall a) be slip-resistant and free of any sharp or abrasive elements, b) be mounted on surfaces that are free of any sharp or abrasive elements, c) be able to resist a load of not less than 1.3 kN applied vertically or horizon tally, d) be 30 mm to 40 mm in diameter, and e) where mounted on a wall, have a clearance of 35 mm to 45 mm from the wall. | obc2019_divb | Div B | 3.7.4.14.(1) | 3.7.4.14. Grab Bar Installation | Grab bars that are installed shall resist a minimum load of 1.3 kN applied vertically or horizontally. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.7.2.8.(1) | Grab Bars | Grab bars shall (a) be slip-resistant and free of any sharp or abrasive elements, (b) be mounted on surfaces that are free of any sharp or abrasive elements, (c) be able to resist a load of not less than 1.3kN applied vertically or horizontally, (d) be 30 mm to 40 mm in diameter, and (e) where mounted on awall, have a clearance of 35 mm to 45 mm from the wall. | obc2019_divb | Div B | 3.8.3.8.(8) | 3.8.3.8. Water Closet Stalls and Enclosures | A fold-down grab bar described in Clause (3)(b) or (4)(a) shall, be mounted on the wall behind the water closet, with the horizontal component 750 mm above the finished floor, and not less than 390 mm and not more than 410 mm from the centre line of the water closet, not require a force of more than 22.2 N to pull it down, be at least 750 mm in length, be installed to resist a load of at least 1.3 kN applied vertically or horizontally, be not less than 30 mm and not more than 40 mm in diameter, and have a slip-resistant surface. (See A-3.8.3.8.(3) and A-3.8.3.8.(8) in Appendix A.) |  | Common Sentence | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B | 3.7.2.8.(1) | Grab Bars | Grab bars shall (a) be slip-resistant and free of any sharp or abrasive elements, (b) be mounted on surfaces that are free of any sharp or abrasive elements, (c) be able to resist a load of not less than 1.3kN applied vertically or horizontally, (d) be 30 mm to 40 mm in diameter, and (e) where mounted on awall, have a clearance of 35 mm to 45 mm from the wall. | obc2019_divb | Div B | 3.8.3.8.(7) | 3.8.3.8. Water Closet Stalls and Enclosures | A grab bar described in Clause (3)(a) or (c) or (4)(b) shall, be installed to resist a load of at least 1.3 kN applied vertically or horizontally, be not less than 30 mm and not more than 40 mm in diameter, have a clearance of not less than 38 mm and not more than 50 mm from the wall to the inside surface of the grab bar, and have a slip-resistant surface. |  | Common Sentence | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B | 3.7.3.1.(1) | Medical Gas Piping | If a non-flammable medical gas piping system is installed, it shall be installed in conformance with (a) CSA Z7396.1-12 Medical Gas Pipeline Systems Part 1: Pipelines for Medical Gases, Medical Vacuum, Medical Support Gases, and Anaesthetic Gas Scavenging Systems and (b) Part 3 of Division B of the NFC. | obc2019_divb | Div B | 3.7.5.2.(1) | 3.7.5.2. Medical Gas Piping | All medical gas piping systems shall be designed, constructed, installed and tested in conformance with, (a) CSA Z7396.1, "Medical Gas Piping Systems - Part 1: Pipelines for Medical Gases, Medical Vacuum, Medical Support Gases, and Anaesthetic Gas Scavenging Systems", and (b) the provisions of the Fire Code made under the Fire Protection and Prevention Act, 1997 or, in the absence of such provisions, Part 3 of Division B of the CCBFC NRCC 56192, "National Fire Code of Canada". |  | Common Sentence | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B | 3.8.2.1.(1) | Exceptions | The requirements of this Section apply to all buildings except (a) detached houses, semi-detached houses, houses with a secondary suite, duplexes, triplexes, townhouses, row houses and boarding houses (see Note A-1.4.1.2.(1), Secondary Suite), (b) buildings of Group F, Division 1 major occupancy, and (c) buildings that are not intended to be occupied on a daily or full-time basis, including automatic telephone exchanges, pumphouses and substations. | obc2019_divb | Div B | 3.8.1.1.(1) | 3.8.1.1. Application | The requirements of this Section apply to all buildings except, (a) houses, triplexes and boarding or rooming houses with fewer than 8 boarders or roomers, (b) buildings of Group F, Division 1 major occupancy, (c) buildings that are not intended to be occupied on a daily or full time basis, including automatic telephone exchanges, pumphouses and substations, and (d) camps for housing of workers. (See Appendix A.) |  | Common Sentence | Yes | Accessibility: Other
2015 | ON | NBC | Div B | 3.8.2.10.(2) | Signs and Indicators | Signs complying with Subsection 3.8.3. shall be installed to indicate the location of (a) barrier-free entrances, (b) barrier-free washrooms, (c) barrier-free showers, (d) barrier-free elevators, (e) barrier-free parking spaces, and (f) facilities for persons with hearing disabilities. Signs required by Article 3.8.2.10. shall incorporate the International Symbol of Access or the International Symbol of Access for Hearing Loss and appropriate graphical or textualinformation that clearly indicates the type of facilities available. (See Note A-3.8.3.9.(1).) | obc2019_divb | Div B | 3.8.3.1.(2) | 3.8.3.1. Accessibility Signs (See Appendix A.) | Where a washroom, elevator, telephone or parking area is required to accommodate persons with disabilities, it shall be identified by a sign consisting of the International Symbol of Access and such other graphic, tactile or written directions as are needed to indicate clearly the type of facility available. |  | Common Sentence | Yes | Accessibility: Other
2015 | ON | NBC | Div B | 3.8.2.10.(2) | Signs and Indicators | Where a washroom is not designed to accommodate persons with physical disabilities in a storey to which a barrier-free path of travel is required, signs shall be provided to indicate the location of barrier-free facilities. | obc2019_divb | Div B | 3.8.3.1.(3) | 3.8.3.1. Accessibility Signs (See Appendix A.) | Where a washroom is not designed to accommodate persons with disabilities in a storey that is required by Article 3.8.2.1. to have a barrier-free path of travel, signs shall be provided to indicate the location of a washroom required to be barrier-free. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.8.2.11.(1) | Counters and Counters for Telephones | Every counter more than 2 m long at which the public is served shall comply with Subsection 3.8.3. (See Note A-3.8.2.11.(1).)(See also Note A-3.8.2.3.) | obc2019_divb | Div B | 3.8.3.15.(1) | 3.8.3.15. Shelves or Counters for Telephones (See Appendix | Where more than one telephone is provided for public use, a built-in shelf or counter shall be provided for at least one telephone. |  | Common Sentence | Yes | Accessibility: Other
2015 | ON | NBC | Div B | 3.8.2.2.(1) | Entrances | In addition to the barrier-free entrances required by Sentence (2), not less than 50% of the pedestrian entrances of a building referred to in Sentence 3.8.2.1.(1) shall be barrier-free and shall lead from (a) the outdoors at sidewalk level, or (b) a ramp that complies with Subsection 3.8.3. and leads from a sidewalk. | obc2019_divb | Div B | 3.8.1.2.(1) | 3.8.1.2. Entrances (See Appendix A.) | Except as provided in Sentence 3.13.8.1.(2), the number of barrier-free entrances into a building shall conform to Table 3.8.1.2. |  | Common Sentence | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B | 3.8.2.2.(1) | Entrances | In addition to the barrier-free entrances required by Sentence (2), not less than 50% of the pedestrian entrances of a building referred to in Sentence 3.8.2.1.(1) shall be barrier-free and shall lead from (a) the outdoors at sidewalk level, or (b) a ramp that complies with Subsection 3.8.3. and leads from a sidewalk. A barrier-free entrance required by Sentence (1) or (2) shall be designed in accordance with Subsection 3.8.3. | obc2019_divb | Div B | 3.8.1.2.(4) | 3.8.1.2. Entrances (See Appendix A.) | A barrier-free entrance shall, be designed in accordance with Article 3.8.3.3., and lead from, the outdoors at sidewalk level, or a ramp that conforms to Article 3.8.3.4. and leads from a sidewalk. |  | Common Sentence | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B | 3.8.2.2.(2) | Entrances | A suite of assembly occupancy, business and personal services occupancy or mercantile occupancy that is located in the first storey of a building, or in a storey to which a barrier-free path of travel is provided, and that is completely separated from the remainder of the building so that there is no access to the remainder of the building, shall have at least one barrier-free entrance. | obc2019_divb | Div B | 3.8.1.2.(3) | 3.8.1.2. Entrances (See Appendix A.) | In addition to the barrier-free entrances required by Sentence (1), a suite of assembly occupancy, business and personal services occupancy or mercantile occupancy that is located in the first storey of a building or in a storey to which a barrier-free path of travel is provided, and that is separated from the remainder of the building so that there is no access to the remainder of the building, shall have at least one barrier-free entrance. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.8.2.2.(4) | Entrances | At a barrier-free entrance that includes more than one doorway, only one of the doorways is required to be designed in accordance with Subsection 3.8.3. | obc2019_divb | Div B | 3.8.1.2.(5) | 3.8.1.2. Entrances (See Appendix A.) | At a barrier-free entrance that includes more than one doorway, only one of the doorways is required to be designed in accordance with Article 3.8.3.3. |  | Common Sentence | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B | 3.8.2.2.(5) | Entrances | If a walkway or pedestrian bridge connects two barrier-freestoreys in different buildings, the path of travel from one storey to the other storey by means of the walkway or bridge shall be barrier-free. (See Note A-3.8.2.3.) | obc2019_divb | Div B | 3.8.1.2.(6) | 3.8.1.2. Entrances (See Appendix A.) | If a walkway or pedestrian bridge connects two barrier-free storeys in different buildings, the path of travel from one storey to the other storey by means of the walkway or bridge shall be barrier-free. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.8.2.3.(1) | Areas Requiring a Barrier-Free Path of Travel | Except as permitted by Sentence (2), a barrier-free path of travel from the entrances required by Sentences 3.8.2.2.(1) and (2) to be barrier-free shall be provided throughout the entrance storey and within all other normally occupied floor areas served by a passenger elevator, escalator, inclined moving walk,or other platform-equipped passenger-elevating device. (See Article 3.3.1.7.for additional requirements regarding floor areas above or below the first storey to which a barrier-free path of travel is required.) | obc2019_divb | Div B | 3.8.1.4.(3) | 3.8.1.4. Escalators and Moving Walks | In a building in which a moving walk provides access between areas on the same floor level, a barrier-free path of travel shall be provided between the areas served by the moving walk. |  | Common Sentence | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B | 3.8.2.3.(1) | Areas Requiring a Barrier-Free Path of Travel | Except as permitted by Sentence 3.8.2.3.(2), a barrier-free path of travel from the entrances required by Sentences 3.8.2.2.(1) and 3.8.2.2.(2) to be barrier-free shall be provided throughout the entrance storey and within all other normally occupied floor areas served by a passenger elevator, escalator, inclined moving walk, or other platform-equipped passenger-elevating device. (See Article 3.3.1.7. for additional requirements regarding floor areas above or below the first storey to which a barrier-free path of travel is required.) | obc2019_divb | Div B | 3.8.2.1.(1) | 3.8.2.1. Areas Requiring Barrier-Free Path of Travel | Except as permitted by Sentence (3), a barrier-free path of travel from the entrances required by Sentences 3.8.1.2.(1) and (3) to be barrier-free shall be provided, (a) throughout the entrance storey, (b) except as permitted by Sentence (2), to and throughout all normally occupied floor areas and rooftop amenity spaces, and (c) throughout all normally occupied floor areas and rooftop amenity spaces that, (i) are exempt from the application of Clause (b), and (ii) are served by a passenger elevator, escalator, inclined moving walk, or other platform equipped passenger elevating device. |  | Common Sentence | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B | 3.8.2.3.(2) | Areas Requiring a Barrier-Free Path of Travel | A barrier-free path of travel for persons in wheelchairs is not required (a) to service rooms, (b) to elevator machine rooms, (c) to janitors rooms, (d) to service spaces, (e) to crawl spaces, (f) to attic or roof spaces, (g) to floor levels not served by a passenger elevator, a platform-equipped passenger-elevating device, an escalator, or an inclined moving walk, (h) to high-hazard industrial occupancies, (i) within portions of a floor area with fixed seats in an assembly occupancy where those portions are not part of the barrier-free path of travel to spaces designated for wheelchair use, (j) within floor levels of a suite of residential occupancy that are not at the same level as the entry level to the suite, (k) within a suite of residential occupancy that has not been designated by an authority having jurisdiction to be accessible for use by persons with physical disabilities, or (l) within those parts of a floor area that are not at the same level as the entry level, provided amenities and uses provided on any raised or sunken level are accessible on the entry level by means of a barrier-free path of travel. | obc2019_divb | Div B | 3.8.2.1.(3) | 3.8.2.1. Areas Requiring Barrier-Free Path of Travel | A barrier-free path of travel described in Sentence (1) is not required to extend, (a) into service rooms, (b) into elevator machine rooms, (c) into janitors rooms, (d) into service spaces, (e) into crawl spaces, (f) into attic or roof spaces, (g) into high hazard industrial occupancies, (h) to portions of a floor area with fixed seats in an assembly occupancy where these portions are not part of the barrier-free path of travel to, (i) spaces designated for wheelchair use, (ii) seats designated for adaptable seating, or (iii) spaces for the storage of wheelchairs and mobility assistive devices, (i) to suites of residential occupancy that are in storeys other than the entrance storey and that have all entrance doors at floor levels that are not required to have a barrier-free path of travel, (j) except as required by Sentence (5), on the inside of a suite of residential occupancy, or (k) to portions of a floor area that are not at the same level as the entry level, provided amenities and uses provided on any raised or sunken level are accessible on the entry level by means of a barrier-free path of travel. |  | Common Sentence | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B | 3.8.2.3.(3) | Areas Requiring a Barrier-Free Path of Travel | In an assembly occupancy, the number of spaces designated for wheelchair use within rooms or areas with fixed seats shall conform to Table 3.8.2.3. (See also Article 3.8.3.21. for additional requirements.) | obc2019_divb | Div B | 3.8.2.1.(4) | 3.8.2.1. Areas Requiring Barrier-Free Path of Travel | In an assembly occupancy with fixed seats, the minimum number of spaces designated for wheelchair use and the minimum number of fixed seats designated for adaptable seating shall conform to Table 3.8.2.1. (See Appendix A.) |  | Common Sentence | Yes | Accessibility: Other
2015 | ON | NBC | Div B | 3.8.2.4.(1) | Access to Storeys Served by Escalators and Moving Walks | In a building in which an escalator or inclined moving walk provides access to any floor level above or below the entrance floor level, an interior barrier-free path of travel shall also be provided to that floor level. (See Note A-3.8.2.4.(1).) | obc2019_divb | Div B | 3.8.1.4.(1) | 3.8.1.4. Escalators and Moving Walks | In a building in which an escalator or inclined moving walk provides access to any floor level above or below the entrance floor level, an interior barrier-free path of travel shall be provided to that floor level. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.8.2.4.(2) | Access to Storeys Served by Escalators and Moving Walks | The route from the escalator or inclined moving walk to the barrier-free path of travel that leads from floor to floor as required by Sentence 3.8.2.4.(1) shall be clearly indicated by appropriate signs. | obc2019_divb | Div B | 3.8.1.4.(2) | 3.8.1.4. Escalators and Moving Walks | The route from the escalator or inclined moving walk to the barrier-free path of travel required by Sentence (1) shall be clearly indicated by appropriate signs. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.8.2.5.(1) | Access to Parking Areas and Exterior Passenger-Loading Zones | A barrier-free path of travel shall be provided between an exterior parking area and a barrier-free entrance referred to in Article 3.8.2.2. (See Note A-3.8.2.5.(1).) Where a passenger elevator serves one or more indoor parking levels, a barrier-free path of travel shall be provided between atleast one parking level and all other parts of the building required to beprovided with barrier-free access in accordance with Subsection 3.8.3. | obc2019_divb | Div B | 3.8.2.2.(1) | 3.8.2.2. Access to Parking Areas | A barrier-free path of travel shall be provided from the entrance described in Article 3.8.1.2. to, (a) an exterior parking area, where exterior parking is provided, and (b) at least one parking level, where a passenger elevator serves an indoor parking level. |  | Common Sentence | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B | 3.8.2.6.(1) | Controls | Except as provided in Sentence 3.5.2.1.(3), controls for the operation of building services or safety devices, including electrical switches, thermostats, faucets, door hardware and intercom switches, that are intended to be operated by the occupant and are located in or adjacent to a barrier-free path of travel shall comply with Subsection 3.8.3. (See Note A-3.8.2.6.(1).) Controls described in this Section shall (a) where located in or adjacent to a barrier-free path of travel, and unless otherwise stated, (i) be mounted 400 mm to 1 200 mm above the floor, (ii) be adjacent to and centered on either the length or the width of a clear floor space of 1 350 mm by 800 mm, and (b) be operable (i) with one hand in a closed fist position, without requiring tight grasping, pinching with fingers, or twisting of the wrist, and (ii) unless otherwise stated,with a force not more than 22N. | obc2019_divb | Div B | 3.8.1.5.(1) | 3.8.1.5. Controls | Except as required by Sentences 3.5.2.2.(1) and 3.8.3.5.(1) for elevators and Sentence 3.8.3.3.(17) for power door operator controls, controls for the operation of building services or safety devices, including electrical switches, thermostats and intercom switches, intended to be operated by the occupant and located in a barrier-free path of travel shall, (a) be mounted, (i) 1 200 mm above the finished floor, in the case of a thermostat or a manual pull station, and (ii) not less than 900 mm and not more than 1 100 mm above the finished floor, in the case of all other controls, and (b) be located so as to be adjacent to and centred on either the length or the width of a clear floor space of 810 mm by 1 370 mm, and (c) be operable, (i) using one hand, without requiring tight grasping, pinching with fingers or twisting of the wrist, and with a force of not more than 22.2 N, in the case of a manual pull station, and (ii) using a closed fist and with a force of not more than 22.2 N, in the case of all other controls. |  | Common Sentence | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B | 3.8.2.7.(1) | Power Door Operators | Except as provided in Sentences (2) and (3), every door that provides a barrier-free path of travel through an entrance referred to in Article 3.8.2.2., including the interior doors of a vestibule where provided, shall be equipped with a power door operator that complies with Subsection 3.8.3.and allows persons to activate the opening of the door in the intended direction of travel, where the entrance serves (a) a hotel, (b) a building of Group B, Division 2 major occupancy,or (c) a building of Group A, Group B, Division 3, Group D or E major occupancy more than 500 m2 in building area. | obc2019_divb | Div B | 3.8.3.3.(4) | 3.8.3.3. Doorways and Doors | Except as permitted by Sentence (12), every door that provides a barrier-free path of travel through a barrier-free entrance required by Article 3.8.1.2. shall be equipped with a power door operator if the entrance serves a building containing a Group A, Group B, Division 2 or 3, Group C, Group D or Group E occupancy. (See Appendix A.) |  | Common Sentence | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B | 3.8.2.8.(1) | Plumbing Facilities | Except as permitted by Sentence (2), a washroom in a storey to which a barrier-free path of travel is required in accordance with Article 3.8.2.3., shall be barrier-free in accordance with Subsection 3.8.3.(See Note A-3.8.2.8.(1) to (4).) | obc2019_divb | Div B | 3.8.2.3.(1) | 3.8.2.3. Washrooms Required to be Barrier-Free (See Appendix | A barrier-free path of travel shall be provided to barrier-free washrooms designed to accommodate persons with disabilities in conformance with the requirements in Articles 3.8.3.8. to 3.8.3.12. |  | Common Sentence | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B | 3.8.2.8.(1) | Plumbing Facilities | Except as permitted by Sentence (2), a washroom in a storey to which a barrier-free path of travel is required in accordance with Article 3.8.2.3., shall be barrier-free in accordance with Subsection 3.8.3.(See Note A-3.8.2.8.(1) to (4).) | obc2019_divb | Div B | 3.8.2.3.(4) | 3.8.2.3. Washrooms Required to be Barrier-Free (See Appendix | Except as permitted in Sentence (5), where washrooms in excess of those required by Subsection 3.7.4. are provided in a storey that is required by Article 3.8.2.1. to have a barrier-free path of travel, the additional washrooms shall be designed to accommodate persons with disabilities in conformance with the requirements of, Articles 3.8.3.8. to 3.8.3.11., or Article 3.8.3.12. |  | Common Sentence | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B | 3.8.2.8.(10) | Plumbing Facilities | Except within a suite of care occupancy or a suite of residential occupancy, where showers are provided in a building, atleast one shower stall in each group of showers shall comply with Subsection 3.8.3. | obc2019_divb | Div B | 3.8.3.13.(1) | 3.8.3.13. Showers and Bathtubs | Except within a suite of residential occupancy, if showers are provided in a building, the number of barrier-free showers shall conform to Table 3.8.3.13. (See Appendix A.) |  | Common Sentence | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B | 3.8.2.8.(2) | Plumbing Facilities | A washroom need not conform to the requirements of Sentence 3.8.2.8.(1) provided it is located within a suite of residential occupancy or a suite of care occupancy, other barrier-free washrooms are provided on the same floor area within 45 m, or it is located in an individual suite that is used for a business and personal services occupancy, a mercantile occupancy or an industrial occupancy, less than 500 m2 in area, and completely separated from, and without access to, the remainder of the building. | obc2019_divb | Div B | 3.8.2.3.(5) | 3.8.2.3. Washrooms Required to be Barrier-Free (See Appendix | Washrooms need not conform to Sentence (4) provided, they are located within suites of residential occupancy, other barrier-free washrooms are provided on the same floor level within 45 m, or (See Appendix A.) they are located in an individual suite that is, used for a business and personal services occupancy, a mercantile occupancy or an industrial occupancy, less than 300 m2 in area, and completely separated from, and without access to, the remainder of the building. |  | Common Sentence | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B | 3.8.2.8.(9) | Plumbing Facilities | Where drinking fountains are provided, at least one shall comply with Subsection 3.8.3. | obc2019_divb | Div B | 3.8.3.16.(1) | 3.8.3.16. Drinking Fountains (See Appendix A.) | Where more than one drinking fountain is provided, at least one shall be a barrier-free fountain that conforms to Sentences (2) and (3). |  | Common Sentence | Yes | Accessibility: Other
2015 | ON | NBC | Div B | 3.8.2.9.(1) | Assistive Listening Devices | In a building of assembly occupancy, all classrooms, auditoria, meeting rooms and theatres with an area of more than 100 m2 shall be equipped with an assistive listening system complying with Subsection 3.8.3. | obc2019_divb | Div B | 3.8.3.7.(1) | 3.8.3.7. Assistive Listening Devices | In buildings of assembly occupancy, all classrooms, auditoria, meeting rooms and theatres with an area of more than 100 m2 and an occupant load of more than 75 shall be equipped with assistive listening systems encompassing the entire seating area. (See Appendix A.) |  | Common Sentence | Yes | Accessibility: Other
2015 | ON | NBC | Div B | 3.8.3.10.(1) | Drinking Fountains | Drinking fountains required by Sentence 3.8.2.8.(9) shall (a) be located along a barrier-free path of travel, (b) have a minimum clear floor space of 800 mm by 1 350 mm in front of it, (c) where it has frontal access, provide a knee clearance in accordance with Sentence 3.8.3.15.(1), (d) have a spout that (i) is located near the front of the unit, at a height between 750 mm and 915 mm above the floor, and (ii) directs water flow in a trajectory that is nearly parallel to the front of the unit, at a height not less than 100 mm, and (e) be equipped with controls that (i) activate automatically, or (ii) are located either on the front or on both sides of it and comply with Sentence 3.8.3.8.(1). | obc2019_divb | Div B | 3.8.3.16.(3) | 3.8.3.16. Drinking Fountains (See Appendix A.) | A barrier-free drinking fountain required by Sentence (1) shall have a clear floor space in front of, or adjacent to, the fountain that is a minimum of 810 mm deep and 1 370 mm wide |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.8.3.10.(1) | Drinking Fountains | Drinking fountains required by Sentence 3.8.2.8.(9) shall (a) be located along a barrier-free path of travel, (b) have a minimum clear floor space of 800 mm by 1 350 mm in front of it, (c) where it has frontal access, provide a knee clearance in accordance with Sentence 3.8.3.15.(1), (d) have a spout that (i) is located near the front of the unit, at a height between 750 mm and 915 mm above the floor, and (ii) directs water flow in a trajectory that is nearly parallel to the front of the unit, at a height not less than 100 mm, and (e) be equipped with controls that (i) activate automatically, or (ii) are located either on the front or on both sides of it and comply with Sentence 3.8.3.8.(1). | obc2019_divb | Div B | 3.8.3.16.(2) | 3.8.3.16. Drinking Fountains (See Appendix A.) | A barrier-free drinking fountain shall, (a) have a spout located near the front of the unit not more than 915 mm above the finished floor, (b) be equipped with controls that are easily operated from a wheelchair using one hand with a force of not more than 22 N or shall operate automatically, (c) project the water at least 100 mm high, (d) provide the water stream at a vertical angle of up to, (i) 30°, where the spout is located less than 75 mm from the front of the fountain, or (ii) 15°, where the spout is located not less than 75 mm and not more than 125 mm from the front of the fountain, (e) be detectable by a cane at a level at or below 680 mm from the finished floor, and (f) where the drinking fountain is cantilevered, meet the following requirements: (i) be mounted not more than 915 mm above the finished floor, (ii) provide a clearance height under the fountain of not less than 735 mm above the finished floor, (iii) have a clear depth under the fountain of not less than 450 mm, (iv) have a clear width under the fountain of not less than 760 mm, (v) have a toe clearance height under the fountain of at least 350 mm above the finished floor from a point 300 mm back from the front edge to the wall, and (vi) have a depth at the base of the fountain of at least 700 mm. |  | Common Sentence | Yes | Accessibility: Other
2015 | ON | NBC | Div B | 3.8.3.11.(1) | Water-Closet Stalls | Water-closet stalls and enclosures required by Sentence 3.8.2.8.(5) shall (a) be not less than 1?500 mm wide by 1?500 mm deep, (b) have a clear floor space of 1 500 mm by 1 500 mm in front of the accessible stall, (c) be equipped with a door that (i) can be latched from the inside with a mechanism conforming to Sentence 3.8.3.8.(1), (ii) is aligned with either the transfer space adjacent to the water closet or with a clear floor space not less than 1 500 mm by 1 500 mm within the stall, (iii) provides a clear opening not less than 850 mm wide when it is open, (iv) is self-closing so that, when at rest, the door is ajar by not more than 50 mm beyond the jamb, (v)swings outward, unless there is sufficient floor space within the stall for the door to swing inward in addition to a clear floor space of at least 800 mm by 1 350 mm (see Note A-3.8.3.11.(1)(c)(v)), (vi) where the door swings outward, is provided with a horizontal, D-shaped, visually contrasting door pull not less than 140 mm long located on the inside such that its midpoint is 200 mm to 300 mm from the hinged side of the door and 800 mm to 1?000 mm above the floor (see Note A-3.8.3.11.(1)(c)(vi)), and (vii) is provided with a horizontal, D-shaped, visually contrasting door pull not less than 140 mm long located on the outside such that its midpoint is 120 mm to 220 mm from the latch side and 800 mm to 1 000 mm above the floor, (d) have a water closet located so that the distance between the centre line of the fixture and the wall on one side is 460 mm to 480 mm, (e) be equipped with an L-shaped grab bar that (i) is mounted on the side wall closest to the water closet, (ii) has horizontal and vertical components not less than 760 mm long mounted with the horizontal component 750 mm to 850 mm above the floor and the vertical component 150 mm in front of the water closet (see Note A-3.8.3.11.(1)(e)(ii)), and (iii) complies with Article 3.7.2.8., (f) be equipped with either one grab bar at least 600 mm long and centred over the water closet, or two grab bars at least 300 mm long and located either side of the flush valve, (i) that conform to Article 3.7.2.8., (ii) are mounted on the rear wall, and (iii) are mounted at the same height as the grab bar on the side wall or 100 mm above the top of the attached water tank, if applicable, (g) be equipped with a coat hook mounted not more than 1?200 mm above the floor on a side wall and projecting not more than 50 mm from the wall, and (h) be equipped with a toilet paper dispenser mounted on the side wall closest to the water closet such that (i) the bottom of the dispenser is 600 mm to 800 mm above the floor, and (ii) the closest edge of the dispenser is 300 mm from the front of the water closet. | obc2019_divb | Div B | 3.8.3.8.(1) | 3.8.3.8. Water Closet Stalls and Enclosures | Every barrier-free water closet stall or enclosure in a washroom described in Sentence 3.8.2.3.(3) or (4) shall, (a) have a clear turning space within the stall or enclosure of at least 1 500 mm in diameter, (b) have a clear floor space in front of the stall or enclosure of at least 1 500 mm in diameter, (c) be equipped with a door that, (i) is capable of being latched from the inside with a mechanism conforming to Subclause 3.8.1.5.(1)(b)(ii), (ii) in an open position, has a clear opening of at least 860 mm wide, (iii) swings outward, unless 820 mm by 1 440 mm clear floor area is provided within the stall to permit the door to be closed without interfering with the wheelchair, (iv) is self-closing so that, when at rest, the door remains open not more than 50 mm beyond the jamb, (v) is provided with a horizontal, D-shaped, visually contrasting door pull on both sides of the door, mounted on the vertical centre line of the door, located at a height not less than 800 mm and not more than 1 000 mm above the finished floor, (vi) is aligned with a clear transfer space required by Subclause (2)(a)(ii) or Clause (2)(b), and (vii) is capable of having the latch required by Subclause (i) released from the outside in case of an emergency, (d) be equipped with a water closet conforming to Article 3.8.3.9. that is located in accordance with Clause (2)(a) or (b), (e) be equipped with a coat hook mounted not more than 1 200 mm above the finished floor on a side wall and projecting not more than 50 mm from the wall, (f) have a clearance of at least 1 700 mm between the outside of the stall face and the face of an in-swinging washroom door and 1 400 mm between the outside of the stall face and any wall-mounted fixture or other obstruction, and (g) be equipped with a toilet paper dispenser mounted on the side wall closest to the water closet so that, (i) the dispenser is located below the grab bar, (ii) the closest edge of the dispenser is 300 mm from the front of the water closet seat, and (iii) the bottom of the dispenser is 600 mm to 800 mm above the finished floor. |  | Common Sentence | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B | 3.8.3.12.(1) | Universal Washrooms | A universal washroom shall (a) be served by a barrier-free path of travel, (b) have a door complying with Article 3.8.3.6. that (i) has a latch-operating mechanism located 900 mm to 1?000 mm above the floor that complies with Sentence 3.8.3.8.(1) and is capable of being locked from the inside, and released from the outside in case of emergency, and (ii) if it is an outward swinging door that is not self-closing, has a door pull not less than 140 mm long located on the inside so that its midpoint is not less than 200 mm and not more than 300 mm from the hinged side of the door and not less than 900 mm and not more than 1?000 mm above the floor (see Note A-3.8.3.11.(1)(c)(vi)), (c) have one lavatory conforming to Article 3.8.3.15., (d) have one water closet conforming to Article 3.8.3.13. and Sentence 3.8.3.11.(1), with a clear floor space at least 900 mm wide that is parallel and adjacent to the open side of the water closet, (e) have grab bars conforming to Clauses 3.8.3.11.(1)(e) and 3.8.3.11.(1)(f), (f) have a coat hook conforming to Clause 3.8.3.11.(1)(g), (g) have a toilet paper dispenser conforming to Clause 3.8.3.11.(1)(h), (h) unless a counter is provided, have a shelf located not more than 1?200 mm above the floor, and (i) be designed to permit a wheelchair to turn in an open space not less than 1?500 mm in diameter. | obc2019_divb | Div B | 3.8.3.12.(1) | 3.8.3.12. Universal Washrooms | A universal washroom shall, (a) be served by a barrier-free path of travel, (b) have a door that, (i) complies with Article 3.8.3.3., (ii) has a graspable latch-operating mechanism that is, (A) operable using a closed fist and with a force of not more than 22.2 N, and (B) located between 900 mm and 1 000 mm above the finished floor, and (iii) is capable of being locked from the inside and released from the outside in case of emergency, (c) have one lavatory conforming to Sentences 3.8.3.11.(1), (3) and (4), (d) have one water closet conforming to Article 3.8.3.9. that is located in accordance with Clause 3.8.3.8.(2)(a) or (b), (e) have grab bars conforming to, |  | Common Sentence | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B | 3.8.3.13.(1) | Water Closets | A water closet for a person with physical disabilities shall (a) be equipped with a seat located 430 mm to 460 mm above the floor, (b) flush automatically or be equipped with a flushing control that (i) is located 500 mm to 900 mm above the floor, (ii) is located no more than 350 mm from the transfer side, and (iii) complies with Sentence 3.8.3.8.(1), (c) be equipped with a seat lid or other back support, and (d) where it has a tank, have a securely attached tank top. | obc2019_divb | Div B | 3.8.3.9.(1) | 3.8.3.9. Water Closets (See Appendix A.) | A water closet described in Clause 3.8.3.8.(1)(d) or (10)(c) or 3.8.3.12.(1)(d) shall, (a) be equipped with a seat located at not less than 430 mm and not more than 485 mm above the finished floor, (b) flush automatically or be equipped with a flushing control that, (i) is located between 500 mm and 900 mm above the finished floor, (ii) is operable from the transfer side, and (iii) is operable using a closed fist and with a force of not more than 22.2 N, and (c) be equipped with a back support where there is no seat lid or tank. |  | Common Sentence | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B | 3.8.3.13.(1) | Water Closets | Water-closet stalls and enclosures required by Sentence 3.8.2.8.(5) shall (a) be not less than 1?500 mm wide by 1?500 mm deep, (b) have a clear floor space of 1 500 mm by 1 500 mm in front of the accessible stall, (c) be equipped with a door that (i) can be latched from the inside with a mechanism conforming to Sentence 3.8.3.8.(1), (ii) is aligned with either the transfer space adjacent to the water closet or with a clear floor space not less than 1 500 mm by 1 500 mm within the stall, (iii) provides a clear opening not less than 850 mm wide when it is open, (iv) is self-closing so that, when at rest, the door is ajar by not more than 50 mm beyond the jamb, (v) swings outward, unless there is sufficient floor space within the stall for the door to swing inward in addition to a clear floor space of at least 800 mm by 1 350 mm (see Note A-3.8.3.11.(1)(c)(v)), (vi) where the door swings outward, is provided with a horizontal, D-shaped, visually contrasting door pull not less than 140 mm long located on the inside such that its midpoint is 200 mm to 300 mm from the hinged side of the door and 800 mm to 1?000 mm above the floor (see Note A-3.8.3.11.(1)(c)(vi)), and (vii) is provided with a horizontal, D-shaped, visually contrasting door pull not less than 140 mm long located on the outside such that its midpoint is 120 mm to 220 mm from the latch side and 800 mm to 1 000 mm above the floor, (d) have a water closet located so that the distance between the centre line of the fixture and the wall on one side is 460 mm to 480 mm, (e) be equipped with an L-shaped grab bar that (i) is mounted on the side wall closest to the water closet, (ii) has horizontal and vertical components not less than 760 mm long mounted with the horizontal component 750 mm to 850 mm above the floor and the vertical component 150 mm in front of the water closet (see Note A-3.8.3.11.(1)(e)(ii)), and (iii) complies with Article 3.7.2.8., (f) be equipped with either one grab bar at least 600 mm long and centred over the water closet, or two grab bars at least 300 mm long and located either side of the flush valve, that (i) conform to Article 3.7.2.8., (ii) are mounted on the rear wall, and (iii) are mounted at the same height as the grab bar on the side wall or 100 mm above the top of the attached water tank, if applicable, (g) be equipped with a coat hook mounted not more than 1?200 mm above the floor on a side wall and projecting not more than 50 mm from the wall, and (h) be equipped with a toilet paper dispenser mounted on the side wall closest to the water closet such that (i) the bottom of the dispenser is 600 mm to 800 mm above the floor, and (ii) the closest edge of the dispenser is 300 mm from the front of the water closet. | obc2019_divb | Div B | 3.8.3.8.(2) | 3.8.3.8. Water Closet Stalls and Enclosures | A water closet described in Clause (1)(d) shall be, (a) located so that, (i) the centre line of the water closet is not less than 460 mm and not more than 480 mm from one side wall, and (ii) a clear transfer space at least 900 mm wide and 1 500 mm deep is provided on the other side of the water closet, or (b) located so that a clear transfer space at least 900 mm wide and 1 500 mm deep is provided on each side of the water closet. (See Appendix A.) |  | Common Sentence | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B | 3.8.3.14.(1) | Urinals | Urinals described in Sentence 3.8.2.8.(6) shall (a) be wall-mounted, with the rim located not more than 430 mm above the floor, (b) be adjacent to an accessible route, (c) have a clear width of approach of 800 mm centred on the urinal and unobstructed by privacy screens, (d) have no step in front of it, (e) have a flush control that (i) is automatic, or (ii) complies with Sentence 3.8.3.8.(1) and is located 900 mm to 1 100 mm above the floor, and (f) have a vertically mounted grab bar installed on each side that (i) complies with Article 3.7.2.8., (ii) is not less than 600 mm long, with its centre line 1 000 mm above the floor, and (iii) is located not more than 380 mm from the centre line of the urinal. | obc2019_divb | Div B | 3.8.3.10.(2) | 3.8.3.10. Urinals (See Appendix A.) | A urinal described in Sentence (1) shall, (a) flush automatically or be equipped with a flushing control that is, (i) located between 900 mm and 1 100 mm above the finished floor, and (ii) operable using a closed fist and with a force of not more than 22.2 N, and (b) have installed on each side, a vertically mounted grab bar that, (i) complies with Article 3.8.3.8.(7), (ii) is not less than 600 mm long, with its centre line 1 000 mm above the finished floor, and (iii) is located not more than 380 mm from the centre line of the urinal. |  | Common Sentence | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B | 3.8.3.14.(1) | Urinals | Urinals described in Sentence 3.8.2.8.(6) shall (a) be wall-mounted, with the rim located not more than 430 mm above the floor, (b) be adjacent to an accessible route, (c) have a clear width of approach of 800 mm centred on the urinal and unobstructed by privacy screens, (d) have no step in front of it, (e) have a flush control that (i) is automatic, or (ii) complies with Sentence 3.8.3.8.(1) and is located 900 mm to 1 100 mm above the floor, and (f) have a vertically mounted grab bar installed on each side that (i) complies with Article 3.7.2.8., (ii) is not less than 600 mm long, with its centre line 1 000 mm above the floor, and (iii) is located not more than 380 mm from the centre line of the urinal. | obc2019_divb | Div B | 3.8.3.10.(1) | 3.8.3.10. Urinals (See Appendix A.) | Where more than one urinal is provided in a washroom described in Sentence 3.8.2.3.(3) or (4), at least one urinal shall, be mounted with the rim located not more than 430 mm above the finished floor, have a clear floor space at least 800 mm wide that is perpendicular to, and centred on, the urinal and is unobstructed by privacy screens, and have no step in front of it. |  | Common Sentence | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B | 3.8.3.15.(1) | Lavatories and Mirrors | Lavatories required by Sentence 3.8.2.8.(7) shall (a) be equipped with faucets complying with Sentence 3.7.2.3.(4), (b) be located so that the distance between the centre line of the lavatory and any side wall is not less than 460 mm, (c) have a rim height not more than 865 mm above the floor, (d) have a clearance beneath the lavatory not less than (i) 760 mm wide, (ii) 735 mm high at the front edge, (iii) 685 mm high at a point 200 mm back from the front edge, and (iv) 230 mm high over the distance from a point 280 mm to a point 430 mm back from the front edge, (e) have insulated water supply and drain pipes where these pipes are exposed (see Note A-3.8.3.15.(1)(e)), (f) have a soap dispenser that is automatic, or complies with Sentence 3.8.3.8.(1) and is located not more than 1 100 mm above the floor, within 500 mm from the front of the lavatory (see Note A-3.8.3.15.(1)(f)), and (g) have a towel dispenser or other hand-drying equipment located close to the lavatory, not more than 1?200 mm above the floor in an area that is accessible to persons in wheelchairs. | obc2019_divb | Div B | 3.8.3.11.(1) | 3.8.3.11. Lavatories, Mirrors and Washroom Accessories (See | A washroom described in Sentence 3.8.2.3.(2), (3) or (4) shall be provided with a lavatory that shall, (a) be located so that the distance between the centre line of the lavatory and the side wall is not less than 460 mm, (b) have a rim height not more than 865 mm above the finished floor, (c) have a clearance beneath the lavatory not less than, (i) 920 mm wide, (ii) 735 mm high at the front edge, (iii) 685 mm high at a point 200 mm back from the front edge, and (iv) 350 mm high over the distance from a point 280 mm to a point 430 mm back from the front edge,(d) have insulated pipes where they would otherwise present a burn hazard or have water supply temperature limited to a maximum of 43°C, (e) be equipped with faucets that, (i) operate automatically or comply with 3.7.4.2.(11)(b)(i) and (ii), and (ii) are located so that the distance from the centre line of the faucet to the edge of the basin or, where the basin is mounted in a vanity, to the front edge of the vanity, is not more than 485 mm, (f) have a minimum 1 370 mm deep floor space to allow for a forward approach, of which a maximum of 500 mm can be located under the lavatory, (g) have a soap dispenser that, (i) operates automatically or is operable using a closed fist and with a force of not more than 22.2 N, and (ii) is located not more than 1 100 mm above the finished floor, within 500 mm from the front of the lavatory, and, (h) have a towel dispenser or other hand drying equipment that is, (i) located to be accessible to persons in wheelchairs, (ii) located so that the dispensing height is not more than 1 200 mm above the finished floor, (iii) operable with one hand, and (iv) located not more than 610 mm, measured horizontally, from the edge of the lavatory. |  | Common Sentence | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B | 3.8.3.15.(2) | Lavatories and Mirrors | Mirrors required by Sentence 3.8.2.8.(8) shall be mounted with their bottom edge not more than 1?000 mm above the floor, or fixed in an inclined position so as to be usable by a person in a wheelchair. | obc2019_divb | Div B | 3.8.3.11.(2) | 3.8.3.11. Lavatories, Mirrors and Washroom Accessories (See | If mirrors are installed in a washroom described in Sentence 3.8.2.3.(2), (3) or (4), at least one mirror shall be, installed above a lavatory required by Sentence (1), and mounted with its bottom edge not more than 1 000 mm above the finished floor or inclined to the vertical to be usable by a person in a wheelchair. |  | Common Sentence | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B | 3.8.3.16.(1) | Showers | Showers required by Sentence 3.8.2.8.(10) shall (a) be not less than 1 500 mm wide and 900 mm deep, (b) have a clear floor space at the entrance to the shower that is not less than 900 mm deep and the same width as the shower, except that fixtures are permitted to project into that space provided they do not restrict access to the shower (see Note A-3.8.3.16.(1)(b)), (c) have no doors or curtains that obstruct the controls or the clear floor space at the entrance to the shower, (d) have a slip-resistant floor surface, (e) have a threshold not more than 13 mm higher than the finished floor, and where it is higher than 6 mm, beveled to a slope no steeper than 1 in 2 (50%), (f) have two grab bars that (i) conform to Sentence 3.7.2.8.(1), (ii) one of which is not less than 1 000 mm long and located vertically on the side wall 50 mm to 80 mm from the adjacent clear floor space, with its lower end 600 mm to 650 mm above the floor, and, (iii) one of which is L-shaped and located on the wall opposite the entrance to the shower, with a horizontal member not less than 1 000 mm long mounted 750 mm to 870 mm above the floor and a vertical member not less than 750 mm long mounted 400 mm to 500 mm from the side wall on which the other vertical grab bar is mounted, (see Note A-3.8.3.16.(1)(f)), (g) have a hinged seat that is not spring-loaded or a fixed seat with a smooth, slip-resistant surface and no rough edges, the seat being (i) not less than 450 mm wide and 400 mm deep, (ii) mounted on the same side wall as the vertical grabbar, at 460 mm to 480 mm above the floor, and (iii) designed to carry a minimum load of 1.3kN, (h) have a pressure-equalizing or thermostatic-mixing valve and other controls that (i) comply with Clause 3.8.3.8.(1)(b), (ii) are mounted on the wall opposite the entrance to the shower at not more than 1 200 mm above the floor and within reach of the seat, (i) have a hand-held shower head with not less than 1 800 mm of flexible hose located so that it (i) can be reached from aseated position, (ii) can be used in a fixed position at a height of 1 200 mm and 2 030 mm, and (iii) does not obstruct the use of the grabbars, and (j) have recessed soap holders that can be reached from the seated position. | obc2019_divb | Div B | 3.8.3.13.(2) | 3.8.3.13. Showers and Bathtubs | A barrier-free shower required by Sentence (1) shall, (a) be not less than 1 500 mm wide and 900 mm deep, (b) have a clear floor space at the entrance to the shower not less than 900 mm deep and the same width as the shower, except that fixtures are permitted to project into that space provided they do not restrict access to the shower, (c) have no doors that obstruct the shower controls or the clear floor space described in Clause (b), (d) have a slip-resistant floor surface, (e) have a threshold that is level with the adjacent finished floor or a bevelled threshold not more than 13 mm higher than the adjacent finished floor, (f) have a hinged seat, other than a spring-loaded hinged seat, or a fixed seat that shall, (i) be not less than 450 mm wide and 400 mm deep, (ii) be mounted on the same side wall as the vertical grab bar between 460 mm and 480 mm above the finished floor, (iii) be designed to carry a minimum load of 1.3 kN, (iv) be located so that the edge of the seat is within 500 mm of the shower controls, and (v) have a smooth and slip-resistant surface and no rough edges, (g) have two grab bars, (i) that conform to Sentence 3.8.3.8.(7) and do not obstruct the use of the shower controls, (ii) one of which is 1 000 mm long vertically located on the side wall between 50 mm and 80 mm from the adjacent clear floor area, and with the lower end between 600 mm and 650 mm above the finished floor, and (iii) one of which is L-shaped, located on the wall opposite the entrance to the shower, with a 1 000 mm long horizontal component mounted between 750 mm and 870 mm above the finished floor and a 750 mm long vertical component mounted between 400 mm and 500 mm from the side wall on which the vertical grab bar described in Subclause (ii) is mounted, (h) have a pressure-equalizing or thermostatic mixing valve that, (i) is operable using a closed fist and with a force of not more than 22.2 N, (ii) is mounted on the wall opposite the entrance to the shower no more than 1 200 mm above the finished floor, and (iii) is located within reach of the seat, (i) have a hand-held shower head with not less than 1 800 mm of flexible hose located so that it, (i) can be reached from a seated position, (ii) can be used in a fixed position at a height of 1 200 mm and 2 030 mm from the finished floor, and (iii) does not obstruct the use of the grab bars, and (j) have fully recessed soap holders that can be reached from the seated position. |  | Common Sentence | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B | 3.8.3.2.(1) | Barrier-Free Path of Travel | Except as required elsewhere in this Part or as permitted by Article 3.8.3.6. pertaining to doorways, the unobstructed width of a barrier-free path of travel shall be not less than 920 mm. | obc2019_divb | Div B | 3.8.1.3.(1) | 3.8.1.3. Barrier-Free Path of Travel | Except as required in Sentence (4) and except as permitted in Subsection 3.8.3., every barrier-free path of travel shall provide an unobstructed width of at least 1 100 mm for the passage of wheelchairs. |  | Common Sentence | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B | 3.8.3.2.(2) | Barrier-Free Path of Travel | Interior and exterior walking surfaces that are within a barrier-free path of travel shall (a) have no opening that will permit the passage of a sphere more than 13 mm in diameter, (b) have any elongated openings oriented approximately perpendicular to the direction of travel, (c) be stable, firm and slip-resistant, (d) have a cross slope no steeper than 1 in 50, (e) be beveled at a maximum slope of 1 in 2 at changes in level between 6 mm and 13 mm, and (f) be provided with sloped floors or ramps at changes in level more than 13 mm. | obc2019_divb | Div B | 3.8.1.3.(2) | 3.8.1.3. Barrier-Free Path of Travel | Interior and exterior walking surfaces that are within a barrier-free path of travel shall, (a) have no opening that will permit the passage of a sphere more than 13 mm in diam, (b) have any elongated openings oriented approximately perpendicular to the direction of travel, (c) be stable, firm and slip-resistant, (d) be bevelled at a maximum slope of 1 in 2 at changes in level not more than 13 mm, and (e) be provided with sloped floors or ramps at changes in level more than 13 mm. |  | Common Sentence | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B | 3.8.3.2.(3) | Barrier-Free Path of Travel | A barrier-free path of travel is permitted to include ramps, passenger elevators or other platform-equipped passenger-elevating devices to overcome a difference in level. | obc2019_divb | Div B | 3.8.1.3.(3) | 3.8.1.3. Barrier-Free Path of Travel | A barrier-free path of travel is permitted to include ramps, passenger elevators or other platform equipped passenger elevating devices to overcome a difference in level. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.8.3.2.(4) | Barrier-Free Path of Travel | The width of a barrier-free path of travel that is more than 30 m long shall be increased to not less than 1500 mm for a length of 1500 mm at intervals not exceeding 30 m. | obc2019_divb | Div B | 3.8.1.3.(4) | 3.8.1.3. Barrier-Free Path of Travel | Every barrier-free path of travel less than 1 600 mm in width shall be provided with an unobstructed space not less than 1 800 mm in width and 1 800 mm in length located not more than 30 m apart. (See Appendix A.) |  | Common Sentence | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B | 3.8.3.20.(1) | Shelves or Counters for Telephones | Shelves or counters required by Sentence 3.8.2.11.(2) shall (a) be level, (b) be not less than 305 mm deep, (c) have, for each telephone provided, a clear space not less than 250 mm wide having no obstruction within 250 mm above the surface, and (d) have a section with a surface not more than 865 mm above the floor serving at least one telephone. | obc2019_divb | Div B | 3.8.3.15.(2) | 3.8.3.15. Shelves or Counters for Telephones (See Appendix | A shelf or counter described in Sentence (1) shall, (a) be level, (b) be not less than 500 mm wide and 350 mm deep, and (c) have, for each telephone provided, a clear space that, (i) is not less than 810 mm wide and 1 370 mm deep, centred on the telephone, and (ii) has no obstruction within 250 mm above the surface. |  | Common Sentence | Yes | Accessibility: Other
2015 | ON | NBC | Div B | 3.8.3.20.(1) | Shelves or Counters for Telephones | Shelves or counters required by Sentence 3.8.2.11.(2) shall (a) be level, (b) be not less than 305 mm deep, (c) have, for each telephone provided, a clear space not less than 250 mm wide having no obstruction within 250 mm above the surface, and (d) have a section with a surface not more than 865 mm above the floor serving at least one telephone. | obc2019_divb | Div B | 3.8.3.15.(3) | 3.8.3.15. Shelves or Counters for Telephones (See Appendix | The top surface of a section of the shelf or counter described in Sentence (1) shall, (a) be located not less than 775 mm and not more than 875 mm from the finished floor, and (b) have a knee space not less than 740 mm high. |  | Common Sentence | Yes | Accessibility: Other
2015 | ON | NBC | Div B | 3.8.3.20.(2) | Shelves or Counters for Telephones | Where a wall-hung telephone is provided above the shelf or counter section described in Sentence 3.8.3.20.(1), it shall be located so that the receiver and coin slot are not more than 1?200 mm above the floor. | obc2019_divb | Div B | 3.8.3.15.(4) | 3.8.3.15. Shelves or Counters for Telephones (See Appendix | Where a wall-hung telephone is provided above the shelf or counter section described in Sentence (3), it shall be located so that the receiver and coin or card slot are not more than 1 200 mm from the finished floor. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.8.3.21.(1) | Spaces in Seating Area | Spaces designated for wheelchair use referred to in Sentence 3.8.2.3.(3) shall be (a) clear and level, or level with removable seats, (b) not less than 900 mm wide and 1?525 mm long to permit a wheelchair to enter from a side approach and 1?220 mm long where the wheelchair enters from the front or rear of the space, (c) arranged so that at least 2 designated spaces are side by side, (d) located adjoining a barrier-free path of travel without infringing on egress from any row of seating or any aisle requirements, and (e) situated, as part of the designated seating plan, to provide a choice of viewing location and a clear view of the event taking place. | obc2019_divb | Div B | 3.8.3.6.(1) | 3.8.3.6. Wheelchair Spaces and Adaptable Seating | Spaces designated for wheelchair use required by Sentence 3.8.2.1.(4) shall be, (a) clear and level or level with removable seats, (b) not less than 900 mm wide and not less than, (i) 1 525 mm long where designed to permit a wheelchair to enter from a side approach, and (ii) 1 220 mm long where designed to permit a wheelchair to enter from the front or rear of the space, (c) arranged so that, (i) at least two of the designated spaces are side by side, and (ii) at least one fixed seat for a companion is located beside, (A) each group of designated spaces, if two or more designated spaces are arranged side by side in a group, and (B) each designated space that is not part of a group described in Sub-subclause (A),(d) located adjoining a barrier-free path of travel without infringing on egress from any row of seating or any aisle requirements, and (e) situated, as part of the designated seating plan, to provide a choice of viewing location and a clear view of the event taking place. |  | Common Sentence | Yes | Accessibility: Other
2015 | ON | NBC | Div B | 3.8.3.3.(1) | Exterior Walks | Exterior walks that form part of a barrier-free path of travel shall a) have a slip-resistant, continuous and even surface, (b) be not less than 1100 mm wide, and (c) have a level area conforming to Clause 3.8.3.5.(1)(c) adjacent to an entrance doorway. | obc2019_divb | Div B | 3.8.3.2.(1) | 3.8.3.2. Exterior Walks | Except as provided in Sentence (2), exterior walks that form part of a barrier-free path of travel shall, (a) be provided by means of a continuous plane not interrupted by steps or abrupt changes in level, (b) have a permanent, firm and slip-resistant surface, (c) except as required in Sentence 3.8.1.3.(4), have an uninterrupted width of not less than 1 100 mm and a gradient not exceeding 1 in 20, (d) be designed as a ramp where the gradient is greater than 1 in 20, (e) have not less than 1 100 mm wide surface of a different texture to that surrounding it, where the line of travel is level and even with adjacent walking surfaces, (f) be free from obstructions for the full width of the walk to a minimum height of 1 980 mm, except that handrails are permitted to project not more than 100 mm from either side into the clear area, (g) have a level area adjacent to the entrance doorway conforming to Clause 3.8.3.4.(1)(c), and (h) have a tactile attention indicator conforming to Article 3.8.3.18. that is located to identify an entry into a vehicular route or area where no curbs or any other element separate the vehicular route or area from a pedestrian route. (See Appendix A.) |  | Common Sentence | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B | 3.8.3.4.(1) | Exterior Passenger-Loading Zones | If an exterior passenger-loading zone is provided, it shall have (a) an access aisle not less than 1500 mm wide and 6000 mm long adjacent and parallel to the vehicle pull-up space, (b) a curb ramp, where there are curbs between the access aisle and the vehicle pull-up space, and (c) a clear height of not less than 2?750 mm at the pull-up space and along the vehicle access and egress routes. | obc2019_divb | Div B | 3.8.2.2.(3) | 3.8.2.2. Access to Parking Areas | If an exterior passenger loading zone is provided, it shall have, (a) an access aisle not less than 2 440 mm wide and 7 400 mm long adjacent and parallel to the vehicle pull-up space, (b) a curb ramp, where there are curbs between the access aisle and the vehicle pull-up space, and (c) a clearance height of not less than 3 600 mm at the vehicle pull-up space and along the vehicle access and egress routes. |  | Common Sentence | Yes | Accessibility: Other
2015 | ON | NBC | Div B | 3.8.3.5.(1) | Ramps | A ramp located in a barrier-free path of travel shall (a) have a clear width not less than 870 mm (see Note A-3.4.3.4.), (b) have a slope not more than 1 in 12 (see Note A-3.8.3.5.(1)(b)), (c) have a level area not less than 1?500 by 1?500 mm at the top and bottom and at intermediate levels of a ramp leading to a door, so that on the latch side the level area extends not less than (i) 600 mm beyond the edge of the door opening where the door opens towards the ramp, or (ii) 300 mm beyond the edge of the door opening where the door opens away from the ramp, (d) have a level area not less than 1?200 mm long and at least the same width as the ramp(i) at intervals not more than 9 m along its length, and (ii) where there is an abrupt change in the direction of the ramp, and (e) except as provided in Sentences 3.8.3.5.(2) and 3.8.3.5.(3), be equipped with handrails conforming to Article 3.4.6.5., except that they shall be not less than 865 mm and not more than 965 mm high, and (f) be equipped with guards conforming to Article 3.4.6.6. | obc2019_divb | Div B | 3.8.3.4.(1) | 3.8.3.4. Ramps | Ramps located in a barrier-free path of travel shall, (a) have a minimum width of 900 mm between handrails, (b) have a maximum gradient of 1 in 12, (c) have a level area of at least 1 670 mm by 1 670 mm at the top and bottom of a ramp and where a door is located in a ramp, so that the level area extends at least 600 mm beyond the latch side of the door opening, except that where the door opens away from the ramp, the area extending beyond the latch side of the door opening may be reduced to 300 mm, (d) have a level area at least 1 670 mm long and at least the same width as the ramp, (i) at intervals of not more than 9 m along its length, and (ii) where there is a change of 90° or more in the direction of the ramp, (e) except as provided in Sentence (2), be equipped with handrails on both sides that shall, (i) be continuously graspable along their entire length and have circular cross-section with an outside diameter not less than 30 mm and not more than 40 mm, or any non-circular shape with a graspable portion that has a perimeter not less than 100 mm and not more than 155 mm and whose largest cross-sectional dimension is not more than 57 mm, (ii) be not less than 865 mm and not more than 965 mm high, measured vertically from the surface of the ramp, except that handrails not meeting these requirements are permitted provided they are installed in addition to the required handrail, (iii) be terminated in a manner that will not obstruct pedestrian travel or create a hazard, (iv) extend horizontally not less than 300 mm beyond the top and bottom of the ramp, (v) be provided with a clearance that conforms to Sentence 3.4.6.5.(13), and (vi) be designed and constructed such that handrails and their supports will withstand the loading values obtained from the nonconcurrent application of a concentrated load not less than 0.9 kN applied at any point and in any direction for all handrails and a uniform load not less than 0.7 kN/m applied in any direction to the handrail, (f) except as provided in Sentence (2), have a wall or a guard on both sides and where a guard is provided the guard shall, (i) be not less than 1 070 mm measured vertically to the top of the guard from the ramp surface, and (ii) be designed so that no member, attachment or opening located between 140 mm and 900 mm above the ramp surface being protected by the guard will facilitate climbing, (g) be provided, (i) with a curb at least 50 mm high on any side of the ramp where no solid enclosure or solid guard is provided, and (ii) with railings or other barriers that extend to within 50 mm of the finished ramp surface or have a curb not less than 50 mm high, and (h) except as provided in Sentence (2), where the ramp is wider than 2 200 mm, have an intermediate handrail with a clear width of 900 mm between the intermediate handrail and one of the handrails described in Clause (e). |  | Common Sentence | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B | 3.8.3.5.(3) | Ramps | The requirement for handrails in Clause (1)(e)need not apply to a ramp serving as an aisle for fixed seating. | obc2019_divb | Div B | 3.8.3.4.(2) | 3.8.3.4. Ramps | Where a ramp serves as an aisleway for fixed seating, the requirements for handrails in Clauses (1)(e) and (h) and for walls or guards in Clause (1)(f) need not apply. |  | Common Sentence | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B | 3.8.3.5.(6) | Ramps | Floors or walks in a barrier-free path of travel having a slope steeper than 1 in 20 shall be designed as ramps. | obc2019_divb | Div B | 3.8.3.4.(3) | 3.8.3.4. Ramps | Floors or walks in a barrier-free path of travel having a slope steeper than 1 in 20 shall be designed as ramps. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.8.3.6.(10) | Doorways and Doors | Except for a door at the entrance to a dwelling unit, a closer for an interior door in a barrier-free path of travel shall have a closing period of not less than 3 s measured from when the door is in an open position of 70° to the doorway, to when the door reaches a point 75 mm from the closed position, measured from the leading edge of the latch side of the door. (See Note A-3.8.3.6.(10).) | obc2019_divb | Div B | 3.8.3.3.(9) | 3.8.3.3. Doorways and Doors | Except for doors at the entrances to dwelling units, closers for interior doors in a barrier-free path of travel shall have a closing period of not less than 3 seconds measured from when the door is in an open position of 70Ã‚Â° to the doorway, to when the door reaches a point 75 mm from the closed position, measured from the leading edge of the latch side of the door. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.8.3.6.(11) | Doorways and Doors | Unless equipped with a power door operator complying with Sentence 3.8.3.6.(6), a swinging door in a barrier-free path of travel shall have a clear space on the latch side extending the height of the doorway and not less than (a) 600 mm beyond the edge of the door opening if the door swings toward the approach side, and (b) 300 mm beyond the edge of the door opening if the door swings away from the approach side. | obc2019_divb | Div B | 3.8.3.3.(10) | 3.8.3.3. Doorways and Doors | Unless equipped with a power door operator, a door in a barrier-free path of travel shall have a clear space on the latch side extending the height of the doorway and not less than, (a) 600 mm beyond the edge of the door opening if the door swings toward the approach side, (b) 300 mm beyond the edge of the door opening if the door swings away from the approach side, and (c) 300 mm beyond both sides of a sliding door. |  | Common Sentence | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B | 3.8.3.6.(12) | Doorways and Doors | A vestibule located in a barrier-free path of travel shall be arranged to allow the movement of wheelchairs between doors and shall provide a distance between 2 doors in series of not less than 1200 mm plus the width of any door that swings into the space in the path of travel from one door to another. | obc2019_divb | Div B | 3.8.3.3.(11) | 3.8.3.3. Doorways and Doors | Vestibules located in a barrier-free path of travel, (a) shall be arranged to allow the movement of wheelchairs between doors, and (b) shall provide, (i) where the doors into the vestibule are in series, a distance between the doors of at least 1 500 mm plus the width of any door that swings into the space in the path of travel from one door to another, and (ii) where the doors into the vestibule are not aligned, a turning diameter of 1 500 mm within the vestibule clear of any door swing. |  | Common Sentence | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B | 3.8.3.6.(13) | Doorways and Doors | Only the active leaf in a multiple-leaf door in a barrier-free path of travel need conform to the requirements of this Article. | obc2019_divb | Div B | 3.8.3.3.(12) | 3.8.3.3. Doorways and Doors | Only the active leaf in a multiple leaf door in a barrier-free path of travel need conform to the requirements of this Article. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.8.3.6.(14) | Doorways and Doors | Except as provided in Sentence 3.8.3.5.(1), the floor surface on each side of a door in a barrier-free path of travel shall be level within a rectangular area (a) as wide as the door plus the clearance required on the latch side by Sentence 3.8.3.6.(11), and (b) whose dimension perpendicular to the closed door is not less than the width of the barrier-free path of travel but need not exceed 1500 mm. | obc2019_divb | Div B | 3.8.3.3.(13) | 3.8.3.3. Doorways and Doors | Except as provided in Clause 3.8.3.4.(1)(c), the floor surface on each side of a door in a barrier-free path of travel shall be level within a rectangular area, (a) as wide as the door plus the clearance required on the latch side by Sentence (10), and (b) whose dimension perpendicular to the closed door is not less than the width of the barrier-free path of travel but need not exceed 1 500 mm. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.8.3.6.(2) | Doorways and Doors | Every doorway that is located in a barrier-free path of travel shall have a clear width not less than 800 mm when the door is in the open position. (See Note A-3.8.3.6.(2).) | obc2019_divb | Div B | 3.8.3.3.(1) | 3.8.3.3. Doorways and Doors | Every doorway that is located in a barrier-free path of travel shall have a clear width of not less than 860 mm when the door is in the open position. (See Appendix A.) |  | Common Sentence | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B | 3.8.3.6.(3) | Doorways and Doors | Doorways in a path of travel to atleast one bathroom within a suite of residential occupancy shall have a clear width not less than 800 mm when the doors are open. (See Note A-3.8.3.6.(3).) | obc2019_divb | Div B | 3.8.3.3.(2) | 3.8.3.3. Doorways and Doors | Except as provided in Sentence 3.3.4.11.(11) and except where no bathroom within the suite is at the level of the suite entrance door to which a barrier-free path of travel is provided in accordance with Sentence 3.8.2.1.(1), the doorway to at least one bathroom and to each bedroom at the same level as such bathroom within a suite of residential occupancy shall have, when the door is in the open position, a clear width of not less than, (a) 760 mm where the door is served by a corridor or space not less than 1 060 mm wide, and (b) 810 mm where the door is served by a corridor or space less than 1 060 mm wide. |  | Common Sentence | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B | 3.8.3.6.(4) | Doorways and Doors | Door-operating devices shall (a) comply with Clause 3.8.3.8.(1)(b), and (b) be operable at a height between 900 mm and 1100 mm above the floor. (See Note A-3.8.3.6.(4).) | obc2019_divb | Div B | 3.8.3.3.(3) | 3.8.3.3. Doorways and Doors | Door opening devices that are the only means of operation shall, (a) be designed to be operable using a closed fist, and (b) be mounted not less than 900 mm and not more than 1 100 mm above the finished floor. (See Appendix A.) |  | Common Sentence | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B | 3.8.3.6.(6) | Doorways and Doors | Power door operators required by Sentence 3.8.2.7.(1) shall (a) activate automatically or through the use of controls that (i) arelocated in a barrier-free pathoftravel, (ii) are marked with the International Symbol of Access, (iii) are located clear of the door swing and no more than 1500 mm from that door swing, (iv) comply with Subclause 3.8.3.8.(1)(a)(ii), (v) are operable from a height between 150 mm and 300 mm as well as between 900 mm and 1 100 mm above the floor,and (vi) are operable by touching or approaching any part of their surface with a fist, arm or foot, and (b) unless equipped with safety sensors, (i) fully open the door in not less than 3s, and (ii) require a force not more than 65N to stop movement of the door. (See Note A-3.8.3.6.(6) and (7).) | obc2019_divb | Div B | 3.8.3.3.(17) | 3.8.3.3. Doorways and Doors | Except where a proximity scanning device is installed in conformance with Sentence (18), the control for a power door operator required by Sentence (4), (5) or (6) shall, (a) have a face dimension of not less than, (i) 150 mm in diameter where the control is circular, or (ii) 50 mm by 100 mm where the control is rectangular, (b) be operable using a closed fist, (c) be located so that, (i) its centre is located not less than 900 mm and not more than 1 100 mm from the finished floor or ground, or (ii) it extends from not more than 200 mm to not less than 900 mm above the finished floor or ground, (d) be located not less than 600 mm and not more than 1 500 mm beyond the door swing where the door opens towards the control, (e) be located to allow persons to activate the opening of the door from either direction of travel, (f) be located so that the path of travel is not obstructed, (g) be located in a clearly visible position, and (h) contain a sign incorporating the International Symbol of Access. |  | Common Sentence | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B | 3.8.3.6.(8) | Doorways and Doors | Except as provided in Sentence 3.8.3.6.(9) and except for a door with a power door operator complying with Sentence 3.8.3.6.(6), when unlatched, a door in a barrier-free path of travel shall open when the force applied to the handle, push plate or latch-releasing device is not more than (a) 38 N in the case of an exterior swinging door, (b) 22 N in the case of an interior swinging door, or (c) 22 N in the case of a sliding door. | obc2019_divb | Div B | 3.8.3.3.(7) | 3.8.3.3. Doorways and Doors | Except as permitted in Sentence (8), and except for doors with power operators, closers for doors in a barrier-free path of travel shall be designed to permit doors to open when a force of not more than 38 N is applied to the handles, push plates or latch-releasing devices in the case of exterior doors and 22 N in the case of interior doors. |  | Common Sentence | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B | 3.8.3.6.(9) | Doorways and Doors | Sentence 3.8.3.6.(8) does not apply to a door at the entrance to a dwelling unit, or where greater forces are required in order to close and latch the door against the prevailing difference in air pressure on opposite sides of the door. (See Note A-3.8.3.6.(9).) | obc2019_divb | Div B | 3.8.3.3.(8) | 3.8.3.3. Doorways and Doors | Sentence (7) does not apply to doors at the entrances to dwelling units, or where greater forces are required in order to close and latch the doors against prevailing differences in air pressures on opposite sides of the doors. (See Appendix A.) |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.8.3.7.(1) | Passenger-Elevating Devices | A passenger-elevating device referred to in Article 3.8.2.3. shall conform to CSA B355 Lifts for Persons with Physical Disabilities | obc2019_divb | Div B | 3.8.3.5.(1) | 3.8.3.5. Passenger Elevating Devices | A passenger elevating device referred to in Article 3.8.2.1. shall conform to CSA B355, "Lifts for Persons with Physical Disabilities". |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.8.3.9.(1) | Signs and Indicators | Signs complying with Subsection 3.8.3. shall be installed to indicate the location of (a) barrier-free entrances, (b) barrier-free washrooms, (c) barrier-free showers, (d) barrier-free elevators, (e) barrier-free parking spaces, and (f) facilities for persons with hearing disabilities. Signs required by Article 3.8.2.10. shall incorporate the International Symbol of Access or the International Symbol of Access for Hearing Loss and appropriate graphical or textualinformation that clearly indicates the type of facilities available. (See Note A-3.8.3.9.(1).) | obc2019_divb | Div B | 3.8.3.1.(1) | 3.8.3.1. Accessibility Signs (See Appendix A.) | Where a building is required to have a barrier-free entrance, signs incorporating the International Symbol of Access shall be installed to indicate the location of, that entrance, ramps located in a required barrier-free path of travel serving that entrance, and an exterior passenger loading zone conforming to Sentence 3.8.2.2.(3), if one is provided. |  | Common Sentence | Yes | Accessibility: Other
2015 | ON | NBC | Div B | 3.9.1.2.(1) | Application | This Section applies to self-service storage buildings that (a) are not more than one storey in building height, (b) do not contain a basement or mezzanine, (c) consist of individual self-service storage units with external accessonly, (d) are used for no purpose other than storage, and (e) except as provided in Sentences 3.9.3.1.(2) and (4), contain no other major occupancy. Where there is a conflict between the requirements ofthis Section and other requirements in Part 3, this Section shall govern. | obc2019_divb | Div B | 3.10.1.1.(1) | 3.10.1.1. Application | Except as provided in this Section, the requirements in this Division apply to self-service storage buildings. |  | Common Sentence | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B | 3.9.1.2.(1) | Application | This Section applies to self-service storage buildings that (a) are not more than one storey in building height, (b) do not contain a basement or mezzanine, (c) consist of individual self-service storage units with external accessonly, (d) are used for no purpose other than storage, and (e) except as provided in Sentences 3.9.3.1.(2) and (4), contain no other major occupancy. | obc2019_divb | Div B | 3.10.4.1.(1) | 3.10.4.1. Application | The requirements in this Subsection apply to 1 storey buildings that do not contain a basement or mezzanine. |  | Common Sentence | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B | 3.9.1.2.(3) | Application | The requirements in Part 3 regarding occupant load shall not apply to self-service storage buildings. | obc2019_divb | Div B | 3.10.2.2.(1) | 3.10.2.2. Occupant Load | The requirements based on occupant load shall not apply. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.9.1.3.(1) | Occupancy Classification | Self-service storage buildings shall be classified as Group F, Division 2 major occupancies. | obc2019_divb | Div B | 3.10.2.1.(1) | 3.10.2.1. Occupancy Classification | A self-service storage building, (a) shall comply with the requirements for a Group F, Division 2 major occupancy, and (b) shall not contain a Group F, Division 1 occupancy. |  | Common Sentence | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B | 3.9.2.1.(1) | Building Area | For the purpose of applying the requirements of Subsections 3.2.1 and 3.2.2 to self-service storage buildings, building area shall mean (a) the building area of each building, or (b) the total of the building areas of all buildings as a group. | obc2019_divb | Div B | 3.10.4.2.(1) | 3.10.4.2. Building Area | For the purposes of Subsection 3.2.2., building area means, (a) the building area of each building, (b) the total of the building areas of all buildings as a group, or (c) the total of the building areas of any number or group of buildings. |  | Common Sentence | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B | 3.9.2.2.(1) | Spatial Separation | Except as provided in Sentence (3), the spatial separation requirements in Subsection 3.2.3.shall apply to self-service storage buildings. | obc2019_divb | Div B | 3.10.4.3.(1) | 3.10.4.3. Spatial Separations | Except as provided in Sentences (2) to (4), the requirements in Subsection 3.2.3. shall apply. |  | Common Sentence | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B | 3.9.2.2.(2) | Spatial Separation | The distance between each group of self-service storage buildings shall be not less than 9 m. | obc2019_divb | Div B | 3.10.4.3.(3) | 3.10.4.3. Spatial Separations | Where the building area conforms to Clause 3.10.4.2.(1)(c), (a) the limiting distance requirements shall apply between each group of buildings, but not between individual buildings within a group, and (b) the distance between each group of buildings shall be not less than 9 m. |  | Common Sentence | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B | 3.9.2.2.(3) | Spatial Separation | Subsection 3.2.3.need not apply between buildings within a group of self-service storage buildings, where the distance between these buildings is at least 6 m. | obc2019_divb | Div B | 3.10.4.3.(4) | 3.10.4.3. Spatial Separations | The distance between individual buildings within a group shall be not less than 6 m. |  | Common Sentence | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B | 3.9.3.1.(1) | Safety Requirements Within Floor Areas | Except as provided in Sentences 3.9.3.1.(2) to 3.9.3.1.(6), the requirements of Section 3.3 shall apply. (See Note A-3.9.3.1.(1).) | obc2019_divb | Div B | 3.10.2.4.(1) | 3.10.2.4. Safety Requirements Within Floor Areas | Except as provided in Sentences (2) to (12), the requirements in Section 3.3. shall apply. |  | Common Sentence | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B | 3.9.3.1.(2) | Safety Requirements Within Floor Areas | Not more than one dwelling unit is permitted to be contained within one of the self-service storage buildings on a property. | obc2019_divb | Div B | 3.10.2.4.(9) | 3.10.2.4. Safety Requirements Within Floor Areas | Not more than two dwelling units shall be contained within one of the buildings on the property. |  | Common Sentence | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B | 3.9.3.1.(3) | Safety Requirements Within Floor Areas | A dwelling unit referred to in Sentence (2) shall be separated from individual self-service storage units by a fire separation having a fire-resistance rating not less than 2 h. | obc2019_divb | Div B | 3.10.2.4.(10) | 3.10.2.4. Safety Requirements Within Floor Areas | Except as provided in Sentence (11), dwelling units shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 2 h. |  | Common Sentence | No
2015 | ON | NBC | Div B | 3.9.3.1.(4) | Safety Requirements Within Floor Areas | Where an office not more than 50 m2 in area is adjacent to a dwelling unit referred to in Sentence (2), it shall be considered as part of the dwelling unit. | obc2019_divb | Div B | 3.10.2.4.(11) | 3.10.2.4. Safety Requirements Within Floor Areas | A fire separation is not required between a dwelling unit and an office where the office is not more than 50 m2 in area. |  | Common Sentence | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B | 3.9.3.1.(5) | Safety Requirements Within Floor Areas | Fire separations required by Sentences 3.3.1.1.(1) and 3.3.5.9.(1) need not be provided between individual self-service storage units. | obc2019_divb | Div B | 3.10.2.4.(12) | 3.10.2.4. Safety Requirements Within Floor Areas | The fire separations required in Sentence 3.3.1.1.(1) need not be provided between individual rental spaces. |  | Common Sentence | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B | 3.9.3.1.(6) | Safety Requirements Within Floor Areas | The floor area of self-service storage buildings shall be (a) subdivided into compartments not more than 500 m2 in area by a fire separation having a fire-resistance rating not less than 1 h, or (b) sprinklered. (See alsoSentence 3.4.6.12.(2) for the exemption applying to exit doors of individual self-service storage units.) | obc2019_divb | Div B | 3.10.2.3.(2) | 3.10.2.3. Structural Fire Protection | The first storey shall be subdivided into areas not more than 500 m2 by a masonry or reinforced concrete fire separation having a fire-resistance rating not less than 1 h, or it shall be sprinklered. |  | Common Sentence | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B | 3.9.3.2.(1) | Sanitary Facilities | Except as provided in Sentence 3.7.2.1.(1), two public washrooms, each containing a water closet and a lavatory, shall be provided within one of the self-service storage buildings on the property. (See Note A-3.9.3.2.(1).) | obc2019_divb | Div B | 3.10.2.7.(2) | 3.10.2.7. Sanitary Facilities | Except as permitted in Sentences 3.7.4.1.(2) and (3), two washrooms, each containing a water closet and a lavatory, shall be provided within one of the buildings on the property. |  | Common Sentence | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B | 5.7.1.2.(1) | Required Protection | The building shall be located, the building site shall be graded, or water shall be directed away from building assemblies so as to prevent or accommodate the accumulation of surface water against the building or adjacent buildings. | obc2019_divb | Div B | 3.1.18.1.(1) | 3.1.18.1 Drainage | The building shall be located and the building site graded so that water will not accumulate at or near the building and will not adversely affect any adjacent properties. |  | Common Sentence | Yes | Water Drainage
2015 | ON | NBC | Div B | 3.1.1.3.(1) | Use of Term Storage Tank | For the purposes of this Part, the term “storage tank” shall mean a vessel for flammable liquids or combustible liquids having a capacity of more than 230L and designed to be installed in a fixed location. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire Hazards
2015 | ON | NBC | Div B | 3.1.13.1.(1) | Interior Finishes, Furnishings and Decorative Materials | Except as otherwise provided by this Subsection, interior finishes, furnishings and decorative materials shall conform to Section 2.3. of Division B of the NFC. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Construction Materials
2015 | ON | NBC | Div B | 3.1.13.6.(6) | Corridors | Where the floor area is sprinklered throughout, the flame-spread rating of the interior ceiling finish of corridors and occupancies referred to in Sentences (1) and (4) shall be not more than 150. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Construction Materials
2015 | ON | NBC | Div B | 3.1.15.2.(4) | Roof Covering Classification | Where buildings conforming to Article 3.2.2.50. or 3.2.2.58. include non-contiguous roof assemblies at different elevations, the roof coverings referred to in Sentence (3) are permitted to be evaluated separately to determine the roof covering classification required. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Mid-rise Wood
2015 | ON | NBC | Div B | 3.1.3.2.(1) | Prohibition of Occupancy Combinations | No major occupancy of Group F, Division 1 shall be contained within a building with any occupancy classified as Group A, B or C. | obc2019_divb | Div B | 3.1.3.2.(1) | 3.1.3.2. Prohibition of Occupancy Combinations | 0 |  | National Only | Yes
2015 | ON | NBC | Div B | 3.1.4.3.(2) | Wires and Cables | Except as permitted in Sentences (3) and (4), optical fibre cables and electrical wires and cables with combustible insulation, jackets or sheathes that are used for the transmission of voice, sound or data and are installed in a plenum in a building permitted to be of combustible construction shall exhibit the following characteristics when tested in conformance with CAN/ULC-S102.4, “Test for Fire and Smoke Characteristics of Electrical Wiring, Cables and Non-Metallic Raceways,” (FT6rating): (a) a horizontal flame distance of not more than 1.5 m, (b) an average optical smoke density of not more than 0.15, and (c) a peak optical smoke density of not more than 0.5. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Construction Materials
2015 | ON | NBC | Div B | 3.1.4.3.(3) | Wires and Cables | Except as permitted in Sentence (4), where totally enclosed noncombustible raceways are used in a plenum, exposed components of wiring systems with combustible insulation, jackets or sheathes, including optical fibre cables and electrical wires and cables that are used for the transmission of voice, sound or data, that are installed in the plenum or that extend not more than 9 m from the plenum, including drop down to the floor level, are permitted, provided they exhibit a vertical char of not more than 1.5 m when tested in conformance with the Vertical Flame Test–Cables in Cable Trays (FT4rating) in CSA C22.2 No.0.3, “Test Methods for Electrical Wires and Cables.” | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Construction Materials
2015 | ON | NBC | Div B | 3.1.4.3.(4) | Wires and Cables | Cables or wires within plenums that are used for the transmission of signals in fire alarm systems need not comply with the requirements of Sentence (2). | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Construction Materials
2015 | ON | NBC | Div B | 3.1.4.8.(2) | Exterior Cladding | A wall assembly conforming to Clause (1)(b) that includes combustible cladding made of fire-retardant-treated wood shall be tested for fire exposure after the cladding has been subjected to the accelerated weathering test specified in ASTM D 2898, “Accelerated Weathering of Fire-Retardant-Treated Wood for Fire Testing.” | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Mid-rise Wood
2015 | ON | NBC | Div B | 3.1.5.10.(4) | Combustible Flooring Elements | Combustible finished flooring is permitted in a building required to be of noncombustible construction. | obc2019_divb | Div B | 3.1.5.8.(4) |  |  |  | National Only | Yes
2015 | ON | NBC | Div B | 3.1.5.12.(2) | Combustible Interior Finishes | Combustible interior wall finishes, other than foamed plastics, that are not more than 25 mm thick are permitted in a building required to be of noncombustible construction, provided they have a flame-spread rating not more than 150 on any exposed surface, or any surface that would be exposed by cutting through the material in any direction. | obc2019_divb | Div B | 3.1.5.10.(2) |  |  |  | National Only | Yes
2015 | ON | NBC | Div B | 3.1.5.12.(4) | Combustible Interior Finishes | Combustible interior ceiling finishes made of fire-retardant-treated wood are permitted in a building required to be of noncombustible construction, provided they are not more than 25 mm thick or are exposed fire-retardant-treated wood battens. | obc2019_divb | Div B | 3.1.5.10.(4) |  |  |  | National Only | Yes
2015 | ON | NBC | Div B | 3.1.5.14.(2) | Combustible Insulation | Combustible insulation with a flame-spread rating not more than 25 on any exposed surface, or any surface that would be exposed by cutting through the material in any direction, is permitted in a building required to be of noncombustible construction. | obc2019_divb | Div B | 3.1.5.12.(2) |  |  |  | National Only | Yes
2015 | ON | NBC | Div B | 3.1.5.14.(3) | Combustible Insulation | Combustible insulation is permitted to be installed above roof decks, outside of foundation walls below ground level, and beneath concrete slabs-on-ground of buildings required to be of noncombustible construction. | obc2019_divb | Div B | 3.1.5.12.(3) |  |  |  | National Only | Yes
2015 | ON | NBC | Div B | 3.1.5.21.(2) | Wires and Cables | Except as permitted in Sentences (3) and (4), optical fibre cables and electrical wires and cables with combustible insulation, jackets or sheathes that are used for the transmission of voice, sound or data and are not located in totally enclosed noncombustible raceways are permitted to be installed in a plenum in a building required to be of noncombustible construction, provided the wires and cables exhibit a horizontal flame distance of not more than 1.5 m, an average optical smoke density of not more than 0.15, and a peak optical smoke density of not more than 0.5 when tested in conformance with CAN/ULC-S102.4, “Test for Fire and Smoke Characteristics of Electrical Wiring, Cables and Non-Metallic Raceways,” (FT6 rating). | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Construction Materials
2015 | ON | NBC | Div B | 3.1.5.21.(3) | Wires and Cables | Except as permitted in Sentence (4), where totally enclosed noncombustible raceways are used in a plenum, exposed components of wiring systems with combustible insulation, jackets or sheathes, including optical fibre cables and electrical wires and cables that are used for the transmission of voice, sound or data, that are installed in the plenum or that extend not more than 9 m from the plenum including drop down to the floor level, are permitted provided they exhibit a vertical char of not more than 1.5 m when tested in conformance with the Vertical Flame Test–Cables in Cable Trays (FT4 rating)in CSA C22.2 No. 0.3,“Test Methods for Electrical Wires and Cables.” | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Construction Materials
2015 | ON | NBC | Div B | 3.1.5.21.(4) | Wires and Cables | Cables or wires within plenums that are used for the transmission of signals in fire alarm systems need not comply with the requirements of Sentences (2) and (3). | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Construction Materials
2015 | ON | NBC | Div B | 3.1.5.23.(2) | Non-metallic Raceways | Totally enclosed non-metallic raceways used in a plenum in a building required more than 1.5 m, an average optical smoke density of not more than 0.15, and a peak optical smoke density of not more than 0.5 when tested in conformance with CAN/ULC S102.4, “Test for Fire and Smoke Characteristics of Electrical Wiring, Cables and Non-Metallic Raceways,” (FT6 rating). | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Construction Materials
2015 | ON | NBC | Div B | 3.1.6.2.(1) | Restrictions | An air-supported structure shall not be located above the first storey on any building. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Tents and Air-Supported Structures
2015 | ON | NBC | Div B | 3.1.6.3.(1) | Clearance to Other Structures | Except as permitted by Sentences (2), (3) and (4), every tent and air-supported structure shall conform to Subsection 3.2.3. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Tents and Air-Supported Structures
2015 | ON | NBC | Div B | 3.1.9.5.(1) | Combustible Piping Penetrations | Combustible sprinkler piping is permitted to penetrate a fire separation provided the fire compartments on each side of the fire separation are sprinklered. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Construction Materials
2015 | ON | NBC | Div B | 3.1.9.5.(2) | Combustible Piping Penetrations | Combustible water distribution piping is permitted to penetrate a fire separation that is required to have a fire-resistance rating without being incorporated in the assembly at the time of testing as required by Article 3.1.9.2., provided the piping is protected at the penetration with a firestop in conformance with Sentence (4). | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Construction Materials
2015 | ON | NBC | Div B | 3.2.2.17.(1) | Arena-Type Building Roof Assembly | The requirements for a roof assembly to have a fire-resistance rating are permitted to be waived for a gymnasium, a swimming pool, an arena, or a rink if no part of the roof assembly is less than 6 m above the main floor or balcony and the roof carries no loads other than normal roof loads, including permanent access walks, and ventilating, sound and lighting equipment, except that the restriction concerning minimum distance shall not apply to (a) an inclined and stepped floor ascending from the main floor which is used for seating purposes only, or (b) a balcony used for seating purposes only. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.18.(2) | Automatic Sprinkler System Required | If a storey in a building or a floor area is required to have an automatic sprinkler system installed throughout in accordance with one or more of Articles 3.2.2.20. to 3.2.2.90. or Section 3.3., the automatic sprinkler system shall also be installed throughout all lower storeys in the building notwithstanding permission in Articles 3.2.2.20. to 3.2.2.90. to construct one or more of those storeys without installing automatic sprinkler protection. (See Note A-3.2.2.18.(2).) | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.44.(1) | Group B, Division 3, up to 3 Storeys, Sprinklered | A building classified as Group B, Division 3 is permitted to conform to Sentence (2) provided (a) except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout, (b) it is not more than 3 storeys in building height, and (c) it has a building area not more than (i) 5 400 m2 if 1 storey in building height, (ii) 2 700 m2 if 2 storeys in building height, or (iii) 1 800 m2 if 3 storeys in building height. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.44.(2) | Group B, Division 3, up to 3 Storeys, Sprinklered | The building referred to in Sentence 3.2.2.44.(1) is permitted to be of combustible construction or noncombustible construction, used singly or in combination, and (a) floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, (b) mezzanines shall have a fire-resistance rating not less than 1 h, and (c) loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.76.(1) | Group F, Division 2, up to 3 Storeys | A building classified as Group F, Division 2 is permitted to conform to Sentence (2) provided (a) it is not more than 3 storeys in building height, and (b) it has a building area not more than the value in Table 3.2.2.76. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.2.76.(2) | Group F, Division 2, up to 3 Storeys | The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and (a) floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min, (b) mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, (c) roof assemblies shall have, if of combustible construction, a fire-resistance rating not less than 45 min, except that in a building not more than 1 storey in building height, the fire-resistance rating is permitted to be waived provided that the roof assembly is constructed as a fire-retardant-treated wood roof system conforming to Article 3.1.14.1., (d) loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall (i) have a fire-resistance rating not less than 45 min, or (ii) be of noncombustible construction, and (e) loadbearing walls, columns and arches supporting a fire separation shall have a fire-resistance rating not less than that required for the fire separation. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.3.16.(2) | Protection of Soffits | The soffit protection required by Sentence (1) shall extend the full width of the opening and to not less than 1 200 mm on either side of it, and shall apply to all openings through the soffit within this limit. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.3.21.(1) | Storage and Process Equipment Located Outdoors | Location of outdoor storage and outdoor process equipment in relation to buildings shall conform to Parts 3 and 4 of Division B of the NFC. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire hazards
2015 | ON | NBC | Div B | 3.2.3.4.(1) | Party Wall | A party wall shall be constructed as a firewall. (See Note A-3.2.3.4.(1).) | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.3.7.(2) | Construction of Exposing Building Face | Except as provided in Sentences (3) and (4) and Article 3.2.3.10., the fire-resistance rating, construction and cladding for exposing building faces of buildings or fire compartments of Group E or Group F, Division 1 or 2 occupancy classification shall comply with Table 3.2.3.7. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.4.1.(1) | Determination of Requirement for a Fire Alarm System | Except as permitted in Sentences (2) and (3), a fire alarm system shall be installed in buildings in which an automatic sprinkler system is installed. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.1.(2) | Determination of Requirement for a Fire Alarm System | Buildings in which a sprinkler system is installed in accordance with NFPA 13D, “Installation of Sprinkler Systems in One- and Two-Family Dwellings and Manufactured Homes, ”need not comply with Sentence (1). | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.1.(3) | Determination of Requirement for a Fire Alarm System | Buildings that contain fewer than 9 sprinklers conforming to Sentence 3.2.5.12.(4) need not comply with Sentence (1). | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.10.(4) | Fire Detectors | Fire detectors required by Sentence (2) shall be installed in elevator hoistways and dumbwaiter shafts where a sprinkler system is not installed within the hoistway or shaft. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.11.(2) | Smoke Detectors | Smoke detectors need not be installed in sleeping rooms and in corridors serving the sleeping rooms within a suite of care occupancy where smoke alarms are installed in accordance with Article 3.2.4.20. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.15.(3) | System Monitoring | The actuation of each waterflow detecting device required by Sentence (1) shall be indicated separately on the fire alarm system annunciator. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.16.(5) | Manual Stations | Where a fire alarm system is installed, a manually operated fire alarm station shall be installed on the roof at each exit from a helicopter landing area. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.5.10.(1) | Hose Connections | Hose connections shall be located in exits, in accordance with NFPA 14, “Installation of Standpipe and Hose Systems.” | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire Suppression
2015 | ON | NBC | Div B | 3.2.5.10.(2) | Hose Connections | Hose connections are not required within a floor area. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire Suppression
2015 | ON | NBC | Div B | 3.2.5.10.(3) | Hose Connections | Hose connections shall be provided with sufficient clearance to permit the use of a standard fire department hose key. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire Suppression
2015 | ON | NBC | Div B | 3.2.5.10.(4) | Hose Connections | Except as permitted by Sentence (5), 64 mm diam hose connections shall be installed in a standpipe system. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire Suppression
2015 | ON | NBC | Div B | 3.2.5.11.(1) | Hose Stations | Hose stations for 38 mm diam hose shall be installed for a standpipe system in a building that is not sprinklered throughout. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire Suppression
2015 | ON | NBC | Div B | 3.2.5.11.(2) | Hose Stations | Hose stations for 38 mm diam hose shall be installed for a standpipe system within every floor area that is not sprinklered throughout.(See Note A-3.2.5.11.(2).) | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire Suppression
2015 | ON | NBC | Div B | 3.2.5.11.(3) | Hose Stations | Hose stations shall be located in the floor area within 5 m of exits and at other locations to provide coverage of the entire floor area. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire Suppression
2015 | ON | NBC | Div B | 3.2.5.11.(6) | Hose Stations | Where a building or part thereof is used as a distillery and the building is sprinklered in conformance with Article 3.2.5.12., small hose (38mm) stations are permitted to be supplied from interior sprinkler piping. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire Suppression
2015 | ON | NBC | Div B | 3.2.5.11.(7) | Hose Stations | Where a hose station is provided in grain handling and storage facilities in which combustible dusts are produced in quantities or concentrations that create an explosion or firehazard,fog and fine spray nozzles shal lbe used instead of nozzles that discharge a solid stream of water to prevent combustible dusts from being raised into suspension. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire Suppression
2015 | ON | NBC | Div B | 3.2.8.4.(2) | Vestibules | An exit opening into an interconnected floor space shall conform to Sentence 3.4.3.2.(6). | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B | 3.2.8.6.(1) | Draft Stops | A draft stop shall be provided at each floor level within an interconnected floor space, immediately adjacent to and surrounding the opening, and shall be not less than 500 mm deep measured from ceiling level down to the underside of the draft stop. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B | 3.2.8.8.(1) | Combustible Content Limits | An interconnected floor space shall be designed so that the combustible contents, excluding interior finishes, in those parts of a floor area in which the ceiling is more than 8 m above the floor, are limited to not more than 16 g of combustible material for each cubic metre of volume of the interconnected floor space. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B | 3.3.2.1.(2) | Scope | Except as required in Sentence (3), provisions 12.2.3.2, 12.2.3.3, 12.2.5.4, 12.2.5.5, 12.2.5.6, 12.2.11.1, 12.4.1 and 12.4.2 of Chapter 12 of NFPA101, “LifeSafetyCode,” are permitted to be used in lieu of Articles 3.3.2.4., 3.3.2.5., 3.3.2.9., 3.3.2.11. and 3.3.2.12. (See Note A-3.3.2.1.(2).) | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Assembly Seating
2015 | ON | NBC | Div B | 3.3.2.1.(3) | Scope | The minimum clear width of aisle accessways between rows of seats shall be calculated according to provisions 12.2.5.5.2, 12.2.5.5.4.1 and 12.2.5.5.5.1 of Chapter 12 of NFPA 101, “Life Safety Code,” except that in no case shall the width be less than 400 mm. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Assembly Seating
2015 | ON | NBC | Div B | 3.3.2.11.(3) | Outdoor Places of Assembly | Exits from outdoor stadia or grandstands shall be located not more than 25 m apart. | obc2019_divb | Div B | 3.3.2.9.(3) |  |  |  | National Only | Yes
2015 | ON | NBC | Div B | 3.3.2.11.(4) | Outdoor Places of Assembly | The capacity of a means of egress for a Group A, Division 4 occupancy shall conform to the requirements of Sentence 3.4.3.2.(3). | obc2019_divb | Div B | 3.3.2.9.(4) |  |  |  | National Only | Yes
2015 | ON | NBC | Div B | 3.3.2.12.(1) | Bleachers | Steps provided in aisles of bleachers of the telescopic type shall (a) have risers not more than 250 mm high, and (b) have treads with a run not less than 280 mm. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Assembly Seating
2015 | ON | NBC | Div B | 3.3.3.4.(1) | Doorway Width | Except as provided in Sentence (2) and within individual suites of care occupancy, the minimum clear width of a doorway shall be 850 mm where it opens into or is located within a public corridor or other facility that provides access to exit for patients or residents in floor areas containing care or treatment occupancies. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.3.3.5.(10) | Compartments and Fire Separations | The fire separation requirements of Sentence (8) do not apply to walls within individual suites of care occupancy. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.3.3.5.(13) | Compartments and Fire Separations | A door or wall separating a patient’s or resident’s sleeping room from an ensuite toiletroom,shower room or similar ancillary space is permitted to incorporate grilles and louvres, provided (a) the adjacent rooms are not used to store flammable or combustible materials, and (b) the openings are located so that smoke cannot pass through these rooms to other parts of the building. (See Note A-3.3.3.5.(13).) | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.3.3.5.(14) | Compartments and Fire Separations | Walls between individual suites of care occupancy and the remainder of the floor area in buildings of care occupancy shall be constructed as fire separations with a fire-resistance rating not less than that specified for residential occupancies in Sentences 3.3.4.2.(1) and (2). | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.3.3.5.(15) | Compartments and Fire Separations | Floor assemblies within individual suites of care occupancy need not be constructed as fire separations, provided the suites meet the conditions described in Clauses 3.3.4.2.(3)(a) and (b). | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.3.5.7.(2) | Vestibules | If access is provided through a fire separation between a storage garage and a Group B, Division 3 occupancy with not more than 10 occupants, access need not be through a vestibule, provided the fire separation complies with Clauses 3.3.4.2.(5)(b) to (d). | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.3.5.8.(1) | Dispensing of Fuel | Facilities for the dispensing of fuel having a flash point below 37.8°C shall not be installed above any space intended for occupancy. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire Hazards
2015 | ON | NBC | Div B | 3.3.5.8.(2) | Dispensing of Fuel | Facilities for the dispensing of fuel having a flashpoint below 37.8°C shall not be installed in any building, except that this requirement does not apply to a canopy which is open on not less than 75% of its perimeter. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire Hazards
2015 | ON | NBC | Div B | 3.3.5.9.(1) | Multiple-Tenant Self-Storage Washouses | Except as provided in Sentence 3.9.3.1.(5) or unless the building is sprinklered throughout, each individual tenancy in a multiple tenant self storage warehouse classified as an industrial occupancy shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 45 min. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire Hazards
2015 | ON | NBC | Div B | 3.3.6.2.(4) | 3.3.6.2. Storage of Dangerous Goods | Where wiring or electrical equipment is located in areas in which flammable gases or vapours, combustible dusts or combustible fibres are present in quantities sufficient to create a hazard, such wiring and electrical equipment shall conform to CSA C22.1, “Canadian Electrical Code, Part I,” for hazardous locations. (See Note A-3.3.6.2.(4).) | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire hazards
2015 | ON | NBC | Div B | 3.3.6.3.(1) | Indoor Storage of Anhydrous Ammonia and Flammable, Toxic and Oxidizing Gases | Where required by the NFC, cylinders of dangerous goods classified as flammable gases stored indoors shall be located in a room (a) that is separated from the remainder of the building by a gas-tight fire separation having a fire-resistance rating of atleast 2 h, (b) that is located on an exterior wallof the building, (c) that can be entered from the exterior, and (d) whose closures leading to the interior of the building are (i) equipped with self-closing devices that keep the closures closed when not in use, and (ii) constructed so as to prevent the migration of gases from the room into other parts of the building. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire hazards
2015 | ON | NBC | Div B | 3.3.6.3.(2) | Indoor Storage of Anhydrous Ammonia and Flammable, Toxic and Oxidizing Gases | Where required by the NFC, cylinders of anhydrous ammonia or dangerous goods classified as toxic or oxidizing gases stored indoors shall be located in a room (a) that is separated from the remainder of the building by a gas-tight fire separation having a fire-resistance rating of atleast 1 h, (b) that is located on an exterior wall of the building, (c) that can be entered from the exterior, and (d) whose closures leading to the interior of the building are (i) equipped with self-closing devices that keep the closures closed when not in use, and (ii) constructed so as to prevent the migration of gases from the room into other parts of the building. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire hazards
2015 | ON | NBC | Div B | 3.4.2.5.(3) | Location of Exits | Exits shall be located and arranged so that they are clearly visible or their locations are clearly indicated and they are accessible at all times. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.4.6.17.(1) | Security for Banks and Mercantile Areas | If a building is sprinklered throughout,the requirements of Sentence 3.4.6.16.(1) are permitted to be waived for exit and egress doors complying with Sentences (2) to (9) that serve a floor area or part of a floor area usedexclusively for (a) a bank, or (b) the sale of retail merchandise. (See Note A-3.4.6.17.(1).) | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.4.6.17.(2) | Security for Banks and Mercantile Areas | Exit and egress doors referred to in Sentence (1) shall be designed to prevent locking at anytime that the part of the floor area that they serve is open to the public. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.4.6.17.(3) | Security for Banks and Mercantile Areas | A sign with the words “This door shall not be locked at anytime that the public is present” in letters not less than 50 mm high shall be permanently affixed to both sides of doors referred to in Sentence (1). | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.4.6.17.(4) | Security for Banks and Mercantile Areas | Exit and egress facilities complying with Sentences (5) to (9) shall be incorporated for egress by persons other than the public from a floor area or a part of a floor area referred to in Sentence (1)during times when the public is neither present nor being admitted to the area that they serve. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.4.6.17.(5) | Security for Banks and Mercantile Areas | In exit and egress facilities referred to in Sentence (4), at least one door at each exit and egress location shall (a) be operable in conformance with Sentence 3.4.6.16.(1), or (b) be equipped with locks conforming to Sentence 3.4.6.16.(4) that release immediately (i) if an alert signal or alarm signal is initiated in the fire alarm system, or (ii) the sprinkler system is actuated. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.4.6.17.(6) | Security for Banks and Mercantile Areas | A door referred to in Sentence (5) shall be permanently and distinctly marked to indicate that it is an emergency exit. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.4.6.17.(7) | Security for Banks and Mercantile Areas | Exit and egress facilities required for evacuation of persons other than the public from a floor area or a part of a floor area referred to in Sentence (1) shall have an aggregate width based on the maximum number of persons other than the public and determined in accordance with Articles 3.4.3.1.to 3.4.3.3. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.4.6.17.(8) | Security for Banks and Mercantile Areas | Travel distance to an exit referred to in Sentence (7) shall not exceed the travel distance determined in accordance with Subsection 3.4.2. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.4.6.17.(9) | Security for Banks and Mercantile Areas | Exit and egress doors serving a floor area or part of a floor area referred to in Sentence (1) are permitted to be equipped with locks that require keys, special devices or specialized knowledge of the door opening mechanism provided (a) the doors do not lead into exit stairs, (b) the doors do not lead from exit stairs to the exterior of the building, (c) the doors do not serve any other occupancy, (d) the area served contains at least one telephone (i) that is accessible and in operation at all times, (ii) that is not coin or card operated, and (iii) marked to indicate that it is for emergency use, (e) the area served is illuminated by normal power or by emergency power when the doors are locked, (f) there are provisions that enable an announcement to be made throughout the area served before the locks are fastened, and (g) the locks are designed for use during times that the building is not occupied. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.4.7.7.(1) | Landings | Platforms for a fire escape shall be provided in conformance with the requirements for stair landings in Articles 3.4.6.3.and 3.4.6.4. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Means of Egress
2015 | ON | NBC | Div B | 3.5.2.1.(1) | Elevators, Escalators and Dumbwaiters | The design,construction, installation and alteration of every elevator, escalator and dumbwaiter shall conform to (a) provincial or territorial regulations or municipal bylaws, or (b) ASMEA17.1/CSA B44, “Safety Code for Elevators and Escalators,” in the absence of the regulations or byl aws referred to in Clause (a). (See Note A-3.5.2.1.(1).) | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Vertical Transportation
2015 | ON | NBC | Div B | 3.5.2.1.(2) | Elevators, Escalators and Dumbwaiters | Before being placed in service, every elevator, escalator or dumbwaiter installation, including safety and control devices, shall be inspected and tested in accordance with (a) provincial or territorial regulations or municipal bylaws, or (b) ASME A17.1/CSA B44, “Safety Code for Elevators and Escalators,” in the absence of the regulations or bylaws referred to in Clause (a). (See Note A-3.5.2.1.(1).) | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Vertical Transportation
2015 | ON | NBC | Div B | 3.5.4.2.(1) | Floor Numbering | Arabic numerals indicating the assigned floor number shall be mounted permanently on both jambs of passenger elevator hoistway entrances in conformance with Appendix E of ASME A17.1/CSAB44, “Safety Code for Elevators and Escalators.” | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Vertical Transportation
2015 | ON | NBC | Div B | 3.6.1.2.(1) | Electrical Wiring and Equipment | The installation of electrical wiring and electrical equipment shall conform to the requirements of (a) provincial or territorial regulations or municipal bylaws, or (b) CSA C22.1, “Canadian Electrical Code, Part I,” in the absence of the regulations or bylaws referred to in Clause (a). | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Building services and utilities
2015 | ON | NBC | Div B | 3.6.1.3.(1) | Lightning Protection Systems | A lightning protection system, when provided, shall conform to the requirements of the appropriate provincial or territorial legislation or, in the absence of such legislation, to CAN/CSA-B72-M,“Installation Code for Lightning Protection Systems.” | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire Hazards
2015 | ON | NBC | Div B | 3.6.1.5.(1) | Appliances Installed Outside a Building | A fuel-fired appliance installedon the roof of a building or in another location outside the building shall be installed not less than (a) 1.2 m from a propertyline, measured horizontally, and (b) 3 m from an adjacent wall of the same building if that wall contains any opening within 3 storeys above and 5 m horizontally from the appliance, unless every opening within these limits is protected by (i) a closure having a fire-protection rating not less than 45 min determined in accordance with Article 3.1.8.4., or (ii) a wired glass assembly permitted for use in a vertical fire separation anddescribedin D-2.3.15. in Appendix D. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Building services and utilities
2015 | ON | NBC | Div B | 3.6.2.7.(1) | Electrical Equipment Vaults | An electrical equipment vault shall conform to Sentences (2) to (8) if it is required by (a) provincial or territorial regulations or municipal bylaws, or (b) CSA C22.1, “Canadian Electrical Code, Part I,” in the absence of the regulations or bylaws referred to in Clause (a). | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Fire Hazards
2015 | ON | NBC | Div B | 3.6.5.1.(3) | Duct Materials | Combustible ducts which are part of a duct system conveying only ventilation air and are contained entirely within a dwelling unit need not comply with the requirements of Sentences (1) and (2). | obc2019_divb | Div B |  |  |  |  | National Only | Yes | HVAC
2015 | ON | NBC | Div B | 3.7.2.1.(2) | Plumbing and Drainage Systems | Waterless urinals are permitted to be used in buildings provided with a water supply. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B | 3.7.2.2.(15) | Water Closets | In a building whose floor area is more than 600 m2 and that includes one or more individual tenant spaces for a business and personal services occupancy or mercantile occupancy, water closets shall be located so that they are accessible to the public when the building is occupied. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B | 3.7.2.2.(16) | Water Closets | The number of water closets required in a suite of mercantile occupancy whose area is not more than 500 m2 is permitted to be determined in accordance with Table 3.7.2.2.-B based solely on the total number of staff. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B | 3.7.2.2.(3) | Water Closets | Except as permitted by Sentence (2), if only one universal washroom is provided in accordance with Section 3.8., the water closet in this room shall not be taken into consideration in determining the number of water closets required by this Article, unless a single water closet is permitted in accordance with Sentence (4). | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B | 3.7.2.9.(1) | Bathtubs | Where a bathtub is installed in a hotel or a motel, it shall (a) have a clear floor space atleast 750 mm wide along its length, except that a water closet or a lavatory is permitted to encroach this space, (b) have faucets and other controls that conform to Clause 3.8.3.8.(1)(b), (c) have a slip-resistant bottom surface, (d) have grab bars that (i) conform to Sentence 3.7.2.8.(1), (ii) are not less than 1 200 mm long located vertically at the end of the bathtub that is adjacent to the clear floor space, with the lower end between 180 mm and 280 mm above the bathtub rim, and (iii) are not less than 1 200 mm long located horizontally along the length of the bathtub at 180 mm to 280 mm above the bathtub rim, and (e) be capable of being accessed along its full length with no tracks mounted on the bathtub rim. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B | 3.8.1.1.(2) | Scope | Buildings and facilities required to be barrier-free in accordance with Subsection 3.8.2. shall be designed in accordance with Subsection 3.8.3. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Accessibility: Other
2015 | ON | NBC | Div B | 3.8.2.11.(2) | Counters and Counters for Telephones | Built-in shelves and counters provided for public telephones shall comply with Subsection 3.8.3. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Accessibility: Other
2015 | ON | NBC | Div B | 3.8.2.5.(3) | Access to Parking Areas and Exterior Passenger-Loading Zones | Exterior passenger-loading zones shall comply with Subsection 3.8.3. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Accessibility: Other
2015 | ON | NBC | Div B | 3.8.2.7.(2) | Power Door Operators | The requirements of Sentence (1) do not apply to an individual suite having an area less than 500 m2 in a building havingonly suites of assembly, care, business and personal services or mercantile occupancy if the suite is completely separated from the remainder of the building so that there is no access to the remainder of the building. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Accessibility: Other
2015 | ON | NBC | Div B | 3.8.2.7.(3) | Power Door Operators | Only the active leaf in a multiple leaf door in a barrier-free path of travel need conform to the requirements of this Article. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Accessibility: Other
2015 | ON | NBC | Div B | 3.8.2.8.(3) | Plumbing Facilities | In a building in which water closets are required in accordance with Subsection 3.7.2., atleast one barrier-free water closet shall be provided in the entrance storey, unless (a) a barrier-free path of travel is provided to barrier-free water closets elsewhere in the building, or (b) the water closets required by Subsection 3.7.2. are for dwelling units only. (See Note A-3.8.2.8.(1) to (4).) | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B | 3.8.2.8.(4) | Plumbing Facilities | Where alterations are made to an existing building, universal washrooms complying with Subsection 3.8.3. are permitted to be provided in lieu of facilities for persons with physical disabilities in washrooms used by the general public.(See Note A-3.8.2.8.(1) to (4).) | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B | 3.8.2.8.(5) | Plumbing Facilities | At least one water-closet stall or enclosure in a washroom required to be barrier-free shall comply with Subsection 3.8.3. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B | 3.8.2.8.(6) | Plumbing Facilities | Where urinals are provided in a barrier-free washroom, at least one urinal shall comply with Subsection 3.8.3. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B | 3.8.2.8.(7) | Plumbing Facilities | A barrier-free washroom shall be provided with a lavatory that complies with Subsection 3.8.3. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B | 3.8.2.8.(8) | Plumbing Facilities | Where mirrors are provided in a barrier-free washroom, atleast one mirror shall comply with Subsection 3.8.3. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B | 3.8.3.1.(1) | Design Standards | Buildings or parts thereof and facilities that are required to be barrier-free shall be designed in accordance with (a) this Subsection, or (b) the provisions of CSA B651, “Accessible Design for the Built Environment,” listed in Table 3.8.3.1., in their entirety. (See Note A-3.8.3.1.(1).) | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Accessibility: Other
2015 | ON | NBC | Div B | 3.8.3.17.(1) | Bathtubs | Bathtubs required by Sentence 3.8.2.8.(11) shall (a) be located in a room with a clear floor space not less than 1 500 mm in diameter, (b) be not less than 1 500 mm long, (c) have a clear floor space not less than 750 mm wide adjacent to its entire length, (d) be capable of being accessed along its full length with no tracks mounted on its rim, (e) have faucets and other controls that (i) conform to Clause 3.8.3.8.(1)(b), and (ii) are located on the centreline or between the centreline of the bathtub and the exterior edge of the bathtub rim, at a maximum height of 450 mm above the rim, (f) have three grab bars (i) that conform to Sentence 3.7.2.8.(1), (ii) that are not less than 1 200 mm long, (iii) two of which are located vertically at each end of the bathtub, set 80 mm to 120 mm in from the outside edge of the bathtub, with their lower end 180 mm to 280 mm above the bathtub rim, and (iv) one of which is located horizontally along the length of the bathtub at 180 mm to 280 mm above the bathtub rim, (g) have a slip-resistant bottom surface, and (h)be equipped with a hand-held shower head with not less than 1 800 mm of flexible hose that can be used in a fixed position at aheight of 1 200 mm and 2 030 mm. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B | 3.8.3.5.(2) | Ramps | Handrails installed in addition to required handrails need not comply with the height requirements stated in Clause (1)(e). | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B | 3.8.3.5.(4) | Ramps | The surfaces of ramps and landings shall a) be hard or resilient where the ramp is steeper than 1 in 15 (see Note A-3.8.3.5.(4)(a)), (b) have across slope no steeper than 1 in 50, and (c) where exposed to water, be designed to drain. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B | 3.8.3.5.(5) | Ramps | Ramps and landings not at grade or adjacent to a wall shall have edge protection consisting of (a) a curb not less than 75 mm high, or (b) a raised barrier or rail located not more than 100 mm from the ramp or landing surface. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B | 3.8.3.6.(1) | Doorways and Doors | Except where stated otherwise, this Article applies to swinging and sliding doors. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B | 3.8.3.6.(5) | Doorways and Doors | A threshold for a doorway referred to in Sentences (2) and (3) shall be not more than 13 mm higher than the finished floor surface and shall be beveled to facilitate the passage of wheelchairs. | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B | 3.8.3.6.(7) | Doorways and Doors | A cane-detectable guard shall be installed on the hinged side of power-assisted doors that swing open into the path of travel.(See Note A-3.8.3.6. (6) and(7).) | obc2019_divb | Div B |  |  |  |  | National Only | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B | 3.1.8.10.(4) | Installation of Fire Dampers |  | obc2019_divb | Div B | 3.1.8.9.(4) | 3.1.8.9. Installation of Fire Dampers | A fire damper shall be installed in the vertical or horizontal position in which it was tested. |  | P/T Only | No
2015 | ON | NBC | Div B | 3.2.2.66.(2) | Group D, up to 4 Storeys, Sprinklered |  | obc2019_divb | Div B | 3.2.2.59.(2) 3.2.2.52.(2) | 3.2.2.52. Group D, up to 4 Storeys, Sprinklered | The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and, floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, mezzanines shall have a fire-resistance rating not less than 1 h, and loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | P/T Only | No
2015 | ON | NBC | Div B | 3.2.2.82.(2) | Group F, Division 2, up to 4 Storeys, Increased Area, Sprinklered |  | obc2019_divb | Div B | 3.2.2.75.(2) | 3.2.2.75. Group F, Division 3, up to 6 Storeys, Sprinklered | Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and, floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, mezzanines shall have a fire-resistance rating not less than 1 h, and loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | P/T Only | No
2015 | ON | NBC | Div B | 3.2.3.7.(3) | Construction of Exposing Building Face |  | obc2019_divb | Div B | 3.2.3.7.(4) | 3.2.3.7. Construction of Exposing Building Face | Except as provided by Sentence (6), cladding for buildings or fire compartments where the maximum permitted area of unprotected openings is more than 10% but not more than 25% of the exposing building face need not be noncombustible where the wall assembly complies with Article 3.1.5.5. |  | P/T Only | Yes | Fire Containment
2015 | ON | NBC | Div B | 3.2.4.11.(3) | Smoke Detectors |  | obc2019_divb | Div B | 3.2.4.22.(16) | 3.2.4.22. Smoke Alarms | Smoke alarms required in suites in a retirement home or smoke detectors permitted to be installed in lieu of smoke alarms as provided in Sentence (6) shall upon actuation provide an audible and visual signal to staff serving those suites, so that the suite containing the actuated smoke alarm or smoke detector can be easily identified. |  | P/T Only | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.18.(8) | Audibility of Alarm Systems |  | obc2019_divb | Div B | 3.2.4.20.(10) | 3.2.4.20. Audibility of Alarm Systems (See Appendix A.) | Audible signal devices within a dwelling unit or a suite of residential occupancy shall be connected to the fire alarm system, (a) in a manner such that a single open circuit at one device will not impair the operation of other audible signal devices on the same circuit that serve the other dwelling units or suites of residential occupancy, or (b) on separate signal circuits that are not connected to the devices in any other dwelling unit, public corridor or suites of residential occupancy. |  | P/T Only | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B | 3.2.4.9.(2) | Electrical Supervision |  | obc2019_divb | Div B | 3.2.9.5.(1) | 3.2.9.5. Supervisory Signal Annunciation for Valves | If a fire alarm system in a building is required by Sentence 3.2.4.9.(1) to have an annunciator, valves controlling water supplies in a standpipe system, other than hose valves, shall be electrically supervised in accordance with Sentence 3.2.4.10.(2). |  | P/T Only | Yes | Fire Suppression
2015 | ON | NBC | Div B | 3.2.5.10.(4) | Hose Connections |  | obc2019_divb | Div B | 3.2.9.3.(1) | 3.2.9.3. Hose Connections | If a standpipe system is required in a building, 38 mm diam hose connections shall be provided in each storey in the building. |  | P/T Only | Yes | Fire Suppression
2015 | ON | NBC | Div B | 3.2.5.11.(4) | Hose Stations |  | obc2019_divb | Div B | 3.4.6.10.(7) | 3.4.6.10. Horizontal Exits | Any change in floor level from one side of a horizontal exit to the other side shall not exceed 2 000 mm. |  | P/T Only | Yes | Exits
2015 | ON | NBC | Div B | 3.2.8.2.(4) | Exceptions to Special Protection |  | obc2019_divb | Div B | 3.4.3.3.(1) | 3.4.3.3. Exits from Interconnected Floor Space | Exit stairs that serve interconnected floor spaces as provided in Articles 3.2.8.3. to 3.2.8.11. shall conform to the requirements in Article 3.2.8.4. and in this Section. |  | P/T Only | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B | 3.2.8.4.(3) | Vestibules |  | obc2019_divb | Div B | 3.2.8.5.(2) | 3.2.8.5. Elevators | Where elevator doors opening into an interconnected floor space are protected by vestibules in conformance with Sentence (1), the elevator doors opening into the lowest storey of the interconnected floor space need not be protected by such vestibules. |  | P/T Only | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B | 3.3.1.11.(2) | Door Swing |  | obc2019_divb | Div B | 3.4.6.16.(5) | 3.4.6.16. Door Release Hardware | Except as permitted by Sentences (6) and (7), electromagnetic locks are not permitted to be installed on exit doors, described in Clause (2)(a), (b) or (c), serving an elementary or secondary school, or leading directly from a high hazard industrial occupancy. |  | P/T Only | Yes | Electromagnetic Locks
2015 | ON | NBC | Div B | 3.3.1.11.(3) | Door Swing Direction of Door Swing |  | obc2019_divb | Div B | 3.4.6.12.(2) | 3.4.6.12. Direction of Door Swing | A door serving a single dwelling unit shall swing on its vertical axis. |  | P/T Only | Yes | Exits
2015 | ON | NBC | Div B | 3.3.1.18.(3) | Guards |  | obc2019_divb | Div B | 3.3.1.17.(3) | 3.3.1.17. Guards | Except as permitted by Sentence 3.3.5.9.(1), openings through any guard that is required by Sentence (1) and that is installed in a building of industrial occupancy shall be of a size which will prevent the passage of a sphere having a diameter more than 200 mm unless it can be shown that the location and size of openings that exceed this limit do not represent a hazard. |  | P/T Only | Yes | Falling, Tripping, Slipping Protection
2015 | ON | NBC | Div B | 3.3.1.5.(2) | Egress Doorways |  | obc2019_divb | Div B | 3.4.2.1.(7) | 3.4.2.1. Minimum Number of Exits | Each egress doorway in Sentence (6) shall be considered as contributing not more than, (a) one-third of the required width where three egress doorways are required, and (b) one-fourth of the required width where four egress doorways are required. |  | P/T Only | Yes | Hotels
2015 | ON | NBC | Div B | 3.3.3.3.(2) | Corridors |  | obc2019_divb | Div B | 3.4.1.11.(1) | 3.4.1.11. Exterior Stairway for Long-Term Care Homes | No open exterior stairway shall serve as a means of egress for residents above the second floor of a long-term care home. |  | P/T Only | Yes | Exits
2015 | ON | NBC | Div B | 3.3.4.4.(6) | Egress from Dwelling Units |  | obc2019_divb | Div B | 3.4.2.4.(4) | 3.4.2.4. Travel Distance | If there is a firewall in an elementary or secondary school, the travel distance shall not be measured to a door in the firewall, but shall be measured to an exterior exit door or an exit door to a stairway. |  | P/T Only | Yes | Schools
2015 | ON | NBC | Div B | 3.3.5.6.(1) | Storage Garage Separation |  | obc2019_divb | Div B | 3.4.4.1.(3) | 3.4.4.1. Fire-Resistance Rating of Exit Separations | In a building within the scope of Article 3.2.2.43A. or 3.2.2.50A., the fire-resistance rating of the fire separation referred to in Sentence (1) shall not be less than 1.5 h. |  | P/T Only | Yes | Mid-rise wood
2015 | ON | NBC | Div B | 3.4.2.2.(2) | Means of Egress from Mezzanines |  | obc2019_divb | Div B | 3.4.2.2.(3) | 3.4.2.2. Mezzanine Exiting | In a floor area that is not sprinklered, a mezzanine need not conform to Sentence (1) where Article 3.2.8.1. does require it to terminate at a vertical fire separation provided the total occupant load of the mezzanine is not more than 60 and, (a) the area of the mezzanine does not exceed the area limits for rooms and suites in Table 3.3.1.5.A., and (b) the distance limits in Table 3.3.1.5.A. are not exceeded from any point on the mezzanine to, (i) the egress doorway from the room in which the mezzanine is located if that room has a single egress doorway, or (ii) an egress facility leading from the mezzanine if the room in which the mezzanine is located has two egress doorways provided in conformance with Subsection 3.3.1. |  | P/T Only | Yes | Mezzanines
2015 | ON | NBC | Div B | 3.4.2.2.(2) | Means of Egress from Mezzanines |  | obc2019_divb | Div B | 3.4.2.2.(4) | 3.4.2.2. Mezzanine Exiting | In a floor area that is sprinklered, a mezzanine need not conform to Sentence (1) where Article 3.2.8.1. does require it to terminate at a vertical fire separation provided the total occupant load of the mezzanine is not more than 60 and, (a) the area of the mezzanine does not exceed the area limits for rooms and suites in Table 3.3.1.5.B., and (b) the distance of travel is not more than 25 m when measured from any point on the mezzanine to, (i) the egress doorway from the room in which the mezzanine is located if that room has a single egress doorway, or (ii) an egress facility leading from the mezzanine if the room in which the mezzanine is located has two egress doorways provided in conformance with Subsection 3.3.1. |  | P/T Only | Yes | Mezzanines
2015 | ON | NBC | Div B | 3.4.4.4.(6) | Integrity of Exits |  | obc2019_divb | Div B | 3.4.1.6.(3) | 3.4.1.6. Restricted Use of Horizontal Exits | Where an elementary or secondary school is subdivided by a firewall, a horizontal exit shall not serve as an exit but is permitted to serve as an access to exit. |  | P/T Only | Yes | Schools
2015 | ON | NBC | Div B | 3.4.5.1.(1) | Exit Signs |  | obc2019_divb | Div B | 3.4.2.1.(6) | 3.4.2.1. Minimum Number of Exits | Every room containing an assembly occupancy serving a hotel, and located in the building containing the hotel, shall be provided with no fewer than, (a) three separate egress doorways from the room where the occupant load is more than 600 persons, and (b) four separate egress doorways from the room where the occupant load is more than 1 000 persons. |  | P/T Only | Yes | Hotels
2015 | ON | NBC | Div B | 3.4.5.2.(1) | Signs for Stairs and Ramps at Exit Level |  | obc2019_divb | Div B | 3.4.5.2.(2) | 3.4.5.2. Signs Within Exit Facilities | An exit stair serving a building more than 6 storeys in building height shall be clearly marked by signs indicating that it does not lead to an exit at the roof level. (See Appendix A.) |  | P/T Only | Yes | Exits
2015 | ON | NBC | Div B | 3.4.6.10.(5) | Horizontal Exits |  | obc2019_divb | Div B | 3.4.4.1.(5) | 3.4.4.1. Fire-Resistance Rating of Exit Separations | The path of exit travel may lead from an exit door or exit enclosure through open air parking that is located below a roof or floor assembly that is part of the building served by the exit door or exit enclosure where, (a) the portion of the path of exit travel that leads through the open air parking is not more than 9 m in length measured from the exit door to a point at ground level at the perimeter of the building, (b) measures are taken to prevent vehicles intended to park in spaces adjacent to the path of exit travel from encroaching on the path of exit travel, and (c) an alternate means of egress not leading through the open air parking is available from the interior side of the door opening onto the path of exit travel through the open air parking area. |  | P/T Only | Yes | Exits
2015 | ON | NBC | Div B | 3.4.6.11.(2) | Doors |  | obc2019_divb | Div B | 3.4.6.11.(1) | 3.4.6.11. Doors | The distance between a stair riser and the leading edge of a door during its swing shall be not less than 300 mm. |  | P/T Only | No
2015 | ON | NBC | Div B | 3.4.6.16.(1) | Door Release Hardware |  | obc2019_divb | Div B | 3.4.6.16.(7) | 3.4.6.16. Door Release Hardware | Electromagnetic locks are permitted to be installed on an exit door that serves only a gaming premises if, the gaming premises is located within a sprinklered floor area, smoke detectors are installed in each room and each corridor accessible to the public, a force of not more than 90 N applied to the door opening hardware initiates an irreversible process that will release the locking device within 15 s and not relock until the door has been opened, and a legible sign conforming with Clause (4)(h) is permanently mounted on the exit door to indicate that the locking device will release within 15 s of applying pressure to the door release hardware. |  | P/T Only | Yes | Gaming Premises
2015 | ON | NBC | Div B | 3.4.6.18.(1) | Emergency Crossover Access to Floor |  | obc2019_divb | Div B | 3.4.6.18.(6) | 3.4.6.18. Emergency Crossover Access to Floor Areas | In a building not more than 6 storeys in building height, doors providing access from exit stairs to a floor area containing a hotel are permitted to have locking devices to prevent entry into the floor area provided the requirements in Clause (4)(b) are complied with. |  | P/T Only | Yes | Hotels
2015 | ON | NBC | Div B | 3.4.6.19.(1) | Floor Numbering |  | obc2019_divb | Div B | 3.4.6.19.(2) | 3.4.6.19. Floor Numbering | Upper case letters indicating the designation assigned to each exit stair shaft shall be mounted permanently on each side of doors to the exit stair shaft and shall, be not less than 60 mm high, raised approximately 0.7 mm above the surface, be located 1 500 mm from the finished floor, and be contrasting in colour with the surface on which they are applied. |  | P/T Only | Yes | Exits
2015 | ON | NBC | Div B | 3.4.6.9.(2) | Curved Flights in Exits |  | obc2019_divb | Div B | 3.4.3.4.(5) | 3.4.3.4. Exit Width Reduction (See Appendix A.) | In an elementary or secondary school, where a stair lift is installed in an exit stair, an intermediate handrail shall be installed between the path of travel of the stair lift and the remainder of the stair to ensure that the stair lift will not reduce the required width of the exit stair. |  | P/T Only | Yes | Schools
2015 | ON | NBC | Div B | 3.4.7.6.(4) | Guards and Railings |  | obc2019_divb | Div B | 3.4.6.6.(6) | 3.4.6.6. Guards | Openings through any guard that is required by Sentence (1) and that is installed in a building of industrial occupancy shall be of a size that will prevent the passage of a sphere having a diameter more than 200 mm unless it can be shown that the location and size of openings that exceed this limit do not represent a hazard. |  | P/T Only | Yes | Exits
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.1.2.(1) | 3.1.1.2. Radon | In addition to all other requirements, a building in the following designated areas shall be designed and constructed so that the annual average concentration of radon 222 does not exceed 200 Bq/m3 of air and the annual average concentration of the short lived daughters of radon 222 does not exceed 0.02 working levels inside the building: (a) the City of Elliot Lake in the Territorial District of Algoma, (b) the Township of Faraday in the County of Hastings, and (c) the geographic Township of Hyman in the Territorial District of Sudbury. |  | P/T Only | Yes | Vapour Management
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.1.3.(1) | 3.1.1.3. Building on Flood Plains | Buildings constructed on flood plains shall (a) be designed and constructed in accordance with good engineering practice to withstand anticipated vertical and horizontal hydrostatic pressures acting on the structure, and (b) incorporate floodproofing measures that will preserve the integrity of exits and means of egress during times of flooding. |  | P/T Only | Yes | Precipitation Management
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.13.7.(6) | 3.1.13.7. High Buildings | A plumbing fixture may have a smoke developed classification more than 300 but not more than 500 if, it is in a room where the wall surfaces have a smoke developed classification not more than 200, and it is located in, a Group C occupancy, or a Group B occupancy and the building is sprinklered. |  | P/T Only | Yes | Construction Materials
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.13.7.(5) | 3.1.13.7. High Buildings | A plumbing fixture that is not located in a Group B occupancy need not comply with Sentence (4) if the building is sprinklered. |  | P/T Only | Yes | Construction Materials
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.13.7.(7) | 3.1.13.7. High Buildings | A therapeutic bathing system in a Group B occupancy need not comply with Sentence 3.1.13.7.(4) if the room in which it is located, (a) does not open directly into patients’ or residents’ sleeping rooms, and (b) is sprinklered. |  | P/T Only | Yes | Construction Materials
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.13.7.(4) | 3.1.13.7. High Buildings | Except as permitted in Sentences (5) to (7), plumbing fixtures in a building regulated by the provisions of Subsection 3.2.6. shall have a smoke developed classification not more than 300. |  | P/T Only | Yes | Construction Materials
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.17.1.(5) | 3.1.17.1. Occupant Load Determination | Except as provided by Sentence (6) or (7), in dining, alcoholic beverage and cafeteria spaces the occupant load shall be determined from Table 3.1.17.1. |  | P/T Only | Yes | Occupant Load
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.17.1.(6) | 3.1.17.1. Occupant Load Determination | The occupant load in Sentence (5) is permitted to be the number of persons for which the space is designed. |  | P/T Only | Yes | Occupant Load
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.17.1.(7) | 3.1.17.1. Occupant Load Determination | The occupant load in Sentence (6) shall be not more than that determined by using an area of 0.6 m2 per person. |  | P/T Only | Yes | Occupant Load
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.17.2.(1) | 3.1.17.2. Dance Floor | The occupant load of a room in which a dance floor is situated shall be calculated in respect of that portion of the room that is not occupied by the dance floor. |  | P/T Only | Yes | Occupant Load
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.17.3.(1) | 3.1.17.3. Public Pools | The occupant load of a public pool, except a wave action pool, shall be determined by the following formula occupant load= D/2.5 + S/1.4 where, D = the water surface area in square metres of the part of the pool that is deeper than 1 350 mm; and S = the water surface area in square metres of the part of the pool that is 1 350 mm in depth or less. |  | P/T Only | Yes | Occupant Load
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.19.1.(1) | 3.1.19.1. Clearance to Buildings | A building shall not be located beneath existing above ground electrical conductors. |  | P/T Only | Yes | Building Services and Utilities
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.19.1.(4) | 3.1.19.1. Clearance to Buildings | Sentences (1) to (3) do not apply to a building containing electrical equipment and electrical installations used exclusively in the generation, transformation or transmission of electrical power or energy intended for sale or distribution to the public. |  | P/T Only | Yes | Building Services and Utilities
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.19.1.(2) | 3.1.19.1. Clearance to Buildings | The horizontal clearance measured from the maximum conductor swing to the building, including balconies, fire escapes, flat roofs or other accessible projections beyond the face of the building, shall, be not less than 1 m, for electrical conductors carrying voltages 750 V or less, except where necessary to connect to the electrical wiring of the building, be not less than 3 m, for electrical conductors carrying voltages greater than 750 V but not exceeding 46 kV, be not less than 3.7 m, for electrical conductors carrying voltages greater than 46 kV but not exceeding 69 kV, or conform to the requirements of CAN/CSA-C22.3 No.1, "Overhead Systems", for electrical conductors carrying voltages greater than 69 kV. |  | P/T Only | Yes | Building Services and Utilities
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.19.1.(3) | 3.1.19.1. Clearance to Buildings | Where the swing of an above ground electrical conductor not owned or operated by an electrical supply authority is not known, a swing of not less than 1.8 m shall be used. |  | P/T Only | Yes | Building Services and Utilities
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.2.6.(1) | 3.1.2.6. Restaurants | A restaurant is permitted to be classified as a Group E major occupancy provided the restaurant is designed to accommodate not more than 30 persons consuming food or drink. |  | P/T Only | Yes | Occupancy Classification
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.20.1.(1) | 3.1.20.1. Glass | Except as provided in Sentence 3.3.4.7.(1), glass in guards shall conform to MMAH Supplementary Standard SB-13, “Glass in Guards”. |  | P/T Only | Yes | Falling, Tripping, Slipping Protection
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.3.2.(4) | 3.1.3.2. Prohibition of Occupancy Combinations | A Group F, Division 2 major occupancy is permitted in a building containing only live/work units if the occupancy is for the exclusive use of the occupants of the live/work units. |  | P/T Only | Yes | Live/work Units
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.3.2.(3) | 3.1.3.2. Prohibition of Occupancy Combinations | A sleeping room or sleeping area shall not open directly into a room or area where food is intended to be stored, prepared, processed, distributed, served, sold or offered for sale. |  | P/T Only | Yes | Food Premises
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.4.3.(3) | 3.1.4.3. Wires and Cables (See Appendix A.) | Service-entrance cables for communication and community antennae distribution systems need not conform to Sentence (1) provided, (a) the service-entrance cables are located in a building permitted to be of combustible construction and are not more than 3 m in length from the point of entry into the building or from the point of leaving protection as required in Clause (1)(b), or (b) the service-entrance cables enter into an electrical or telephone service room separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h. |  | P/T Only | Yes | Construction Materials
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.4.3.(2) | 3.1.4.3. Wires and Cables (See Appendix A.) | The requirement in Clause (1)(a) is considered to be met where the wires and cables, (a) exhibit a vertical char of not more than 1.5 m when tested in conformance with the Vertical Flame Test ‚¬ Cables in Cabletrough in Clause 4.11.4. of CSA C22.2 No. 0.3, "Test Methods for Electrical Wires and Cables" (FT4 Rating), or (b) exhibit a flame-spread of not more than 1.5 m, a smoke density of not more than 0.5 at peak optical density and a smoke density not more than 0.15 at average optical density when tested in conformance with the Flame and Smoke Test in the Appendix to CSA C22.2 No. 0.3, "Test Methods for Electrical Wires and Cables" (FT6 Rating). |  | P/T Only | Yes | Construction Materials
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.4.9.(1) | 3.1.4.9. Combustible Piping | Except as provided by Sentence (2), combustible piping and tubing and associated adhesives used in a building within the scope of Article 3.2.2.43A. or 3.2.2.50A. shall have a flame-spread rating not more than 25. |  | P/T Only | Yes | Mid-rise Wood
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.4.9.(2) | 3.1.4.9. Combustible Piping | Sentence (1) does not apply to, (a) combustible sprinkler piping and associated adhesives, (b) combustible tubing for pneumatic controls and associated adhesives, provided the tubing has an outside diameter not more than 10 mm, (c) combustible piping and tubing and associated adhesives used in public pools and public spas, and (d) combustible piping and tubing and associated adhesives concealed in a concrete floor slab. |  | P/T Only | Yes | Mid-rise Wood
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.5.18.(2) | 3.1.5.18. Wires and Cables | The requirement in Clause (1)(a) is considered to be met where the wires and cables exhibit a flame-spread of not more than 1.5 m, a smoke density of not more than 0.5 at peak optical density and a smoke density not more than 0.15 at average optical density when tested in conformance with the Flame and Smoke Test in the Appendix to CSA C22.2 No. 0.3, "Test Methods for Electrical Wires and Cables", (FT6 Rating). |  | P/T Only | Yes | Construction Materials
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.5.21.(1) | 3.1.5.21. Wires in Computer Room Floors | Optical fibre cables and electrical wires and cables with combustible insulation, jackets or sheathes, located in the space below a raised floor in a computer room, are permitted in a building required to be of noncombustible construction provided they do not convey flame or continue to burn for more than 1 min when tested in conformance with the Vertical Flame Test in Clause 4.11.1. of CSA C22.2 No. 0.3, "Test Methods for Electrical Wires and Cables", (FT1 Rating). |  | P/T Only | Yes | Construction Materials
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.5.21.(2) | 3.1.5.21. Wires in Computer Room Floors | The requirement in Sentence (1) is considered to be met where the wires and cables, (a) exhibit a vertical char of not more than 1.5 m when tested in conformance with the Vertical Flame Test ‚¬ Cables in Cabletrough in Clause 4.11.4. of CSA C22.2 No. 0.3, "Test Methods for Electrical Wires and Cables", (FT4 Rating), or (b) exhibit a flame-spread of not more than 1.5 m, a smoke density of not more than 0.5 at peak optical density and a smoke density not more than 0.15 at average optical density when tested in conformance with the Flame and Smoke Test in the Appendix to CSA C22.2 No. 0.3, "Test Methods for Electrical Wires and Cables", (FT6 Rating). |  | P/T Only | Yes | Construction Materials
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.5.22.(1) | 3.1.5.22. Combustible Components in Public Pools and Public | Combustible fittings and components in a public pool or public spa, including main drains, piping, skimmers, return inlets, steps, ladder rungs and liners, are permitted in a building required to be of noncombustible construction. |  | P/T Only | Yes | Construction Materials
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.5.23.(1) | 3.1.5.23. Marquees Having Combustible Elements | Except as permitted in Sentence (2), exterior marquees, not greater than 7.5 m from ground level to the top of the marquee, having combustible elements, other than fabrics or films conforming to Sentence 3.1.16.1.(1), are permitted on a building required to be of noncombustible construction, provided every opening in the exposed wall of the building above the marquee is protected with wired glass in accordance with MMAH Supplementary Standard SB-2, “Fire Performance Ratings” where these openings are within (a) 4.5 m horizontally of the marquee, and (b) 9 m vertically above the marquee. |  | P/T Only | Yes | Construction Materials
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.5.23.(2) | 3.1.5.23. Marquees Having Combustible Elements | The protection required by Sentence (1) is permitted to be waived if the building is sprinklered. |  | P/T Only | Yes | Construction Materials
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.5.24.(1) | 3.1.5.24. Combustible Mezzanines | In a building required to be of noncombustible construction, a mezzanine located within a live/work unit is permitted to be of combustible construction, provided the area of the mezzanine is not more than 25% of the floor area of the live/work unit or 20 m2, whichever is less, and has no obstructions more than 1 070 mm above the floor. |  | P/T Only | Yes | Live/work Units
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.5.26.(1) | 3.1.5.26. Combustible Solar Collector Systems | A combustible solar collector system is permitted to be installed above the roof of a building required to be of noncombustible construction. |  | P/T Only | Yes | Construction Materials
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.5.5.(4) | 3.1.5.5. Combustible Components for Exterior Walls | The requirements of this Article do not apply where foamed plastic insulation is used in an exterior wall assembly of a building and the insulation is protected in conformance with Sentences 3.2.3.8.(1) and (2). |  | P/T Only | Yes | Construction Materials
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.8.10.(4) | 3.1.8.10. Twenty-Minute Closures | In elementary and secondary schools, a door assembly conforming to Articles 9.10.13.2. and 9.10.13.3. is permitted to be used as a closure in a fire separation having a fire-resistance rating of 30 min. |  | P/T Only | Yes | Fire Containment
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.8.18.(1) | 3.1.8.18. Sprinkler Protected Glazed Wall Assembly | A sprinkler protected glazed wall assembly shall be constructed in accordance with the requirements of ULC/ORD C263.1, "Sprinkler-Protected Windows Systems". |  | P/T Only | Yes | Fire Containment
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.8.18.(2) | 3.1.8.18. Sprinkler Protected Glazed Wall Assembly | A sprinkler protected glazed wall assembly shall not be installed in, (a) fire separations requiring a fire-resistance rating of more than two hours, (b) a firewall, (c) a high hazard industrial occupancy, or (d) any part of an exit serving, (i) a floor area subject to the requirements of Subsection 3.2.6., (ii) a care occupancy, (iii) a care and treatment occupancy, (iv) a detention occupancy, or (v) a residential occupancy. |  | P/T Only | Yes | Fire Containment
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.8.18.(3) | 3.1.8.18. Sprinkler Protected Glazed Wall Assembly | Where a sprinkler protected glazed wall assembly is installed in an exit fire separation permitted in Sentence (2), (a) the building shall be sprinklered, and (b) the exits protected with the sprinkler protected glazed wall assemblies shall not comprise more than one-half of the required number of exits from any floor area. |  | P/T Only | Yes | Fire Containment
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.8.8.(4) | 3.1.8.8. Fire Dampers Waived | In a Group B, Division 3 occupancy which contains sleeping accommodation for not more than 10 persons, which has not more than six occupants who require assistance in evacuation in case of an emergency and which is equipped with a fire alarm system, a duct need not be equipped with a fire damper at a fire separation, provided duct-type smoke detectors have been installed to control smoke circulation as described in Article 3.2.4.13. |  | P/T Only | Yes | Fire Containment
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.8.8.(3) | 3.1.8.8. Fire Dampers Waived | In elementary and secondary schools, a continuous noncombustible duct having a melting point above 760°C that pierces a fire separation having a fire-resistance rating of 30 min need not be equipped with a fire damper at the fire separation. |  | P/T Only | Yes | Fire Containment
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.9.4.(4) | 3.1.9.4. Combustible Piping Penetrations | Except as required by Sentence (7), combustible drain piping is permitted to penetrate a horizontal fire separation, provided it leads directly from a noncombustible water closet through a concrete floor slab and the piping is sealed at the penetration by a fire stop in conformance with Clause 3.1.9.1.(1)(a). |  | P/T Only | Yes | Construction Materials
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.9.4.(5) | 3.1.9.4. Combustible Piping Penetrations | Except as required by Sentence (7), combustible piping is permitted to penetrate a vertical or horizontal fire separation, provided the fire compartments on each side of the fire separation are sprinklered and the piping is sealed at the penetration by a fire stop in conformance with Clause 3.1.9.1.(1)(a). |  | P/T Only | Yes | Construction Materials
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.9.4.(6) | 3.1.9.4. Combustible Piping Penetrations | Except as required by Sentence (7), combustible piping not more than 25 mm in diameter containing chlorine gas is permitted to penetrate a fire separation between a chlorine gas service room built in conjunction with a public pool or public spa and the remainder of the building, provided the piping is sealed at the penetration by a fire stop in conformance with Clause 3.1.9.1.(1)(a). |  | P/T Only | Yes | Construction Materials
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.1.9.4.(7) | 3.1.9.4. Combustible Piping Penetrations | Where combustible piping penetrates a firewall or a horizontal fire separation described in Sentence 3.2.1.2.(1), the piping shall be sealed at the penetration by a fire stop that has an FT rating not less than the fire-resistance rating required for the firewall or horizontal fire separation when subjected to the fire test method in CAN/ULC-S115, "Fire Tests of Firestop Systems", and, (a) the fire stop shall have been tested with a pressure differential of 50 Pa between the exposed and unexposed sides, with the higher pressure on the exposed side, or the (b) fire compartments on each side of the firewall or horizontal fire separation shall be sprinklered. |  | P/T Only | Yes | Construction Materials
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.10.2.3.(1) | 3.10.2.3. Structural Fire Protection | Except as provided in Sentence (2) and Sentence 3.10.4.2.(1), the requirements in Subsections 3.2.1. and 3.2.2. shall apply. |  | P/T Only | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.10.2.4.(2) | 3.10.2.4. Safety Requirements Within Floor Areas | A corridor need not be constructed as a public corridor where the travel distance, measured from inside the rental space to the nearest exit, is not more than 15 m provided that the corridor walls, (a) are of noncombustible construction, (b) have no openings other than doors and the doors are of solid construction, and (c) are continuous from the floor to the underside of the floor above, the ceiling or the roof. |  | P/T Only | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.10.2.4.(8) | 3.10.2.4. Safety Requirements Within Floor Areas | Corridors shall be provided with, (a) natural lighting that shall be uniformly distributed and be at least 4% of the corridor area, or (b) emergency lighting, conforming to Sentences 3.2.7.4.(1) and (2), that shall provide average levels of illumination not less than 10 lx at floor level. |  | P/T Only | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.10.2.4.(7) | 3.10.2.4. Safety Requirements Within Floor Areas | Dead end corridors are not permitted. |  | P/T Only | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.10.2.4.(4) | 3.10.2.4. Safety Requirements Within Floor Areas | Egress doors from a rental space are not required to swing in the direction of exit travel or swing on a vertical axis provided, (a) the area of the rental space is not more than 50 m2, and (b) the distance of travel within the rental space is not more than 10 m. |  | P/T Only | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.10.2.4.(6) | 3.10.2.4. Safety Requirements Within Floor Areas | Where egress doors from a rental space open onto a corridor and do not swing in the direction of exit travel, the corridor shall be not less than 1 100 mm in width. |  | P/T Only | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.10.2.4.(5) | 3.10.2.4. Safety Requirements Within Floor Areas | Where egress doors from a rental space open onto a corridor and swing in the direction of exit travel, the corridor shall be not less than 1 500 mm wide, and the doors shall be not more than 914 mm wide. |  | P/T Only | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.10.2.4.(3) | 3.10.2.4. Safety Requirements Within Floor Areas | Where the building is sprinklered, doors in a public corridor do not require to be equipped with self-closing devices and latches provided that the travel distance is measured from inside the rental space to the nearest exit. |  | P/T Only | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.10.2.5.(1) | 3.10.2.5. Exit Requirements | Except as provided in Sentences (2) and (3), the requirements in Section 3.4. shall apply. |  | P/T Only | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.10.2.5.(3) | 3.10.2.5. Exit Requirements | Exit doors from rental spaces are not required to swing on a vertical axis provided, (a) the area of the rental space is not more than 50 m2, and (b) the travel distance within the rental space is not more than 10 m. |  | P/T Only | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.10.2.5.(2) | 3.10.2.5. Exit Requirements | The clear width of an exit stair shall be not less than 1 100 mm. |  | P/T Only | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.10.2.6.(1) | 3.10.2.6. Service Facilities | Except as provided in Sentence (2), the requirements in Section 3.6. shall apply. |  | P/T Only | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.10.2.6.(2) | 3.10.2.6. Service Facilities | Except where located in and serving only the dwelling units, a fuel-fired appliance shall be located in a service room separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h. |  | P/T Only | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.10.2.7.(1) | 3.10.2.7. Sanitary Facilities | Except as provided in Sentence (2), the requirements in Subsection 3.7.4. shall apply. |  | P/T Only | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.10.3.1.(1) | 3.10.3.1. Application | The requirements in this Subsection apply to all buildings except a 1 storey building that does not contain a basement or mezzanine. |  | P/T Only | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.10.3.2.(1) | 3.10.3.2. Spatial Separations | Except as provided in Sentence (2), the requirements in Subsection 3.2.3. shall apply. |  | P/T Only | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.10.3.2.(2) | 3.10.3.2. Spatial Separations | The distance between buildings shall be not less than 9 m. |  | P/T Only | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.10.3.3.(2) | 3.10.3.3. Fire Alarm Systems | A fire alarm system shall be installed. |  | P/T Only | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.10.3.3.(1) | 3.10.3.3. Fire Alarm Systems | Except as provided in Sentences (2) and (3), the requirements in Subsection 3.2.4. shall apply. |  | P/T Only | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.10.3.3.(3) | 3.10.3.3. Fire Alarm Systems | Within the first storey, manual pull stations are required only in corridors. |  | P/T Only | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.10.3.4.(2) | 3.10.3.4. Provisions for Firefighting | Access routes for fire department vehicles shall be provided and shall be not less than 9 m wide. |  | P/T Only | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.10.3.4.(1) | 3.10.3.4. Provisions for Firefighting | Except as provided in Sentences (2) and (3), the requirements in Subsection 3.2.5. shall apply. |  | P/T Only | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.10.3.4.(3) | 3.10.3.4. Provisions for Firefighting | Hydrants shall be located in the access routes required in Sentence (2) so that, for a building provided with a fire department connection for a standpipe system or a sprinkler system, a fire department pumper vehicle can be located adjacent to a hydrant, and the unobstructed path of travel for the firefighter from the vehicle to the fire department connection is not more than 45 m, and for a building that is not sprinklered, a fire department pumper vehicle can be located in the access route so that the unobstructed path of travel for the firefighter is not more than, 45 m from the hydrant to the vehicle, and 45 m from the vehicle to every opening in the building. |  | P/T Only | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.10.3.5.(1) | 3.10.3.5. Standpipe Systems | Except as provided in Sentence (2), the requirements in Subsection 3.2.9. shall apply. |  | P/T Only | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.10.3.5.(2) | 3.10.3.5. Standpipe Systems | Hose stations are not required in the first storey. |  | P/T Only | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.10.4.3.(2) | 3.10.4.3. Spatial Separations | Where the building area conforms to Clause 3.10.4.2.(1)(b), the limiting distance requirements shall not apply between individual buildings. |  | P/T Only | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.10.4.4.(1) | 3.10.4.4. Fire Alarm Systems | Except as provided in Sentence (2), the requirements in Subsection 3.2.4. shall not apply. |  | P/T Only | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.10.4.4.(2) | 3.10.4.4. Fire Alarm Systems | The requirements for smoke alarms in Article 3.2.4.22. shall apply to a dwelling unit. |  | P/T Only | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.10.4.5.(2) | 3.10.4.5. Provisions for Firefighting | Access routes for fire department vehicles shall be provided and shall be not less than 9 m wide. |  | P/T Only | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.10.4.5.(5) | 3.10.4.5. Provisions for Firefighting | An adequate water supply for firefighting shall be provided for every building. |  | P/T Only | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.10.4.5.(1) | 3.10.4.5. Provisions for Firefighting | Except as provided in Sentences (2) to (7), the requirements in Subsection 3.2.5. shall not apply. |  | P/T Only | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.10.4.5.(3) | 3.10.4.5. Provisions for Firefighting | Hydrants shall be located in the access routes required in Sentence (2) so that the locations conform to Sentence 3.10.3.4.(3). |  | P/T Only | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.10.4.5.(4) | 3.10.4.5. Provisions for Firefighting | The access routes required in Sentence (2) shall conform to the requirements in Sentence 3.2.5.6.(1). |  | P/T Only | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.10.4.5.(6) | 3.10.4.5. Provisions for Firefighting | Where a sprinkler system is installed, the system shall conform to the requirements in Articles 3.2.5.13., 3.2.5.16. and 3.2.5.18. |  | P/T Only | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.10.4.5.(7) | 3.10.4.5. Provisions for Firefighting | Where combustible sprinkler piping is installed, it shall conform to the requirements in Article 3.2.5.14. |  | P/T Only | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.14.1.1.(1) | 3.14.1.1. Application | Except as provided in this Subsection, tents are exempted from complying with the requirements of this Division. |  | P/T Only | Yes | Tents and Air-Supported Structures
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.14.1.2.(2) | 3.14.1.2. General | Articles 3.14.1.3., 3.14.1.7. and 3.14.1.8. do not apply to tents that, (a) do not exceed 225 m2 in ground area, (b) do not exceed 225 m2 in aggregate ground area and are closer than 3 m apart, (c) do not contain bleachers, and (d) are not enclosed with sidewalls. |  | P/T Only | Yes | Tents and Air-Supported Structures
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.14.1.2.(1) | 3.14.1.2. General | Except as provided in Sentence (2), the requirements of this Subsection shall apply to all tents. |  | P/T Only | Yes | Tents and Air-Supported Structures
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.14.1.3.(2) | 3.14.1.3. Means of Egress | A tent need not conform to Article 3.4.6.12. except where swing type doors are provided. |  | P/T Only | Yes | Tents and Air-Supported Structures
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.14.1.3.(3) | 3.14.1.3. Means of Egress | Where the area between adjacent tents or a tent and the property line is used as a means of egress, the minimum width between stake lines shall be the width necessary for means of egress, but not less than 3 m. |  | P/T Only | Yes | Tents and Air-Supported Structures
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.14.1.4.(3) | 3.14.1.4. Clearance to Other Structures | A walkway between a building and (a) a tent occupied by the public is permitted provided, the tent is not closer than 3 m from the building, and (b) the walkway conforms to Article 3.2.3.19. |  | P/T Only | Yes | Tents and Air-Supported Structures
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.14.1.4.(1) | 3.14.1.4. Clearance to Other Structures | Tents shall not be erected closer than 3 m to the property line. |  | P/T Only | Yes | Tents and Air-Supported Structures
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.14.1.7.(1) | 3.14.1.7.(1) | Where bleachers are provided in tents, they shall be designed in conformance with Articles 3.3.2.8., 3.3.2.10. and Subsection 4.1.5. |  | P/T Only | Yes | Tents and Air-Supported Structures
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.14.1.8.(2) | 3.14.1.8. Sanitary Facilities | Article 3.7.4.17. applies to sanitary facilities in Sentence (1). |  | P/T Only | Yes | Tents and Air-Supported Structures
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.14.1.8.(1) | 3.14.1.8. Sanitary Facilities | Except as provided in Sentence (3), the minimum number of water closets for tents shall be determined in accordance with Table 3.7.4.3.E. |  | P/T Only | Yes | Tents and Air-Supported Structures
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.14.1.8.(3) | 3.14.1.8. Sanitary Facilities | Sanitary privies, chemical closets or other means for the disposal of human waste may be provided in lieu of toilet fixtures. |  | P/T Only | Yes | Tents and Air-Supported Structures
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.14.1.9.(1) | 3.14.1.9. Provision for Firefighting | Access shall be provided to all tents for the purpose of firefighting. |  | P/T Only | Yes | Tents and Air-Supported Structures
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.14.2.1.(1) | 3.14.2.1. Application | Except as provided in this Subsection, the requirements of this Division apply to air-supported structures. |  | P/T Only | Yes | Tents and Air-Supported Structures
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.14.2.2.(3) | 3.14.2.2. General | Except as provided in Sentence (5), air-supported structures are exempt from complying with Articles 3.2.2.20. to 3.2.2.83., except for maximum building size. |  | P/T Only | Yes | Tents and Air-Supported Structures
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.14.2.2.(2) | 3.14.2.2. General | Except where no fire separation is required between major occupancies, air-supported structures shall contain not more than one major occupancy. |  | P/T Only | Yes | Tents and Air-Supported Structures
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.14.2.2.(5) | 3.14.2.2. General | Interior construction contained within air-supported structures must meet the construction requirements of Articles 3.2.2.20. to 3.2.2.83. |  | P/T Only | Yes | Tents and Air-Supported Structures
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.14.2.3.(4) | 3.14.2.3. Spatial Separation | An air-supported structure is permitted to be attached to another building provided the building to which it is attached, (a) has a building area not more than 200 m2, (b) conforms to the requirements of other Parts of the Code based on the building area of the attached building, and (c) is sprinklered or separated from the air-supported structure by a fire separation having a fire-resistance rating of not less than 1 h. |  | P/T Only | Yes | Tents and Air-Supported Structures
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.14.2.3.(3) | 3.14.2.3. Spatial Separation | Except as provided in Sentence (4), an air-supported structure is permitted to be attached to another building provided the building to which it is attached, conforms to the requirements of other Parts of this Division based on the total building areas of the air-supported structure and the attached building, is sprinklered, and is separated from the air-supported structure by a fire separation having a fire-resistance rating of not less than 1 h. |  | P/T Only | Yes | Tents and Air-Supported Structures
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.14.2.5.(2) | 3.14.2.5. Flame Resistance | Materials for fabrics used in connection with air-supported structures are exempt from compliance with the requirements for flame-spread ratings for interior finishes in Subsection 3.1.13. |  | P/T Only | Yes | Tents and Air-Supported Structures
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.1.1.(7) | 3.2.1.1. Exceptions in Determining Building Height | Mezzanines, elevated walkways and platforms that are intended to be occupied in Group F, Division 2 or 3 major occupancies need not be considered as storeys in calculating building height provided, the building is of noncombustible construction, and the occupant load is not more than four persons. |  | P/T Only | Yes | Fire Containment
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.2.17.(2) | 3.2.2.17. Sprinklers in Lieu of Roof Rating | The fire-resistance rating of roof assemblies required by Clause 3.2.2.43A.(2)(b) or 3.2.2.50A.(2)(b) is not permitted to be waived. |  | P/T Only | Yes | Fire Containment
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.2.17.(1) | 3.2.2.17. Sprinklers in Lieu of Roof Rating | The requirements in Articles 3.2.2.20. to 3.2.2.83. for roof assemblies to have a fire-resistance rating are permitted to be waived provided, (a) except as provided by Sentence (2), the building is sprinklered, (b) the sprinkler system in Clause (a) is electrically supervised in conformance with Sentence 3.2.4.10.(3), and (c) the operation of the sprinkler system in Clause (a) will cause a signal to be transmitted to the fire department in conformance with Sentence 3.2.4.8.(4). |  | P/T Only | Yes | Fire Containment
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.2.29.(3) | 3.2.2.29. Group A, Division 3, Any Height, Any Area | If intended for occasional use for trade shows and similar exhibition purposes, the building referred to in Sentence (1) that is more than 1 500 m2 in building area shall be sprinklered. |  | P/T Only | Yes | Fire Containment
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.2.44.(4) | 3.2.2.44. Group C, up to 4 Storeys, Noncombustible Construction | The dwelling units described in Subclause (1)(a)(ii) shall be separated by continuous vertical fire separations that extend through all storeys and service spaces of the separated portions. |  | P/T Only | Yes | Fire Containment
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.2.48.(2) | 3.2.2.48A. Group C, Retirement Home, Any Height, Any Area, | Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and, (a) except as permitted by Sentence 3.2.2.7.(1), the building shall be sprinklered, (b) floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h, (c) mezzanines shall have a fire-resistance rating not less than 1 h, and (d) loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | P/T Only | Yes | Retirement Homes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.2.48.(1) | 3.2.2.48A. Group C, Retirement Home, Any Height, Any Area, | Except as permitted by Articles 3.2.2.48B. to 3.2.2.48E., a retirement home shall conform to Sentence (2). |  | P/T Only | Yes | Retirement Homes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.2.48.(1) | 3.2.2.48B. Group C, Retirement Home, up to 4 Storeys, Sprinklered, | A retirement home is permitted to conform to Sentence (2) provided, (a) except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered, (b) it is not more than 4 storeys in building height, and (c) it has a building area not more than, (i) 12 000 m2 if 1 storey in building height, (ii) 6 000 m2 if 2 storeys in building height, (iii) 4 000 m2 if 3 storeys in building height, or (iv) 3 000 m2 if 4 storeys in building height. |  | P/T Only | Yes | Retirement Homes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.2.48.(2) | 3.2.2.48B. Group C, Retirement Home, up to 4 Storeys, Sprinklered, | The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and, (a) floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h, (b) mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 1 h, and (c) loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | P/T Only | Yes | Retirement Homes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.2.48.(1) | 3.2.2.48C. Group C, Retirement Home, up to 4 Storeys, Sprinklered | A retirement home is permitted to conform to Sentence (2) provided, (a) except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered, (b) it is not more than 4 storeys in building height, and (c) it has a building area not more than, (i) 6 600 m2 if 1 storey in building height, (ii) 3 300 m2 if 2 storeys in building height, (iii) 2 200 m2 if 3 storeys in building height, or (iv) 1 650 m2 if 4 storeys in building height. |  | P/T Only | Yes | Retirement Homes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.2.48.(2) | 3.2.2.48C. Group C, Retirement Home, up to 4 Storeys, Sprinklered | The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and, (a) floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, (b) mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 1 h, and (c) loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | P/T Only | Yes | Retirement Homes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.2.48.(1) | 3.2.2.48D. Group C, Retirement Home, up to 3 Storeys, Sprinklered, | A retirement home is permitted to conform to Sentence (2) provided, (a) except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered, (b) it is not more than 3 storeys in building height, and (c) it has a building area that is, (i) not limited if the building is not more than 1 storey in building height, (ii) not more than 12 000 m2 if 2 storeys in building height, or (iii) not more than 8 000 m2 if 3 storeys in building height. |  | P/T Only | Yes | Retirement Homes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.2.48.(2) | 3.2.2.48D. Group C, Retirement Home, up to 3 Storeys, Sprinklered, | Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) is permitted to be of noncombustible construction, and, (a) floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, (b) mezzanines shall have a fire-resistance rating not less than 1 h, and (c) loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | P/T Only | Yes | Retirement Homes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.2.48.(1) | 3.2.2.48E. Group C, Retirement Home, up to 3 Storeys, Sprinklered, | A retirement home is permitted to conform to Sentence (2) provided, (a) except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered, (b) it is not more than 3 storeys in building height, and (c) it has a building area not more than, (i) 4 800 m2 if 1 storey in building height, (ii) 2 400 m2 if 2 storeys in building height, or (iii) 1 600 m2 if 3 storeys in building height. |  | P/T Only | Yes | Retirement Homes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.2.48.(2) | 3.2.2.48E. Group C, Retirement Home, up to 3 Storeys, Sprinklered, | The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and, (a) floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min, (b) mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, and (c) loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | P/T Only | Yes | Retirement Homes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.2.5.(2) | 3.2.2.5. Applicable Building Height and Area | For the purposes of Sentence (1), a retirement home is deemed to be a separate major occupancy. |  | P/T Only | Yes | Retirement Homes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.2.6.(2) | 3.2.2.6. Multiple Major Occupancies | For the purposes of Sentence (1), a retirement home is deemed to be a separate major occupancy. |  | P/T Only | Yes | Retirement Homes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.2.68.(2) | 3.2.2.68. Group F, Division 2, up to 6 Storeys | (2) Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and, (a) floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h, (b) mezzanines shall have a fire-resistance rating not less than 1 h, (c) if the building is not sprinklered, roof assemblies shall have a fire-resistance rating not less than 1 h, and (d) loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. |  | P/T Only | Yes | Fire Containment
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.2.68.(1) | 3.2.2.68. Group F, Division 2, up to 6 Storeys | A building classified as Group F, Division 2 is permitted to conform to Sentence (2) provided, (a) it is not more than 6 storeys in building height, and (b) it has a building area not more than the value in Table 3.2.2.68.A. or Table 3.2.2.68.B. |  | P/T Only | Yes | Fire Containment
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.2.7.(3) | 3.2.2.7. Superimposed Major Occupancies | For the purposes of Sentences (1) and (2), a retirement home is deemed to be a separate major occupancy. |  | P/T Only | Yes | Retirement Homes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.2.8.(2) | 3.2.2.8. Exceptions for Major Occupancies | A helicopter landing area on the roof of a building need not be considered a major occupancy for purposes of Subsection 3.2.2. where such landing area is not more than 10% of the area of the roof |  | P/T Only | Yes | Fire Containment
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.2.8.(1) | 3.2.2.8. Exceptions for Major Occupancies | For the purposes of Sentence (1), a retirement home is deemed to be a separate major occupancy. |  | P/T Only | Yes | Retirement Homes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.3.1.(11) | 3.2.3.1. Limiting Distance and Area of Unprotected Openings | The required limiting distance for an exposing building face is permitted to be measured to a point beyond the property line that is not the centre line of a street, lane or public thoroughfare if, (a) the owners of the properties on which the limiting distance is measured and the municipality enter into an agreement in which such owners agree that, (i) each owner covenants that, for the benefit of land owned by the other covenantors, the owner will not construct a building on his or her property unless the limiting distance for exposing building faces in respect of the proposed construction is measured in accordance with the agreement, (ii) the covenants contained in the agreement are intended to run with the lands, and the agreement shall be binding on the parties and their respective heirs, executors, administrators, successors and assigns, (iii) the agreement shall not be amended or deleted from title without the consent of the municipality, and (iv) they will comply with such other conditions as the municipality considers necessary, including indemnification of the municipality by the other parties, and (b) the agreement referred to in Clause (a) is registered against the title of the properties to which it applies. |  | P/T Only | Yes | Fire Containment
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.3.1.(12) | 3.2.3.1. Limiting Distance and Area of Unprotected Openings | Where an agreement referred to in Sentence (11) is registered against the title of a property, the limiting distance for exposing building faces shall be measured to the point referred to in the agreement. |  | P/T Only | Yes | Fire Containment
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.3.16.(2) | 3.2.3.16. Protection of Soffits | Where an attic or roof space, including its adjoining eave overhangs, is separated by construction conforming to Article 3.1.11.7. into compartments such that the resulting spaces are not common to more than two suites of residential occupancy or more than two patients’ or residents’ sleeping rooms in a Group B, Division 2 or 3 occupancy, the requirements in Sentence (1) do not apply. |  | P/T Only | Yes | Fire containment
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.3.7.(7) | 3.2.3.7. Construction of Exposing Building Face | A wall assembly described in Sentence (6) that includes combustible cladding of fire-retardant treated wood shall be tested for fire exposure after the cladding has been conditioned in conformance with ASTM D2898, "Accelerated Weathering of Fire-Retardant-Treated Wood for Fire Testing". |  | P/T Only | Yes | Mid-rise Wood
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.4.10.(5) | 3.2.4.10. Electrical Supervision | If a fire alarm system is required in a building, electrical supervision shall be provided to indicate, on the fire alarm system annunciator, a loss of power to a heat tracing cable that is installed to heat, a standpipe riser, a sprinkler line as part of a fire suppression system, or an exit or means of egress to keep it free of ice and snow. |  | P/T Only | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.4.12.(2) | 3.2.4.12. Smoke and Heat Detectors | Except as provided in Article 3.2.4.16., if a fire alarm system is required, heat detectors shall be installed in, every room in portions of buildings classified as Group A, Division 1, except in a hotel, in every suite, and every room not located within a suite, in portions of buildings classified as Group C major occupancy and more than 3 storeys in building height, and in a floor area containing a hotel, in every room in a suite and in every room not located in a suite other than washrooms within a suite, saunas, refrigerated areas and swimming pools. |  | P/T Only | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.4.18.(6) | 3.2.4.18. Manual Pull Stations | Except as permitted by Sentence (3), in Group C apartment buildings other than retirement homes, if a pull station is not installed on a floor area in accordance with Sentence (1) or (4), (a) a manual pull station shall be installed in every dwelling unit in the floor area near each egress door leading from the dwelling unit, (b) smoke detectors shall be installed in the floor area in public corridors and stairwells, and (c) fire detectors shall be installed in the floor area in all common public areas and in rooms not located within dwelling units. |  | P/T Only | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.4.18.(5) | 3.2.4.18. Manual Pull Stations | In a building containing a hotel, a manual pull station shall be installed in the main reception area serving the hotel. |  | P/T Only | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.4.18.(7) | 3.2.4.18. Manual Pull Stations | In floor areas where the manual pull stations are located in dwelling units, a legible sign stating FIRE ALARM PULL STATIONS LOCATED IN APARTMENT UNITS shall be posted near every exit in a public corridor. |  | P/T Only | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.4.18.(8) | 3.2.4.18. Manual Pull Stations | Key switch activated pull stations are permitted in an impeded egress zone and a contained use area in Group B, Division 1 and 2 occupancies. |  | P/T Only | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.4.19.(5) | 3.2.4.19. Alert and Alarm Signals | Visual signal devices are permitted to be installed in lieu of audible signal devices in the compartments referred to in Article 3.3.3.6. |  | P/T Only | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.4.19.(6) | 3.2.4.19. Alert and Alarm Signals | Visual signal devices required by Clauses (4)(b) and (c) are not required in, (a) a classroom, and (b) a Group B, Division 3 occupancy that contains sleeping accommodation for not more than 10 persons and not more than six occupants require assistance in evacuation in case of an emergency. |  | P/T Only | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.4.21.(2) | 3.2.4.21. Visual Signals | Visual signal devices permitted by Sentence 3.2.4.19.(5) shall be installed so that the signal from at least one device is visible throughout the compartment in which they are installed. (See Appendix A.) |  | P/T Only | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.4.22.(13) | 3.2.4.22. Smoke Alarms | Smoke alarms required by Sentence (1) shall have a visual signalling component conforming to the requirements in 18.5.3. (Light, Color and Pulse Characteristics) of NFPA 72, “National Fire Alarm and Signaling Code”. |  | P/T Only | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.4.22.(15) | 3.2.4.22. Smoke Alarms | The luminous intensity for visual signalling components required by Sentence (13) that are installed in sleeping rooms shall be a minimum of 175 cd. |  | P/T Only | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.4.22.(14) | 3.2.4.22. Smoke Alarms | The visual signalling component required by Sentence (13) need not, (a) be integrated with the smoke alarm provided it is interconnected to it, (b) be on battery backup, or (c) have synchronized flash rates, when installed in a dwelling unit. |  | P/T Only | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.4.7.(3) | 3.2.4.7. Silencing of Alarm Signals | Except as provided by Clause 3.2.4.23.(3)(a), in a care and treatment occupancy an alert signal is permitted to be silenced automatically after 1 min. |  | P/T Only | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.4.9.(8) | 3.2.4.9. Annunciator and Zone Indication | In a building containing a hotel in which a trouble signal sounding device has a silencing switch, a trouble light shall be installed in, the main reception area serving the hotel, or another continually-supervised location. |  | P/T Only | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.4.9.(9) | 3.2.4.9. Annunciator and Zone Indication | In a long-term care home, a remote audiovisual fire alarm trouble signal shall be located at the main nursing station. |  | P/T Only | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.5.13.(9) | 3.2.5.13. Automatic Sprinkler Systems | The sprinkler system described in Sentence (3) shall be provided with a minimum 20 min water supply when installed in a retirement home. |  | P/T Only | Yes | Fire Suppression
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.5.15.(4) | 3.2.5.15. Sprinklered Service Space | If a building is sprinklered, sprinkler protection need not be provided in the space below a raised floor in a computer room, if the optical fibre cables and electrical wires and cables in this space conform to the test requirements in Article 3.1.5.21., if the building is of noncombustible construction and other combustible components are limited to those permitted in Subsection 3.1.5., if this space is used to circulate conditioned air and the air handling system is designed to prevent the circulation of smoke upon a signal from a smoke detector, if all of this space is easily accessible by providing access sections or panels in the raised floor, and if the computer room is more than 2 000 m2 and the annunciator has separate zone indicators of the actuation of smoke detectors located in this space so that the coverage for each zone is not more than 2 000 m2. |  | P/T Only | Yes | Fire Suppression
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.5.15.(5) | 3.2.5.15. Sprinklered Service Space | Where a room, chute or bin is required to be sprinklered as indicated in Sentence 3.3.4.3.(1), Article 3.6.2.5. and Sentence 3.6.3.3.(6), the sprinklers may be supplied with water from the fire standpipe system provided that, except for a chute, not more than eight sprinklers are required to protect any room or bin based on a maximum coverage of 12 m2 per sprinkler, the standpipe riser is, not less than 6 in. in diameter, or hydraulically designed to meet combined water supply as specified in Clause (c), the water supply for a standpipe system, pumping capability and water storage facility, if required, is increased to supply 95 L/min for each sprinkler over and above the requirements for the standpipe system up to maximum 760 L/min for sprinklers, a waterflow detecting device shall be installed in the sprinkler main adjacent to the point of connection to the standpipe riser, and the activation of each waterflow detecting device in Clause (d) shall be indicated separately on the fire alarm system annunciator. |  | P/T Only | Yes | Fire Suppression
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.5.16.(3) | 3.2.5.16. Fire Department Connections | The fire department connections required in Sentences (1) and (2) shall be, located on the outside of a building adjacent to a street or an access route, not less than 300 mm and not more than 900 mm above ground level, and provided with two 65 mm hose connections with female swivel hose couplings. |  | P/T Only | Yes | Fire Suppression
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.5.3.(2) | 3.2.5.3. Roof Access | Clearance and access around roof signs or other obstructions shall provide, (a) a passage not less than 900 mm wide by 1 800 mm high, clear of all obstructions except for necessary horizontal supports not more than 600 mm above the roof surface, (i) around every roof sign, and (ii) through every roof sign at locations not more than 15 m apart, and (b) a clearance of not less than 1 200 mm between any portion of a roof sign and any opening in the exterior wall face or roof of the building in which it is erected. |  | P/T Only | Yes | Emergency Response
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.5.7.(2) | 3.2.5.7. Water Supply (See Appendix A.) | Hydrants shall be located within 90 m horizontally of any portion of a building perimeter that is required to face a street in Subsection 3.2.2. |  | P/T Only | Yes | Fire Suppression
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.6.2.(6) | 3.2.6.2. Limits to Smoke Movement | A building that is not sprinklered shall be designed in accordance with MMAH Supplementary Standard SB-4, "Measures for Fire Safety in High Buildings", to limit the danger to occupants and firefighters from exposure to smoke in a building fire. |  | P/T Only | Yes | High Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.6.4.(5) | 3.2.6.4. Emergency Operation of Elevators | In a building that is not sprinklered, automatic emergency recall operation shall be provided for all elevators serving storeys above the first storey. |  | P/T Only | Yes | High Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.6.4.(7) | 3.2.6.4. Emergency Operation of Elevators | Smoke detectors in Sentence (6) shall be designed as part of the building fire alarm system. |  | P/T Only | Yes | High Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.6.4.(6) | 3.2.6.4. Emergency Operation of Elevators | The automatic emergency recall feature in Sentence (5) shall be actuated by, smoke detectors installed in each elevator lobby on each storey, or (See Appendix A.) the building fire alarm system. |  | P/T Only | Yes | High Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.6.6.(5) | 3.2.6.6. Venting to Aid Firefighting | In a building that is not sprinklered, venting of floor areas required in Sentence (1) shall not be provided by the building exhaust system. |  | P/T Only | Yes | High Buildings
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.7.1.(5) | 3.2.7.1. Minimum Lighting Requirements | Elevator machine rooms shall be equipped to provide illumination to an average level of not less than 100 lx at floor level. |  | P/T Only | Yes | Falling, Tripping, Slipping Protection
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.7.1.(7) | 3.2.7.1. Minimum Lighting Requirements | Every area where food is intended to be processed, prepared or manufactured and where equipment or utensils are intended to be cleaned shall be equipped to provide illumination to a level of not less than 500 lx measured at the floor level. |  | P/T Only | Yes | Falling, Tripping, Slipping Protection
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.7.1.(6) | 3.2.7.1. Minimum Lighting Requirements | Every place of assembly intended for the viewing of motion pictures or the performing arts, shall be equipped to provide an average level of illumination at floor level in the aisles of not less than 2 lx during the viewing. |  | P/T Only | Yes | Falling, Tripping, Slipping Protection
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.7.1.(8) | 3.2.7.1. Minimum Lighting Requirements | Every storage room, dressing room, sanitary facility, service area and corridor serving the areas in Sentence (7) shall be equipped to provide illumination to a level of not less than 300 lx measured at the floor level. |  | P/T Only | Yes | Falling, Tripping, Slipping Protection
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.7.5.(2) | 3.2.7.5. Emergency Power Supply Installation | Every emergency power supply shall be equipped with an emergency audible and visual trouble indication. |  | P/T Only | Yes | Emergency Power
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.7.7.(2) | 3.2.7.7. Fuel Supply Shut-Off Valves and Exhaust Pipes | Where pipes for exhaust gases from emergency power systems penetrate required fire separations, they shall be enclosed in a separate service space having a fire-resistance rating equal to that of the penetrated floor assembly, but not less than 45 min. |  | P/T Only | Yes | Emergency Power
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.7.9.(4) | 3.2.7.9. Emergency Power for Building Services | Except as provided by Sentence (5), an emergency power supply capable of operating under a full load for not less than 30 min shall be provided by emergency generator for water supply for firefighting in conformance with Article 3.2.5.7., if the supply is dependent on electrical power supplied to the building, and the building is not within the scope of Subsection 3.2.6. |  | P/T Only | Yes | Emergency Response
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.7.9.(5) | 3.2.7.9. Emergency Power for Building Services | Sentence (4) does not apply to the water supply for a standpipe system. |  | P/T Only | Yes | Emergency Response
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.8.1.(5) | 3.2.8.1. Application | An interconnected floor space is permitted in an elementary or secondary school provided, (a) the interconnected floor space consists of the first storey, and the storey next above or below it, but not both, (b) the interconnected floor space is sprinklered, (c) the portions of the upper floor area that do not terminate at an exterior wall, a firewall or a vertical shaft shall terminate at a vertical fire separation extending from the floor assembly to the underside of the floor or roof assembly above, (d) except as provided in Clause (e), the fire separation required in Clause (c) need not have a fire-resistance rating, (e) where a corridor is located immediately adjacent to the fire separation required in Clause (c), the fire separation shall have a fire-resistance rating of not less than 30 min, and (f) where a portion of a floor area is not within the interconnected floor space, the required access to exit from this portion of the floor area shall not lead through the interconnected floor space. |  | P/T Only | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.8.1.(4) | 3.2.8.1. Application | Except as permitted in Sentence (5), an elementary or secondary school shall not, (a) contain an interconnected floor space, or (b) be located in an interconnected floor space. |  | P/T Only | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.8.3.(1) | 3.2.8.3. Configuration | In buildings constructed in conformance with Articles 3.2.8.4. to 3.2.8.11., the unprotected openings through floor assemblies in an interconnected floor space shall be of sufficient size and shall be positioned relative to each other so as to be capable of containing, within the full height of the interconnected floor space, a cylinder conforming to Sentence (2). |  | P/T Only | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.8.3.(2) | 3.2.8.3. Configuration | The cylinder referred to in Sentence (1) shall have a cross-section that, where taken at a right angle to the longitudinal axis of such cylinder, is, a circle at least 9 m in diameter, or an ellipse at least 7 m wide along the minor axis and at least 65 m2 in area. (See Appendix A.) |  | P/T Only | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.8.4.(4) | 3.2.8.4. Exits | Except where exits serving the floor area are at ground level, the increased travel distance to exits permitted by Clause 3.4.2.5.(1)(c) shall not apply to a floor area within an interconnected floor space. |  | P/T Only | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.8.4.(7) | 3.2.8.4. Exits | The requirements of Sentence (6) need not be applied where a floor area that is a portion of an interconnected floor space and that has a floor level more than 18 m above grade is separated from the remainder of the interconnected floor space by a fire separation having a fire-resistance rating of at least 1 h, except that no fire-resistance rating is required for such fire separation where all of the major occupancies contained within the interconnected floor space may be classified as light hazard occupancies in conformance with Appendix A of NFPA 13 “Installation of Sprinkler Systems”. |  | P/T Only | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.8.4.(2) | 3.2.8.4. Exits | Where a building containing an interconnected floor space is more than 75 m in height, measured between grade and the floor level of the top storey, the exit stairshaft protection required in Sentence (1) shall be accomplished by the provision, between each floor area and each exit stairshaft, of a vestibule provided with a mechanical air supply or with a vent opening to the outdoors. |  | P/T Only | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.8.6.(1) | 3.2.8.6. Group B Sleeping Rooms | Openings provided for access between an interconnected floor space and a building or a portion of a building containing Group B major occupancy sleeping rooms shall be provided with vestibules that are provided with a mechanical air supply and that are designed, to restrict the passage of smoke from the interconnected floor space into the area containing sleeping rooms in accordance with the limits described in Sentence 3.2.8.4.(1), and in conformance with Clause 3.2.8.4.(3)(a). |  | P/T Only | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.8.7.(2) | 3.2.8.7. Sprinklers | In a building containing an interconnected floor space, (a) waterflow alarm signals from sprinkler systems shall be transmitted to the fire department in conformance with Sentence 3.2.4.8.(4), and (b) sprinkler systems shall be electrically supervised as required by Sentence 3.2.4.10.(3). |  | P/T Only | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.8.9.(4) | 3.2.8.9. Smoke Control | A building containing an interconnected floor space may be designed so that, in the event of a fire arising in a floor area or part of a floor area within the interconnected floor space, automatic detection of such fire will activate air handling equipment that, extracts air directly from such floor area or part of a floor area at the rate of at least six air changes per hour, and supplies air in sufficient quantities and at appropriate locations to prevent smoke from passing out of such floor area into other portions of the interconnected floor space. |  | P/T Only | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.8.9.(7) | 3.2.8.9. Smoke Control | Except where zoned mechanical exhaust described in Sentence (4) has been activated, upon automatic detection of smoke within the volume of the interconnected floor space, the mechanical exhaust described in Sentence (6) shall be automatically activated and supply air shall be provided in sufficient quantity and at appropriate locations to allow a consistent rate of removal of smoke throughout the volume of the interconnected floor space. |  | P/T Only | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.8.9.(5) | 3.2.8.9. Smoke Control | For purposes of Sentences (6) and (7), the volume of an interconnected floor space need not include the aggregate volume of those floor areas or portions of floor areas designed to have zoned air extraction in accordance with Sentence (4). |  | P/T Only | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.8.9.(2) | 3.2.8.9. Smoke Control | The design of the smoke control system shall assume an outdoor temperature equal to the January design temperature on a 2.5% basis. |  | P/T Only | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.8.9.(3) | 3.2.8.9. Smoke Control | Upon activation of the sprinkler system or automatic detection of smoke by at least two smoke detectors in a single zone within an interconnected floor space, the system shall, stop air moving fans that provide for the normal exhausting or re-circulating of air in an interconnected floor space, activate exit stairshaft protection required in Article 3.2.8.4., activate elevator protection required in Article 3.2.8.5., and activate the vestibule air supply required in Sentence 3.2.8.6.(1). |  | P/T Only | Yes | Interconnected Floor Space
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.9.1.(7) | 3.2.9.1. Where Required | A standpipe system is not required to be installed in a dwelling unit that, extends not more than 3 storeys above adjacent ground level, is completely cut off from the remainder of the building so that there is no access to the remainder of the building, and has direct access to its interior by means of an exterior doorway located not more than 1 500 mm above or below adjacent finished ground level. |  | P/T Only | Yes | Fire Suppression
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.9.1.(5) | 3.2.9.1. Where Required | A standpipe system is not required to be installed in a rooftop enclosure if this enclosure has an area not more than 50 m2. |  | P/T Only | Yes | Fire Suppression
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.9.1.(4) | 3.2.9.1. Where Required | A standpipe system is not required to be installed in the lowest storey in a building if this storey is a service room that has an area not more than 50 m2. |  | P/T Only | Yes | Fire Suppression
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.9.1.(3) | 3.2.9.1. Where Required | A standpipe system shall be installed in every basement of a building that is regulated by Sentence 3.2.2.15.(2). |  | P/T Only | Yes | Fire Suppression
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.9.1.(2) | 3.2.9.1. Where Required | A standpipe system shall be installed in every basement of a building that requires a standpipe system above grade. |  | P/T Only | Yes | Fire Suppression
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.9.2.(9) | 3.2.9.2. Standpipe System Design | A standpipe riser shall be located in, an exit stair shaft, or a vertical service space separated from the adjacent floor area by a fire separation having a fire-resistance rating conforming to Table 3.6.3.1. |  | P/T Only | Yes | Fire Suppression
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.9.2.(7) | 3.2.9.2. Standpipe System Design | Couplings for hoses or other fittings used in connection with such couplings shall conform to ULC-S513, “Threaded Couplings for 38 mm and 65 mm Fire Hose” or CAN/ULC-S543, “Internal Lug Quick Connect Couplings for Fire Hose”. |  | P/T Only | Yes | Fire Suppression
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.9.2.(8) | 3.2.9.2. Standpipe System Design | If freezing of piping may occur, a dry standpipe system may be provided and so arranged through the use of listed devices to, (a) automatically admit water to the system by opening of a hose valve, and (b) transmit a signal to an attended location. |  | P/T Only | Yes | Fire Suppression
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.9.2.(6) | 3.2.9.2. Standpipe System Design | Pumps required to have a rated net head pressure greater than 280 kPa and their controllers shall be listed and labelled. |  | P/T Only | Yes | Fire Suppression
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.9.3.(2) | 3.2.9.3. Hose Connections | In addition to the requirements in Sentence (1), if a standpipe system is required, 65 mm diam hose connections shall be installed in each storey in the building if the building, is more than 25 m high, measured between grade and the ceiling of the top storey, or has a building area of more than 4 000 m2. |  | P/T Only | Yes | Fire Suppression
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.9.4.(4) | 3.2.9.4. Hose Stations | A hose cabinet referred to in Sentence (3) shall be of sufficient size to, contain the equipment referred to in Sentence (3), contain a listed fire extinguisher, and provide sufficient clearance to permit the use of a standard fire department hose key. |  | P/T Only | Yes | Fire Suppression
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.9.4.(7) | 3.2.9.4. Hose Stations | A hose is permitted to penetrate an exit in order to provide the required coverage to, a service room referred to in Sentence 3.2.9.1.(4), a rooftop enclosure referred to in Sentence 3.2.9.1.(5), a room not more than 50 m2 in area, or a room or group of rooms not more than 200 m2 in area in a sprinklered floor area. |  | P/T Only | Yes | Fire Suppression
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.9.4.(10) | 3.2.9.4. Hose Stations | A hose station in a Group B, Division 1 major occupancy is permitted to be located in a secure area, or in a lockable cabinet provided that, identical keys for all cabinets are located at all guard stations, or electrical remote release devices are provided and are connected to an emergency power supply. |  | P/T Only | Yes | Fire Suppression
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.9.4.(2) | 3.2.9.4. Hose Stations | Each hose station shall be equipped with a hose rack filled with not more than 30 m of 38 mm diam fire hose and the hose rack and fire hose shall be, (a) listed, or (b) approved by the Factory Mutual Research Corporation. |  | P/T Only | Yes | Fire Suppression
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.9.4.(6) | 3.2.9.4. Hose Stations | Except as permitted in Sentence (7), hose stations shall be located so that it is not necessary to penetrate an exit with a hose in order to provide the design coverage required in Clause (5)(a). |  | P/T Only | Yes | Fire Suppression
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.9.4.(3) | 3.2.9.4. Hose Stations | Except in a Group F occupancy, at each hose station, hose connections, valves, fire hose, nozzle and hose rack shall be in a hose cabinet. |  | P/T Only | Yes | Fire Suppression
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.9.4.(5) | 3.2.9.4. Hose Stations | Hose stations shall be located, so that every portion of the building can be reached by a hose stream and is within 3 m of a nozzle attached to the hose required in Sentence (2), not more than 5 m from every required exit serving a floor area, except, for the first storey, or if additional hose stations are required to achieve full coverage of the floor area, and in a conspicuous location where they are not likely to be obstructed. |  | P/T Only | Yes | Fire Suppression
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.9.4.(1) | 3.2.9.4. Hose Stations | If a standpipe system is required in a building, hose stations shall be provided in each storey in the building. |  | P/T Only | Yes | Fire Suppression
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.9.6.(1) | 3.2.9.6. Water Supply for 38mm Hose Connections | If a standpipe and hose system is required, the water supply shall be sufficient to provide a flow, measured at each of the two hydraulically most remote 38 mm diam hose connections, (a) of not less than 380 L/min, (b) for not less than 30 min, (c) at a pressure of not less than 450 kPa, and (d) of not less than 190 L/min from each of the two outlets simultaneously. |  | P/T Only | Yes | Fire Suppression
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.9.7.(4) | 3.2.9.7. Water Supply for 65 mm Hose Connections | If the building is 84 m or more high, measured between grade and the ceiling level of the top storey, the building shall be served by no fewer than two sources of water supply from a public water system. |  | P/T Only | Yes | Fire Suppression
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.9.7.(3) | 3.2.9.7. Water Supply for 65 mm Hose Connections | If the building is 84 m or more high, measured between grade and the ceiling level of the top storey, the water supply required in Sentence (1) shall be provided by sufficient pumping capacity. |  | P/T Only | Yes | Fire Suppression
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.9.7.(2) | 3.2.9.7. Water Supply for 65 mm Hose Connections | If the building is less than 84 m high, measured between grade and the ceiling level of the top storey, the water supply required in Sentence (1) is permitted to be supplied through the fire department connection. |  | P/T Only | Yes | Fire Suppression
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.9.7.(1) | 3.2.9.7. Water Supply for 65mm Hose Connections | If 65 mm diam hose connections are required, the water supply shall be sufficient to provide a flow, measured at each of the two hydraulically most remote 65 mm diam hose connections, (a) of not less than 1 890 L/min, (b) for not less than 30 min, (c) at a pressure of not less than 450 kPa, and (d) of not less than 945 L/min from each of the two outlets simultaneously. |  | P/T Only | Yes | Fire Suppression
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.1.12.(11) | 3.3.1.12. Doors and Door Hardware | A door in an access to exit in a gaming premise is permitted to be equipped with an electromagnetic locking device conforming to Sentences 3.4.6.16.(4) and (7). |  | P/T Only | Yes | Gaming Premises
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.1.3.(10) | 3.3.1.3. Means of Egress | Means of egress from a roof for personnel servicing rooftop equipment or for a below ground service room that is not normally occupied, is permitted to be provided by stairways or fixed ladders. |  | P/T Only | Yes | Means of Egress
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.1.4.(5) | 3.3.1.4. Public Corridor Separations | The sprinkler system in Sentences (3) and (4) shall be electrically supervised in conformance with Sentence 3.2.4.10.(3) and, upon operation, shall cause a signal to be transmitted to the fire department in conformance with Sentence 3.2.4.8.(4) when the corridor serves a Group E or Group F, Division 1 or 2 occupancy. |  | P/T Only | Yes | Fire Detection and Notification
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.1.5.(5) | 3.3.1.5. Egress Doorways | Except for a mezzanine which is not considered as a storey in calculating building height in Sentence 3.2.1.1.(4), where the space below a mezzanine is enclosed, an egress facility from the mezzanine shall not lead into the enclosed space. |  | P/T Only | Yes | Means of Egress
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.1.5.(3) | 3.3.1.5. Egress Doorways | Except for a mezzanine within a dwelling unit, every mezzanine that is not required to terminate at a vertical fire separation in Article 3.2.8.2. shall have two egress facilities placed in such a manner that one facility could provide egress from the mezzanine if the other facility becomes inaccessible to the occupants of the mezzanine due to a fire that might originate in the room or suite in which the mezzanine is located, (a) where the occupancy of the mezzanine, room or suite is classified as Group F, Division 1, (b) where the mezzanine is intended for an occupant load of more than 60 persons, (c) in a floor area that is not sprinklered if, (i) the area of a mezzanine is more than the value in Table 3.3.1.5.A., or (ii) the travel distance to an egress doorway or an egress facility is more than the value in Table 3.3.1.5.A., or (d) in a floor area that is sprinklered if, (i) the travel distance to an egress doorway or an egress facility is more than 25 m, or (ii) the area of the mezzanine is more than the value in Table 3.3.1.5.B. |  | P/T Only | Yes | Mezzanines
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.1.5.(4) | 3.3.1.5. Egress Doorways | For the purpose of Clauses (3)(c) and (d), (a) if the room or suite in which the mezzanine is located is permitted to have one egress doorway, the travel distance is measured from any point on the mezzanine to that doorway, or (b) if the room or suite in which the mezzanine is located is required to have more than one egress doorway, the travel distance is measured from any point on the mezzanine to the nearest egress facility leading from the mezzanine. |  | P/T Only | Yes | Mezzanines
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.1.9.(14) | 3.3.1.9. Corridors | A dead end corridor is permitted in a high hazard industrial occupancy where there is a second and separate egress doorway from each room or suite not leading into a dead end corridor. |  | P/T Only | Yes | Means of Egress
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.1.9.(13) | 3.3.1.9. Corridors | A dead end corridor is permitted in a low or medium hazard industrial occupancy where, the dead end corridor, serves an occupant load of not more than 30 persons, is not more than 9 m long, and is provided with doors having self-closing devices, or there is a second and separate egress doorway from each room or suite not leading into a dead end corridor. |  | P/T Only | Yes | Means of Egress
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.1.9.(12) | 3.3.1.9. Corridors | A dead end corridor is permitted in a mercantile occupancy where, the dead end corridor, serves an occupant load of not more than 30 persons, is not more than 9 m long, and is provided with doors having self-closing devices, or there is a second and separate egress doorway from each room or suite not leading into a dead end corridor. |  | P/T Only | Yes | Means of Egress
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.1.9.(8) | 3.3.1.9. Corridors | A dead end corridor is permitted in an assembly occupancy where there is a second and separate egress doorway from each room or suite not leading into a dead end corridor. |  | P/T Only | Yes | Means of Egress
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.1.9.(10) | 3.3.1.9. Corridors | Dead end corridors in Sentence (9) shall contain no door openings to service rooms containing fuel-fired appliances or rooms that may be considered a hazard. |  | P/T Only | Yes | Means of Egress
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.2.2.(9) | 3.3.2.2. Fire Separations | A kitchen shall not be located within the fire compartment required in Sentence (8). |  | P/T Only | Yes | Schools
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.2.2.(5) | 3.3.2.2. Fire Separations | Except as provided in Sentence (6), in an elementary or secondary school, a hazardous classroom containing an auto repair shop shall be separated from the remainder of the building by a fire-separation having a fire-resistance rating not less than, 2 h where the building is not sprinklered, or 1 h where the building is sprinklered. |  | P/T Only | Yes | Hazardous Classrooms
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.2.2.(8) | 3.3.2.2. Fire Separations | Except as required in Sentence (9), in an elementary or secondary school, where the occupant load of a room exceeds 200 persons, the room and any ancillary rooms of a complementary use shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than, (a) 1 h where the building is not sprinklered, or (b) 30 min where the building is sprinklered. |  | P/T Only | Yes | Schools
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.2.2.(4) | 3.3.2.2. Fire Separations | Except as required in Sentences (5) to (7), in an elementary or secondary school, a hazardous classroom shall be separated from the remainder of the building by a fire-separation having a fire-resistance rating not less than, (a) 1 h where the building is not sprinklered, or (b) 30 min where the building is sprinklered. |  | P/T Only | Yes | Hazardous Classrooms
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.2.2.(7) | 3.3.2.2. Fire Separations | In an elementary or secondary school, a hazardous classroom containing a spray painting operation shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than, 2 h, or 1 h where the spray painting operation is separated from the classroom by a fire-separation having a fire-resistance rating not less than 1 h. |  | P/T Only | Yes | Hazardous Classrooms
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.2.2.(6) | 3.3.2.2. Fire Separations | In an elementary or secondary school, if there is a group of hazardous classrooms or a group of hazardous classrooms and ancillary rooms of a complementary use, the fire separation required by Sentence (4) or (5) need not be provided within the group but the fire separation is required between the group and the remainder of the building. |  | P/T Only | Yes | Hazardous Classrooms
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.2.3.(5) | 3.3.2.3. Fixed Seats | The requirements of Sentence (3) do not apply if, there are not more than seven seats between any seat and the nearest aisle, where the seats are served by a single aisle, there are not more than 20 seats between any seat and the nearest aisle, where the seats are served by two aisles, each row has an unobstructed passage with minimum width of 400 mm plus 6.1 mm for each additional seat above 16 seats in the row, and the travel distance is not more than 45 m measured along the path of travel from any seat to an exit or to an egress doorway. |  | P/T Only | Yes | Assembly Seating
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.2.4.(4) | 3.3.2.4. Aisles | A converging aisle shall terminate at, an egress doorway from the seating area, or an exit from the seating area. |  | P/T Only | Yes | Assembly Seating
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.2.4.(14) | 3.3.2.4. Aisles | Dead-end aisles are permitted to be more than 10 m long, but not more than 13 m long if, the seating area is separated from other seating areas and adjacent occupancies, including a corridor serving any seating area, by a fire separation in accordance with Sentences 3.3.2.2.(1) and (2), the travel distance is not more than 25 m measured along the path of travel from any seat to an exit, to an egress doorway or to an opening into a vomitory, at least one means of egress, comprising not less than 30 per cent of the required exit capacity, is through an exterior exit, an exit stairway or a corridor not containing an occupancy, each row served by a dead-end aisle has a minimum unobstructed width of 400 mm plus 6.1 mm for each additional seat above seven seats in a row, but not more than 550 mm, the activation of a fire detector or a sprinkler head in the seating area will, cause the shutdown of the projection system serving the seating area, and turn on the normal lighting in the seating area, a voice communication system is installed in conformance with Article 3.2.4.23., a smoke control system is installed to control movement of smoke in the seating area or a smoke exhaust system is provided so that, in the event of detection of smoke by a smoke detector in the seating area, air handling equipment is activated to extract air directly from the seating area at the rate of at least six air changes per hour, and the floor area is sprinklered. |  | P/T Only | Yes | Assembly Seating
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.2.4.(13) | 3.3.2.4. Aisles | Dead-end aisles are permitted to be more than 6 m long, but not more than 10 m long if, the seating area is separated from other seating areas and adjacent occupancies, including a corridor serving any seating area, by a fire separation in accordance with Sentences 3.3.2.2.(1) and (2), the travel distance is not more than 25 m measured along the path of travel from any seat to an exit, to an egress doorway or to an opening into a vomitory, at least one means of egress, comprising not less than 30 per cent of the required exit capacity, is through an exterior exit, an exit stairway or a corridor not containing an occupancy, each row served by the dead-end aisle has a minimum unobstructed width of 400 mm plus 6.1 mm for each additional seat above seven seats in a row, but not more than 550 mm, the minimum ceiling height above the seating area is 3 m, the activation of a fire detector or a sprinkler head in the seating area will, cause the shutdown of the projection system serving the seating area, and turn on the normal lighting in the seating area, and the floor area is sprinklered. |  | P/T Only | Yes | Assembly Seating
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.2.4.(9) | 3.3.2.4. Aisles | If rows of seats discharge directly into the converging aisle, the width required by Sentence (8) shall be increased by 25 mm for each metre of length of the aisle where the rows of seats discharge into the aisle. |  | P/T Only | Yes | Assembly Seating
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.2.4.(2) | 3.3.2.4. Aisles | In this Subsection, a converging aisle is an aisle into which the occupants of two or more aisles converge in travelling to an exit. |  | P/T Only | Yes | Assembly Seating
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.2.4.(11) | 3.3.2.4. Aisles | The requirements in Sentences (5) to (10) and (17) do not apply if, (a) the minimum clear width of an aisle is in accordance with Article 3.3.1.16., but is not less than 900 mm if serving seats on one side only, (b) the minimum clear width of an aisle is in accordance with Article 3.3.1.16., but is not less than 1 200 mm if serving seats on both sides, (c) the minimum clear width of a converging aisle is in accordance with Article 3.3.1.16., but not less than the width of the widest aisle leading to the converging aisle, (d) the minimum clear width of an exit leading directly from the seating area is in accordance with Article 3.4.3.2., (e) except as provided in Clause (f), the minimum clear width of an egress doorway leading directly from the seating area is in accordance with Article 3.3.1.16., but not less than the required width of the aisle or the converging aisle leading to the doorway, and (f) if more than one vomitory is provided, (i) the minimum total clear width of the egress doorways leading from one vomitory is not less than the required width of the aisle or the converging aisle leading to the doorways, and (ii) the minimum clear width of egress doorways from additional vomitories is in accordance with Article 3.3.1.16. |  | P/T Only | Yes | Assembly Seating
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.2.4.(10) | 3.3.2.4. Aisles | The width of an egress doorway or an exit leading directly from the seating area shall be not less than the required width of the widest aisle or converging aisle plus 50% of the total required width of the remaining aisles and converging aisles that it serves. |  | P/T Only | Yes | Assembly Seating
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.3.2.(3) | 3.3.3.2. Fire Separations | Except as permitted by Sentence (4), in a Group B, Division 3 occupancy, walls separating corridors serving sleeping rooms from adjacent rooms shall be constructed as fire separations having a fire-resistance rating not less than 1 h, except that the fire-resistance rating need not be more than 45 min where the floor assembly is not required to be more than 45 min. |  | P/T Only | Yes | Care Occupancy
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.3.2.(5) | 3.3.3.2. Fire Separations | The door in the fire-separation required in Sentence (4) is permitted to be equipped with a roller latch and need not be provided with a self-closing device. |  | P/T Only | Yes | Care Occupancy
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.3.2.(4) | 3.3.3.2. Fire Separations | The walls separating sleeping rooms from adjacent rooms and corridors in those parts of a floor area classified as a Group B, Division 3 occupancy shall be constructed as fire separations but are not required to have a fire-resistance rating if, (a) those parts of the floor area contain sleeping accommodation for not more than 10 persons, and (b) not more than six occupants require assistance in evacuation in case of an emergency. |  | P/T Only | Yes | Care Occupancy
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.3.8.(1) | 3.3.3.8. Handrails | Corridors and ramps used by residents in a long-term care home shall be equipped with handrails on each side conforming to Sentences 3.4.6.5.(5) to (7) and (11) to (13). |  | P/T Only | Yes | Falling, Tripping, Slipping Protection
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.4.10.(1) | 3.3.4.10. Resistance to Forced Entry | Resistance to forced entry into dwelling units shall conform to the applicable requirements in Articles 9.7.5.2. and 9.7.5.3. |  | P/T Only | Yes | Dwelling Units
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.4.11.(6) | 3.3.4.11. Retirement Homes | A closure in a fire separation between fire compartments referred to in Sentence (2) shall be weatherstripped or otherwise designed and installed to retard the passage of smoke. |  | P/T Only | Yes | Retirement Homes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.4.11.(12) | 3.3.4.11. Retirement Homes | A voice communication system conforming to Article 3.2.4.23. shall be provided in a retirement home. |  | P/T Only | Yes | Retirement Homes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.4.11.(8) | 3.3.4.11. Retirement Homes | Each fire compartment referred to in Sentence (2) shall be capable of accommodating, in addition to its own occupants, the occupants of the largest adjacent fire compartment based on a clear floor space of 1.5 m2 per resident in the adjacent fire compartment. |  | P/T Only | Yes | Retirement Homes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.4.11.(2) | 3.3.4.11. Retirement Homes | Except as permitted by Sentence (3), a floor area containing residentsÃ¢â‚¬â„¢ sleeping rooms in a retirement home where sleeping accommodation is provided for more than 10 residents shall be divided into no fewer than two fire compartments, each not more than 1 000 m2 in area. |  | P/T Only | Yes | Retirement Homes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.4.11.(4) | 3.3.4.11. Retirement Homes | Except as permitted by Sentence (5), fire separations separating fire compartments required by Sentence (2) shall have a fire-resistance rating not less than 1 h. |  | P/T Only | Yes | Retirement Homes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.4.11.(1) | 3.3.4.11. Retirement Homes | Floor areas containing residentsÃ¢â‚¬â„¢ sleeping rooms in a retirement home shall conform to Sentences (2) to (12). |  | P/T Only | Yes | Retirement Homes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.4.11.(10) | 3.3.4.11. Retirement Homes | In a retirement home, a dead end public corridor is permitted provided it is not more than 3 m long. |  | P/T Only | Yes | Retirement Homes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.4.11.(9) | 3.3.4.11. Retirement Homes | The fire separation required by Sentence 3.3.5.5.(1) between a retirement home and a repair garage shall have no openings. |  | P/T Only | Yes | Retirement Homes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.4.11.(5) | 3.3.4.11. Retirement Homes | The fire-resistance rating of a fire separation referred to in Sentence (4) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for, the floor assembly above the floor area, or the floor assembly below the floor area, if there is no floor assembly above. |  | P/T Only | Yes | Retirement Homes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.4.11.(3) | 3.3.4.11. Retirement Homes | The floor area on either side of a horizontal exit conforming to Article 3.4.6.10. is permitted to be considered as a fire compartment in applying the requirements of this Article. |  | P/T Only | Yes | Retirement Homes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.4.11.(11) | 3.3.4.11. Retirement Homes | The minimum clear width of doorways serving residents in a retirement home shall be 860 mm. |  | P/T Only | Yes | Retirement Homes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.4.11.(7) | 3.3.4.11. Retirement Homes | The travel distance from any point within each fire compartment referred to in Sentence (2) to a door to an adjoining fire compartment shall be not more than 45 m. |  | P/T Only | Yes | Retirement Homes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.4.4.(8) | 3.3.4.4. Egress from Dwelling Units | Each dwelling unit in a building conforming to Subclause 3.2.2.44.(1)(a)(ii) shall be served by, a direct exit that is an exterior doorway located not more than 1.5 m above adjacent ground level, or a stairway that, leads to an exterior doorway not more than 1.5 m above adjacent ground level, has no access to another dwelling unit, and is separated from the remainder of the building with a fire separation having a fire-resistance rating not less than 1 h. |  | P/T Only | Yes | Dwelling Units
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.4.4.(7) | 3.3.4.4. Egress from Dwelling Units | Where a balcony is provided to meet the requirements of Sentence (3) or (4), the balcony shall have, a solid floor having a fire-resistance rating not less than that required for a floor assembly between suites, and an area providing not less than 1.5 m2 per suite occupant, based on occupant load, and a minimum dimension of 1 200 mm. |  | P/T Only | Yes | Dwelling Units
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.4.7.(3) | 3.3.4.7. Stairs, Ramps, Landings, Handrails and Guards for | Loads on exterior guards serving a single dwelling unit shall comply with Part 4. |  | P/T Only | Yes | Dwelling Units
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.5.8.(1) | 3.3.5.8. Toe-Boards Required | Where tools or other objects could fall from the floor of an upper level to a lower level in a room or space intended for use as a Group F occupancy, the edge of the floor at the upper level shall be provided with a toe-board extending from the floor surface to a height at least 125 mm above the floor surface |  | P/T Only | Yes | Risk of Collision
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.6.3.(4) | 3.3.6.3. Indoor Storage of Compressed Gases | A room described in Sentence (1) or (3) shall be, (a) mechanically vented to the outside so as to ensure at least one air change per hour, or (b) naturally vented to the outside so as to ensure cross ventilation through non-closable louvered openings with, (i) at least one opening having an aggregate free opening area of at least 0.2 m2 per 100 m2 of the floor area located not more than 300 mm from the ceiling, and (ii) at least one opening having an aggregate free opening area of at least 0.2 m2 per 100 m2 of the floor area located not more than 300 mm from the floor. |  | P/T Only | Yes | Fire Hazards
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.6.3.(5) | 3.3.6.3. Indoor Storage of Compressed Gases | Except as permitted by Sentences (6) and (7), where required by the Fire Code made under the Fire Protection and Prevention Act, 1997, an area intended for the storage of cylinders containing compressed gases that may react with one another shall be divided into separate fire compartments having a fire-resistance rating of not less than 1 h. |  | P/T Only | Yes | Fire Hazards
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.6.3.(1) | 3.3.6.3. Indoor Storage of Compressed Gases | Except as provided by Sentence (3), where required by the Fire Code made under the Fire Protection and Prevention Act, 1997, a room intended for the indoor storage of cylinders containing flammable compressed gases shall meet the following requirements, (a) it is separated from the remainder of the building by a gas-tight fire separation having a fire-resistance rating of not less than 2 h, (b) it is located on an exterior wall of the building, (c) it can be entered from the exterior, (d) it is ventilated in conformance with Sentence (4), (e) it is constructed so that an exterior wall provides explosion venting, (i) in the ratio of 0.2 m2 for each cubic metre of room volume, or (ii) in the ratio computed in accordance with NFPA 68, "Explosion Protection by Deflagration Venting", but in no case less than 0.065 m2 of vent area for each cubic metre of room volume, (f) it is not intended to contain fuel-fired equipment or high temperature heating elements, and (g) it is not intended to be used for a purpose other than the storage of compressed gas. |  | P/T Only | Yes | Fire Hazards
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.6.3.(7) | 3.3.6.3. Indoor Storage of Compressed Gases | Separate fire compartments required by Sentence (5) need not be provided, if the area intended for the storage of cylinders containing compressed gases that are heavier than air is separated by a concrete or masonry wall having a height of at least 1.5 m and projecting such that the minimum distance that vapour can travel between two cylinders of gas that may react with each other is not less than 15 m, measured horizontally. |  | P/T Only | Yes | Fire Hazards
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.6.3.(6) | 3.3.6.3. Indoor Storage of Compressed Gases | Separate fire compartments required by Sentence (5) need not be provided, if the area intended for the storage of cylinders containing compressed gases that are lighter than air is separated by a concrete or masonry wall having a height of at least 2.0 m and projecting at least 1.0 m, measured horizontally, beyond the cylinders. |  | P/T Only | Yes | Fire Hazards
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.6.3.(2) | 3.3.6.3. Indoor Storage of Compressed Gases | Where a closure is installed in the fire separation separating the room from the remainder of the building in accordance with Clause (1)(a), it shall be, (a) equipped with a self-closing device that keeps the closure closed when not in use, and (b) constructed so as to prevent the migration of gases from the room into other parts of the building. |  | P/T Only | Yes | Fire Hazards
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.6.3.(3) | 3.3.6.3. Indoor Storage of Compressed Gases | Where required by the Fire Code made under the Fire Protection and Prevention Act, 1997, a room intended for the storage of not more than three cylinders of flammable compressed gases that are heavier than air and that have an aggregate capacity not exceeding 100 kg shall be, (a) separated from the remainder of the building by a gas-tight fire separation having a fire-resistance rating of not less than 45 min, (b) located at or above grade, and (c) ventilated in conformance with Sentence (4). |  | P/T Only | Yes | Fire Hazards
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.6.4.(5) | 3.3.6.4. Storage and Dispensing Rooms for Flammable Liquids | A dispensing room in an occupancy or facility described in Sentence (4) which has an area greater than 15 m2 or in which the travel distance from any point to the nearest egress door is more than 4.5 m shall, (a) be located in a floor area that has at least two exits, and (b) have at least two egress doors. |  | P/T Only | Yes | Fire Hazards
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.6.4.(4) | 3.3.6.4. Storage and Dispensing Rooms for Flammable Liquids | A room in an occupancy or facility covered by Regulation 851 of the Revised Regulations of Ontario, 1990 (Industrial Establishments), made under the Occupational Health and Safety Act, or Ontario Regulation 67/93 (Health Care and Residential Facilities), made under that Act, where Class IA liquids are intended to be stored in closed containers or Class I liquids are intended to be dispensed or stored in open containers, shall be designed to prevent critical structural and mechanical damage from an internal explosion in accordance with good engineering practice, such as that described in NFPA 68, “Explosion Protection by Deflagration Venting”. |  | P/T Only | Yes | Fire Hazards
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.6.4.(6) | 3.3.6.4. Storage and Dispensing Rooms for Flammable Liquids | An egress door serving a room described in Sentence (5) shall, (a) be equipped with a self-closing device, and (b) swing on a vertical axis in the direction of travel to the exit. |  | P/T Only | Yes | Fire Hazards
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.6.4.(3) | 3.3.6.4. Storage and Dispensing Rooms for Flammable Liquids | Sentence (2) does not apply to a room intended for the storage of distilled beverage alcohol |  | P/T Only | Yes | Fire Hazards
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.6.4.(7) | 3.3.6.4. Storage and Dispensing Rooms for Flammable Liquids | The minimum distance between the egress doors described in Clause (5)(b) shall be not less than three-quarters of the maximum diagonal dimension of the room. |  | P/T Only | Yes | Fire Hazards
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.6.4.(8) | 3.3.6.4. Storage and Dispensing Rooms for Flammable Liquids | The travel distance within the room to the nearest egress door described in Clause (5)(b) shall be not more than 23 m. |  | P/T Only | Yes | Fire Hazards
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.4.1.5.(2) | 3.4.1.5. Exterior Exit Passageways | Every exterior exit passageway that has a drop of more than 500 mm on any side shall have guards on the open sides not less than 1 070 mm high. |  | P/T Only | Yes | Exits
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.4.4.4.(10) | 3.4.4.4. Integrity of Exits | In elementary and secondary schools, an exit shall be designed so that it does not serve as an access from one portion of a floor area to another portion of the same floor area |  | P/T Only | Yes | Schools
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.4.5.1.(10) | 3.4.5.1. Exit Signage | An exit sign is not required within a suite containing a Group B, Division 3 occupancy if the following requirements are met: (a) the suite contains sleeping accommodation for not more than 10 persons, and (b) not more than 6 occupants require assistance in evacuation in case of an emergency. |  | P/T Only | Yes | Care Occupancy
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.4.5.1.(9) | 3.4.5.1. Exit Signage | Except for suite doors opening directly to the exterior, every exit serving a hotel shall have an exit sign placed over or adjacent to it. |  | P/T Only | Yes | Hotels
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.4.6.1.(2) | 3.4.6.1. Surface Finish of Ramps and Stairs | A tactile attention indicator conforming to Article 3.8.3.18. shall be installed, (a) at the top of the stairs, starting one tread depth back from the edge of the top stair, and (b) at the leading edge of landings where a doorway opens onto stairs, starting one tread depth back from the edge of the landing |  | P/T Only | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.4.6.12.(3) | 3.4.6.12. Direction of Door Swing | Except in a high hazard industrial occupancy, an exit door need not swing in the direction of exit travel where it serves, (a) a room, suite or floor area having an occupant load of not more than 60 persons, or (b) as part of a means of egress from more than one floor area and the floor areas so served have a total occupant load of not more than 60 persons. |  | P/T Only | Yes | Exits
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.4.6.4.(6) | 3.4.6.4. Dimensions of Landings (See Appendix A.) | Where the direction of exit travel changes at a landing, the landing is permitted to be chamfered or curved in plan, provided the required width of the stair is maintained where measured perpendicular to the direction of exit travel across the landing. |  | P/T Only | Yes | Exits
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.4.6.5.(16) | 3.4.6.5. Handrails | In a long-term care home, a Group B, Division 3 occupancy and a retirement home, a continuous handrail shall be provided on both sides of a stair throughout the length of the stair, including landings, except where a handrail is interrupted by doorways or newels at changes in direction. |  | P/T Only | Yes | Care Occupancy
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.5.2.1.(1) | 3.5.2.1. Required Elevator | Except as provided in Sentence (2), in a Group B, Division 2 or 3 occupancy, if sleeping rooms or patient or resident services are provided on more than one floor level and the floor levels are not connected by ramps conforming to Article 3.8.3.4., such floor levels shall be served by at least one elevator that is large enough to accommodate a stretcher in a horizontal position. |  | P/T Only | Yes | Vertical Transportation
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.5.2.1.(2) | 3.5.2.1. Required Elevator | Sentence (1) does not apply to those parts of a floor area classified as a Group B, Division 3 occupancy if, (a) those portions of the floor area contain sleeping accommodation for not more than 10 persons, and (b) not more than six occupants require assistance in evacuating in the case of an emergency. |  | P/T Only | Yes | Vertical Transportation
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.6.1.1.(2) | 3.6.1.1. Scope | Except for plemun requirements of 3.6.4.3., the fire saftey characteristics of heating, ventilating and air-conditioning systems shall comly with Part 6. |  | P/T Only | Yes | Fire Containment
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.6.1.5.(1) | 3.6.1.5. Fixed Access Ladders | If a fixed ladder is installed to provide access to a roof of a building, the design and installation of the attachment and anchorage system for the ladder shall be as described in MMAH Supplementary Standard SB-8, "Design, Construction and Installation of Anchorage System for Fixed Access Ladders". |  | P/T Only | Yes | Means of Egress
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.6.2.1.(11) | 3.6.2.1. Fire Separations around Service Rooms | The fire separation provisions for a fuel-fired applaicne in a portable classroom shall confrom to Article 3.9.3.7. |  | P/T Only | Yes | Fire Containment
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.6.2.7.(3) | 3.6.2.7. Electrical Equipment Vaults | A vault, that is part of a building and houses electrical equipment indoors, shall have, (a) roofs or ceilings consisting of reinforced concrete of adequate strength for the conditions and not less than 150 mm thick, and (b) floors consisting of reinforced concrete of adequate strength for the conditions and not less than 150 mm thick, except that floors that are at excavation level are permitted to be of reinforced concrete not less than 100 mm thick. |  | P/T Only | Yes | Fire Containment
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.6.2.7.(6) | 3.6.2.7. Electrical Equipment Vaults | A ventilation duct or opening, that penetrates the fire separation to the outdoors, need not be protected by a closure at the penetration. |  | P/T Only | Yes | Fire Containment
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.6.2.7.(13) | 3.6.2.7. Electrical Equipment Vaults | All ventilation openings shall be protected in conformance with Sentences 6.2.3.12.(3) and (4) and the protection shall be installed in such a manner that it cannot be removed from the outside by the use of common tools and it is tamperproof. |  | P/T Only | Yes | Fire Containment
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.6.2.7.(18) | 3.6.2.7. Electrical Equipment Vaults | Every electrical equipment vault shall be provided with, (a) adequate lighting, controlled by one or more switches located near the entrance, (b) luminaires located so that they may be relamped without danger to personnel, and (c) a grounded receptacle located in a convenient location inside the vault, near the entrance. |  | P/T Only | Yes | Referenced Standard
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.6.2.7.(11) | 3.6.2.7. Electrical Equipment Vaults | In the vault ventilation system in Sentence (10), the inlet for fresh air shall lead from an outdoor area and shall terminate at a point not more than 1 000 mm above the floor level of the vault. |  | P/T Only | Yes | Fire Containment
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.6.2.7.(15) | 3.6.2.7. Electrical Equipment Vaults | The floor of the electrical equipment vault described in Sentences (1) and (2) may be provided with a floor drain connected to a covered sump capable of holding all of the liquid from the largest item of electrical equipment, and the connection shall have a noncombustible trap to prevent the spread of fire from the vault to the sump. |  | P/T Only | Yes | Building services and utilities
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.6.2.7.(4) | 3.6.2.7. Electrical Equipment Vaults | Walls, roofs or ceilings, and floors shall be adequately anchored together in a manner designed to resist dislodgement by explosion. |  | P/T Only | Yes | Fire Containment
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.6.2.7.(17) | 3.6.2.7. Electrical Equipment Vaults | Where doors are provided between the vault described in Sentence (16) and the rest of the building, they shall have suitable seals such as weatherstripping to minimize the entrance of dust into the vault. |  | P/T Only | Yes | Referenced Standard
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.6.2.7.(16) | 3.6.2.7. Electrical Equipment Vaults | Where the electrical equipment vault is located in a hazardous location classified as Class II, Division 1 in accordance with the Electrical Safety Code adopted under Ontario Regulation 164/99 (Electrical Safety Code) made under the Electricity Act, 1998, it shall have, (a) no vent opening except to the exterior of the building, and (b) suitable pressure-relief openings communicating only with the air outside the building. |  | P/T Only | Yes | Referenced Standard
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.6.2.7.(12) | 3.6.2.7. Electrical Equipment Vaults | Where the vault ventilation system in Sentence (9) is a mechanical system, it shall be separate from the system for the remainder of the building and shall be designed so that, (a) the vault temperature is thermostatically controlled, (b) the fan is located so that it may be serviced without danger to personnel, (c) a high temperature alarm is provided in the vault, (d) the system is automatically shut off in the event of a fire in the vault, and (e) a filter is provided in the air inlet if there is a possibility of dirt being drawn in. |  | P/T Only | Yes | fire Containment
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.6.2.7.(10) | 3.6.2.7. Electrical Equipment Vaults | Where the vault ventilation system in Sentence (9) is directly from an outdoor area by natural ventilation without the use of ducts, and where the electrical equipment is the principal source of heat, the combined net area of inlet and outlet openings shall be not less than 0.002 m2/kVa of electrical equipment capacity with a minimum of 0.093 m2, except that, (a) where equipment in the power class as described in CAN/CSA-C88-M, "Power Transformers and Reactors" is installed, ventilation requirements are permitted to be based on the actual full-load losses, or (b) where the equipment is installed for emergency purposes only and is not normally energized, it need not be considered in determining the ventilation requirements. |  | P/T Only | Yes | Fire Containment
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.1.2.(1) | 3.7.1.2. Residential Room Dimensions | The areas of rooms in dwelling units, dormitories, boarding houses and rooming houses shall conform to Part 9. |  | P/T Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.1.3.(1) | 3.7.1.3. Sleeping Areas in Group B and Child Care Facilities | (1) Except as provided in Sentence (2), a sleeping area in a Group B occupancy shall provide not less than 4.7 m2 per person in a room having, (a) an area not less than 7 m2, (b) a horizontal dimension not less than 2 000 mm, and (c) a ceiling height not less than 2 300 mm. |  | P/T Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.1.3.(3) | 3.7.1.3. Sleeping Areas in Group B and Child Care Facilities | A child care facility shall provide sleeping accommodation having not less than 0.93 m2 of floor surface area for each child with not less than 2 300 mm ceiling height over the entire room area. |  | P/T Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.1.3.(2) | 3.7.1.3. Sleeping Areas in Group B and Child Care Facilities | Sleeping rooms for residents in long-term care homes shall have, exclusive of space provided for washrooms and for built-in or portable clothes closets, a floor space not less than, (a) 10.22 m2 in a single-bed unit, (b) 16.72 m2 in a two-bed unit, (c) 25.08 m2 in a three-bed unit, and (d) 29.73 m2 in a four-bed unit. |  | P/T Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.1.4.(2) | 3.7.1.4. Sleeping Areas in Camps | A camp for housing of workers shall have an area of not less than 3.72 m2 per employee in every room used for sleeping purposes. |  | P/T Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.1.4.(1) | 3.7.1.4. Sleeping Areas in Camps | Recreational camps shall have an area in the sleeping quarters of not less than 3.72 m2 per camper or, if double or triple tier bunk units are used, 2.79 m2 per camper. |  | P/T Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.2.1.(1) | 3.7.2.1. Window Areas | Except as provided in Sentences (2) and (3) or otherwise permitted, every room used for sleeping in any building, and every principal room such as living room, dining room or combination of them in dwelling units shall be provided with windows having areas conforming to Part 9, except that Article 9.9.10.1. does not apply. |  | P/T Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.2.1.(2) | 3.7.2.1. Window Areas | Long-term care homes shall have, in an activity room, a sitting room or a lounge, one or more windows with a total unobstructed glass area, exclusive of skylights, of not less than 10% of the area of the room, and in a residentsÃ¢â‚¬â„¢ sleeping room, one or more windows that, have a total unobstructed glass area, exclusive of skylights, of not less than 10% of the area of the room, open to the outdoors and have a total unobstructed glass area, exclusive of skylights, of not less than 5% of the area of the room, and are installed with the bottom edge of the glass of every window not more than 660 mm above the floor. |  | P/T Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.2.1.(3) | 3.7.2.1. Window Areas | Play activity rooms in a child care facility and work areas in live/work units shall have one or more windows that conform to Clause (2)(a). |  | P/T Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.4.1.(1) | 3.7.4.1. Plumbing and Drainage Systems | Except as permitted in Sentence (3), each building situated on property that abuts on a street in which a public or municipal water main is located shall be provided with or have accessible to its occupants a plumbing system including a potable water supply, a sanitary drainage system and plumbing fixtures. |  | P/T Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.4.1.(3) | 3.7.4.1. Plumbing and Drainage Systems | Plumbing fixtures need not be provided in a building that is not normally occupied by persons where such installations are impractical and other fixtures are available in nearby buildings when the subject building is in use. |  | P/T Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.4.15.(1) | 3.7.4.15. Clearances for Water Closets | Except in a dwelling unit and except as required by Section 3.8., a minimum clearance of 380 mm shall be provided in front of a water closet. |  | P/T Only | No
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.4.16.(2) | 3.7.4.16. Privacy | Except in a room for private use, water closets, urinals, lavatories, showers and bathtubs shall not be visible from the entrance to the room where it contains at least, two water closets, one water closet and one urinal, one shower stall, or one bathtub. |  | P/T Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.4.16.(1) | 3.7.4.16. Privacy | If a room contains not more than 1 water closet, the doorway to the room shall be provided with a full height door that is capable of being locked from the inside. |  | P/T Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.4.17.(1) | 3.7.4.17. Water Temperature Control | A water distribution system supplying hot water to plumbing fixtures shall conform to the requirements in Subsection 7.6.5. |  | P/T Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.4.18.(1) | 3.7.4.18. Drinking Water | On every floor where work will be performed and within 100 m of any area where work will be performed, potable water shall be provided from, (a) a fountain with an upward jet, (b) a tap from a piped water supply, or (c) a tap from a covered vessel. |  | P/T Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.4.19.(1) | 3.7.4.19. Pharmacies | Every pharmacy shall be provided with a sink with hot and cold potable water for washing utensils used in the preparation, service or storage of drugs. |  | P/T Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.4.2.(1) | 3.7.4.2. Plumbing Fixtures, General | For the purposes of this Subsection, the occupant load shall be determined in accordance with the provisions in Subsection 3.1.17. except that in a Group D occupancy, the area per person shall be 14 m2. (See Appendix A.) |  | P/T Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.4.2.(8) | 3.7.4.2. Plumbing Fixtures, General | Where one water closet is required for males and one water closet is required for females, the following may be provided in lieu of the water closets otherwise required by this Subsection: one universal washroom conforming to Sentence 3.8.3.12.(1), and one washroom containing one water closet that is permitted to be used by both sexes provided the door to the room can be locked from the inside. |  | P/T Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.4.3.(7) | 3.7.4.3. Plumbing Fixtures for Assembly Occupancies | Except as provided in Sentence (8), in every dining room, restaurant, cafeteria and alcoholic beverage establishment having not more than 40 seats, employees are permitted to share the sanitary facilities provided for patrons, and the minimum number of water closets shall conform to Table 3.7.4.3.D. based on, (a) a male occupant load of 50% of the number of seats plus the number of male employees, and (b) a female occupant load of 50% of the number of seats plus the number of female employees. |  | P/T Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.4.3.(4) | 3.7.4.3. Plumbing Fixtures for Assembly Occupancies | Except as provided in Sentences (6) and (7), the number of water closets required for dining rooms, restaurants and cafeteria shall conform to Table 3.7.4.3.D. |  | P/T Only | Yes | Food Premises
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.4.3.(2) | 3.7.4.3. Plumbing Fixtures for Assembly Occupancies | Except for motion picture theatres, the number of water closets required for Group A, Division 1 occupancies shall conform to Table 3.7.4.3.B. |  | P/T Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.4.3.(10) | 3.7.4.3. Plumbing Fixtures for Assembly Occupancies | For a parking lot that is part of a restaurant where patrons are intended to eat in vehicles parked on the lot, the number of water closets required shall conform to, Table 3.7.4.3.G. where food service by employees is not provided on the parking lot, or Table 3.7.4.3.H. where employees serve food on the parking lot. |  | P/T Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.4.3.(6) | 3.7.4.3. Plumbing Fixtures for Assembly Occupancies | In every dining room, restaurant, cafeteria and alcoholic beverage establishment having more than 40 seats, separate sanitary facilities shall be provided for employees, in addition to facilities provided for patrons, and the number of water closets and lavatories required shall conform to Table 3.7.4.3.F |  | P/T Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.4.3.(9) | 3.7.4.3. Plumbing Fixtures for Assembly Occupancies | The number of employees in Sentences (6) to (8) shall be the maximum number of employees who are normally present on the premises at one time and shall include only those who are present for more than 25 per cent of the working day. |  | P/T Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.4.3.(12) | 3.7.4.3. Plumbing Fixtures for Assembly Occupancies | The number of water closets required for dance halls and recreational establishments shall be at least one fixture for each 100 males and one fixture for each 75 females. |  | P/T Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.4.3.(11) | 3.7.4.3. Plumbing Fixtures for Assembly Occupancies | The number of water closets required for drive-in theatres shall conform to Table 3.7.4.3.H. |  | P/T Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.4.3.(5) | 3.7.4.3. Plumbing Fixtures for Assembly Occupancies | The number of water closets required for establishments used primarily for the consumption of alcoholic beverages that provide limited or no food service shall conform to Table 3.7.4.3.E. |  | P/T Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.4.3.(15) | 3.7.4.3. Plumbing Fixtures for Assembly Occupancies | The number of water closets required for non-residential college buildings shall be at least one fixture for each 100 males and one fixture for each 75 females. |  | P/T Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.4.3.(3) | 3.7.4.3. Plumbing Fixtures for Assembly Occupancies | The number of water closets required shall conform to Table 3.7.4.3.C. for, motion picture theatres, Group A, Division 3 occupancies, Group A, Division 4 occupancies, and outdoor pools. |  | P/T Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.4.3.(8) | 3.7.4.3. Plumbing Fixtures for Assembly Occupancies | Where a separate employee washroom is provided, the same room may be used by both female and male employees provided that, (a) the total number of employees is not more than 5, and (b) the door to the room can be locked from the inside. |  | P/T Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.4.4.(3) | 3.7.4.4. Plumbing Fixtures for Care, Care and Treatment or | The number of water closets required for employees in Group B, Division 2 or 3 occupancies shall conform to Table 3.7.4.4. |  | P/T Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.4.6.(4) | 3.7.4.6. Plumbing Fixtures for Other Residential Occupancies | A camp for housing of workers shall include, at least one shower or other area of bathing, and provisions for at least one washing machine or laundry tub for every 15 beds. |  | P/T Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.4.6.(2) | 3.7.4.6. Plumbing Fixtures for Other Residential Occupancies | At least one water closet or privy shall be provided for every, 10 campers of each sex in a recreational camp, and 10 employees of each sex in a camp for housing of workers. |  | P/T Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.4.6.(3) | 3.7.4.6. Plumbing Fixtures for Other Residential Occupancies | In recreational camps and camps for housing of workers, no fewer than two lavatories or provision for a pail or other portable container of sound construction shall be provided for each of the water closets or privies required in Sentence (2). |  | P/T Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.4.8.(1) | 3.7.4.8. Plumbing Fixtures for Mercantile Occupancies | Except as provided in this Article, the number of water closets required for employees in mercantile occupancies shall conform to Table 3.7.4.8. |  | P/T Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.4.8.(4) | 3.7.4.8. Plumbing Fixtures for Mercantile Occupancies | For a restaurant classified as mercantile occupancy, the number of water closets and lavatories required shall conform to Article 3.7.4.3. |  | P/T Only | Yes | Food Premises
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.5.1.(1) | 3.7.5.1. Electrical Systems | In anaesthetizing locations, electrical systems shall be designed, constructed, installed and tested in conformance with CSA Z32, "Electrical Safety and Essential Electrical Systems in Health Care Facilities". |  | P/T Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.5.3.(1) | 3.7.5.3. Shielding of X-Ray Equipment | Every installation of an x-ray machine or of x-ray equipment in a building shall be shielded to protect any person who could be exposed to radiation inside and outside the building. |  | P/T Only | Yes | Health: Indoor Conditions
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.6.2.(3) | 3.7.6.2. Room Finishes | Wall and ceiling finishes of rooms and passageways shall be easy to clean. |  | P/T Only | Yes | Food Premises
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.6.3.(1) | 3.7.6.3. Location of Plumbing Fixtures | A room containing a water closet shall be located where, it does not open directly into any room or area where food or drink for human consumption, or an ingredient of food or drink for human consumption, is intended to be stored, prepared, processed, distributed, served, sold or offered for sale, and it is not necessary for the public to go through the food preparation areas to gain access to the plumbing fixtures. |  | P/T Only | Yes | Food Premises
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.6.3.(3) | 3.7.6.3. Location of Plumbing Fixtures | A room containing plumbing fixtures for the public in Sentence (2) need not be located in the restaurant if, the room is located in the building containing the restaurant, and the distance of travel between the restaurant and the room is not more than 45 m. |  | P/T Only | Yes | Food Premises
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.6.3.(2) | 3.7.6.3. Location of Plumbing Fixtures | Except as permitted in Sentence (3), a room containing plumbing fixtures for the public and employees in a restaurant shall be located in the restaurant. |  | P/T Only | Yes | Food Premises
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.6.4.(3) | 3.7.6.4. Lavatories, Appliances and Sinks | A retail food premises is exempt from compliance with this Article if its eating and drinking area does not exceed 56 m2 and any one or more of the following applies: it is designed to sell only cold drinks in or from the original container, it is designed to sell only frozen confections in the original package or wrapper, it is designed to prepare and sell only hot beverages, it is designed to prepare and sell only popped corn, roasted nuts or french-fried potatoes, it is designed to sell only food or drink for human consumption that, is pre-packaged at a premises other than the food premises at which it is being offered for sale, and is not capable of supporting the growth of pathogenic organisms or the production of the toxins of such organisms. |  | P/T Only | Yes | Food Premises
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.6.4.(1) | 3.7.6.4. Lavatories, Appliances and Sinks | A separate lavatory for the handwashing of employees shall be constructed in a location convenient for employees in each manufacturing, processing and preparation area. |  | P/T Only | Yes | Food Premises
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.6.4.(2) | 3.7.6.4. Lavatories, Appliances and Sinks | If equipment and facilities for the cleaning and sanitizing of utensils are provided, they shall consist of, (a) mechanical equipment, or (b) drainage racks of corrosion-resistant materials and, (i) a three-compartment sink or three sinks, or (ii) a two-compartment sink or two sinks, where the first compartment or sink can be used effectively for washing and rinsing and the second compartment or sink can be used effectively for sanitizing. |  | P/T Only | Yes | Food Premises
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.6.5.(1) | 3.7.6.5. Hot and Cold Water Supply | A hot and cold water supply shall be provided to, (a) every plumbing appliance and fixture required by Article 3.7.6.4., (b) every area where food or drink for human consumption, or an ingredient of food or drink for human consumption, is manufactured, processed or prepared, and (c) every area where utensils are washed. |  | P/T Only | Yes | Food Premises
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.6.5.(2) | 3.7.6.5. Hot and Cold Water Supply | This Article does not apply to a retail food premises described in Sentence 3.7.6.4.(3). |  | P/T Only | Yes | Food Premises
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.6.6.(2) | 3.7.6.6. Employee Facilities | Every room containing sanitary units for employees shall have a floor area not less than 2.3 m2. |  | P/T Only | Yes | Food Premises
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.6.6.(1) | 3.7.6.6. Employee Facilities | In a food premises, where dressing rooms are provided for employees, there shall be separate dressing rooms for males and females that, are large enough for the employees to change and store their clothing, and are equipped with lockers or other facilities suitable for storing the clothing of the employees. |  | P/T Only | Yes | Food Premises
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.6.7.(1) | 3.7.6.7. Sleeping Quarters | A room or space intended to be used as sleeping quarters shall not open directly into any room where food or drink for human consumption, or an ingredient of food or drink for human consumption, is manufactured, processed, prepared, stored, displayed, handled, served, distributed, sold or offered for sale. |  | P/T Only | Yes | Food Premises
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.1.2.(2) | 3.8.1.2. Entrances (See Appendix A.) | One of the barrier-free entrances required by Sentence (1) shall be the principal entrance to the building. |  | P/T Only | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.1.3.(6) | 3.8.1.3. Barrier-Free Path of Travel | A normally occupied floor area that is not required by Article 3.8.2.1. to have a barrier-free path of travel shall meet the following requirements: interior walking surfaces throughout the normally occupied floor area shall comply with Clauses (2)(a) to (e), and where the headroom of an area in a corridor or aisle in the normally occupied floor area is reduced to less than 1 980 mm, a guardrail or other barrier with its leading edge at or below 680 mm from the finished floor shall be provided. (See Appendix A.) |  | P/T Only | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.1.3.(5) | 3.8.1.3. Barrier-Free Path of Travel | Where the headroom of an area in a barrier-free path of travel is reduced to less than 1 980 mm, a guardrail or other barrier with its leading edge at or below 680 mm from the finished floor shall be provided. (See Appendix A.) |  | P/T Only | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.1.5.(2) | 3.8.1.5. Controls | A signal intended for the public to indicate the operation of a building security system that controls access to a building shall consist of an audible and visual signal. |  | P/T Only | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.2.1.(2) | 3.8.2.1. Areas Requiring Barrier-Free Path of Travel | A barrier-free path of travel described in Clause (1)(b) is not required to extend, (a) to floor areas or portions of floor areas containing a Group B, Division 2 or 3 occupancy that are not required by Article 3.5.2.1. to be connected by a ramp or served by an elevator, (b) to Group C or Group D occupancies that are in floor areas in a building that, (i) is three or fewer storeys in building height, and (ii) has a building area not exceeding 600 m2, (c) to Group F, Division 2 or 3 occupancies that are not required by Sentence 3.8.2.2.(1) to be served by an elevator, (d) to portions of restaurants and licensed beverage establishments where the same amenities and uses are provided on other floor areas that have a barrier-free path of travel, or (e) to portions of child care facilities that have all entrance doors at floor levels that do not have a barrier-free path of travel. |  | P/T Only | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.2.1.(6) | 3.8.2.1. Areas Requiring Barrier-Free Path of Travel | Bathrooms required by Clause (5)(b) shall, (a) contain a lavatory, (b) contain a water closet, (c) contain a bathtub or a shower, (d) have wall reinforcement installed in conformance with Sentence 3.3.4.9.(1), and (e) be designed to permit a wheelchair to turn in an open space not less than 1 500 mm in diameter. |  | P/T Only | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.2.1.(5) | 3.8.2.1. Areas Requiring Barrier-Free Path of Travel | In a Group C major occupancy apartment building, not less than 15% of all suites of residential occupancy shall be provided with a barrier-free path of travel from the suite entrance door into the following rooms and spaces that shall be located at the same level as the barrier-free path of travel: (a) at least one bedroom, (b) at least one bathroom conforming to Sentence (6), (c) a kitchen or kitchen space, and (d) a living room or space. |  | P/T Only | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.2.1.(7) | 3.8.2.1. Areas Requiring Barrier-Free Path of Travel | The number of suites described in Sentence (5) having 1, 2 or 3 or more bedrooms shall be in proportion to the number of suites of residential occupancy having 1, 2 or 3 or more bedrooms in the remainder of the building. |  | P/T Only | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.2.1.(8) | 3.8.2.1. Areas Requiring Barrier-Free Path of Travel | The suites described in Sentence (5) shall be distributed among storeys that are required by Article 3.8.2.1. to have a barrier-free path of travel, having regard to the height of the suite above grade. |  | P/T Only | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.2.2.(2) | 3.8.2.2. Access to Parking Areas | The vehicular entrance to and egress from at least one parking level described in Sentence (1) and all areas intended to be used by wheelchair accessible vehicles to gain access to a parking space on that level shall have a vertical clearance of not less than 2 100 mm |  | P/T Only | Yes | Accessibility: Other
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.2.3.(2) | 3.8.2.3. Washrooms Required to be Barrier-Free (See Appendix | The number of universal washrooms conforming to Article 3.8.3.12. provided in a building in which a washroom is required by Subsection 3.7.4. shall conform to Table 3.8.2.3.A. (See Appendix A.) |  | P/T Only | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.2.3.(6) | 3.8.2.3. Washrooms Required to be Barrier-Free (See Appendix | Where a washroom required by Subsection 3.7.4. is provided in a storey that is not required by Article 3.8.2.1. to have a barrier-free path of travel, the washroom shall, conform to Article 3.8.3.9. and Sentences 3.8.3.10.(4) and 3.8.3.11.(5), and be provided with at least one ambulatory water closet stall or enclosure conforming to Sentence 3.8.3.8.(10). |  | P/T Only | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.2.3.(3) | 3.8.2.3. Washrooms Required to be Barrier-Free (See Appendix | Where a washroom required by Subsection 3.7.4. is provided in a storey that is required by Article 3.8.2.1. to have a barrier-free path of travel, the washroom shall conform to Articles 3.8.3.8. to 3.8.3.11., and the number of barrier-free water closet stalls or enclosures provided in the washroom shall conform to Table 3.8.2.3.B. |  | P/T Only | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.2.4.(3) | 3.8.2.4. Hotels | A suite having a barrier-free path of travel required by Sentence (1) shall have a bathroom that, (a) conforms to Clauses 3.8.3.12.(1)(a) to (h) and (j), (b) has an unobstructed area at least 1 200 mm in diameter extending the full height of the room, except that a door is permitted to open on the inside if it does not reduce the unobstructed area, and (c) has a bathtub or shower that conforms to Article 3.8.3.13. |  | P/T Only | Yes | Hotels
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.2.4.(5) | 3.8.2.4. Hotels | An entrance door to a suite having a barrier-free path of travel required by Sentence (1) shall have, (a) a power door operator conforming to Article 3.8.3.3., and (b) a door viewer located at a height no higher than 1 100 mm above the finished floor. |  | P/T Only | Yes | Hotels
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.2.4.(1) | 3.8.2.4. Hotels | Except as permitted in Sentence (2), at least 10% of the suites of a hotel shall, (a) have a barrier-free path of travel extending to, (i) the inside of each room, and (ii) a balcony where required by Sentence 3.3.1.7.(2), and (b) be distributed among storeys that are required by Article 3.8.2.1. to have a barrier-free path of travel, having regard to the height of the suite above grade. |  | P/T Only | Yes | Hotels
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.2.4.(4) | 3.8.2.4. Hotels | Except as required by Sentence 3.8.3.3.(17) for power door operator controls, controls for the operation of building services or safety devices, including electrical switches, thermostats and intercom switches, intended to be operated by the occupant and located within a suite having a barrier-free path of travel required by Sentence (1) shall conform to Sentence 3.8.1.5.(1). |  | P/T Only | Yes | Hotels
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.2.4.(2) | 3.8.2.4. Hotels | Not more than 20 suites need comply with Sentence (1). |  | P/T Only | Yes | Hotels
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.2.4.(8) | 3.8.2.4. Hotels | The emergency power receptacle described in Sentence (7) shall be identified with a legible sign having the words EMERGENCY POWER OUTLET permanently mounted on the wall beside the receptacle. |  | P/T Only | Yes | Hotels
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.2.4.(6) | 3.8.2.4. Hotels | Where a door is provided between a suite having a barrier-free path of travel required by Sentence (1) and an adjoining suite, the door shall conform to Sentences 3.8.3.3.(1) and (3). |  | P/T Only | Yes | Hotels
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.2.4.(7) | 3.8.2.4. Hotels | Where an emergency power supply is supplied by a generator, it shall supply at least one emergency power receptacle in at least one of the suites having a barrier-free path of travel required by Sentence (1). (See Appendix A.) |  | P/T Only | Yes | Hotels
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.3.1.(4) | 3.8.3.1. Accessibility Signs (See Appendix A.) | Signs incorporating the International Symbol of Access shall be installed where necessary to indicate the location of a barrier-free means of egress. |  | P/T Only | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.3.1.(5) | 3.8.3.1. Accessibility Signs (See Appendix A.) | Where a wall mounted tactile sign is provided in a building, characters, symbols or pictographs on the sign shall be located not less than 1 200 mm and not more than 1 500 mm above the finished floor. (See Appendix A.) |  | P/T Only | Yes | Accessibility: Other
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.3.1.(6) | 3.8.3.1. Accessibility Signs (See Appendix A.) | Where a wall mounted tactile sign is provided in a storey that is not required by Article 3.8.2.1. to have a barrier-free path of travel, characters, symbols or pictographs on the sign shall conform to Sentence (5). |  | P/T Only | Yes | Accessibility: Other
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.3.10.(4) | 3.8.3.10. Urinals (See Appendix A.) | Where more than one urinal is provided in a washroom described in Sentence 3.8.2.3.(6), at least one urinal conforming to Sentences (1) to (3) shall be provided in the washroom. |  | P/T Only | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.3.10.(3) | 3.8.3.10. Urinals (See Appendix A.) | Where privacy screens are installed for a urinal described in Sentence (1), they shall, (a) be mounted a minimum of 460 mm from the centre line of the urinal, and (b) have a clearance of at least 50 mm from the grab bars required by Clause (2)(b). |  | P/T Only | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.3.11.(5) | 3.8.3.11. Lavatories, Mirrors and Washroom Accessories (See | A washroom described in Sentence 3.8.2.3.(6) shall be provided with a lavatory conforming to Clauses (1)(e), (g) and (h). |  | P/T Only | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.3.11.(3) | 3.8.3.11. Lavatories, Mirrors and Washroom Accessories (See | If dispensing or hand-operated washroom accessories, other than those located in water closet stalls or enclosures and those described in Clause (1)(g), are provided, they shall be mounted so that, the dispensing height is not less than 900 mm and not more than 1 200 mm above the finished floor, the controls or operating mechanisms are mounted not less than 900 mm and not more than 1 200 mm above the finished floor, and a minimum 1 370 mm deep floor space is provided in front of the controls or operating mechanisms to allow for a front approach. |  | P/T Only | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.3.12.(3) | 3.8.3.12. Universal Washrooms | A clear space not less than 810 mm wide and 1 830 mm long shall be provided in each universal washroom for an adult-size change table. |  | P/T Only | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.3.12.(6) | 3.8.3.12. Universal Washrooms | A universal washroom need not conform to Sentences (3) and (4) if, (a) it is located in an individual suite that, (i) is used for an assembly occupancy, a business and personal services occupancy, a mercantile occupancy or an industrial occupancy, and (ii) meets one of the following requirements, (A) it is located in a building that is less than 300 m2 in building area, or (B) it is less than 300 m2 in area, if located in a building that is at least 300 m2 in building area, or (b) another universal washroom conforming to this Article is provided on the same floor level within 45 m. |  | P/T Only | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.3.12.(2) | 3.8.3.12. Universal Washrooms | A universal washroom shall have, an emergency call system that consists of audible and visual signal devices inside and outside of the washroom that are activated by a control device inside the washroom, and an emergency sign that contains the words IN THE EVENT OF AN EMERGENCY PUSH EMERGENCY BUTTON AND AUDIBLE AND VISUAL SIGNAL WILL ACTIVATE in letters at least 25 mm high with a 5 mm stroke and that is posted above the emergency button. |  | P/T Only | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.3.12.(5) | 3.8.3.12. Universal Washrooms | Where an adult-size change table is installed, it shall, (a) when fully loaded, have a surface height above the finished floor that can be adjusted from between 450 mm and 500 mm at the low range to between 850 mm and 900 mm at the high range, (b) be designed to carry a minimum load of 1.33 kN, (c) have a clear floor space parallel to the long side of the table not less than 760 mm wide and 1 500 mm long, and (d) in the case of a fold-down table, (i) be installed so that it does not encroach into a clear transfer space described in Clause 3.8.3.8.(2)(a) or (b), and (ii) have no operating mechanisms higher than 1 200 mm. |  | P/T Only | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.3.12.(4) | 3.8.3.12. Universal Washrooms | Where the clear space provided for an adult-size change table is adjacent to a wall, reinforcement shall be installed in the wall to permit the future installation of the change table. |  | P/T Only | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.3.13.(2) | 3.8.3.13. Showers and Bathtubs | All other controls installed in a shower described in Sentence (2) shall comply with Subclauses (2)(h)(i) to (iii). |  | P/T Only | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.3.13.(4) | 3.8.3.13. Showers and Bathtubs | Individual bathtubs that are provided for the use of patients or residents in buildings of Group B, Division 2 or 3 occupancy shall, (a) be located in a room with a clear floor space not less than 1 500 mm in diameter, (b) be not less than 1 500 mm long, (c) be capable of being accessed along the full length of the bathtub with no tracks mounted on the bathtub rim, (d) have faucets that, (i) are operable using a closed fist and with a force of not more than 22.2 N, and (ii) are located on the centre line of the bathtub or between the centre line of the bathtub and the exterior edge of the bathtub rim, at a maximum height of 450 mm above the rim, (e) unless the bathtub is free-standing, have three grab bars, (i) conforming to Sentence 3.8.3.8.(7), (ii) that are not less than 1 200 mm long, (iii) two of which are located vertically at each end of the bathtub, mounted between 80 mm and 280 mm above the bathtub rim, and (iv) one of which is located horizontally along the full length of the bathtub, mounted between 80 mm and 280 mm above the bathtub rim, (f) have a slip-resistant bottom surface, and (g) be equipped with a hand-held shower head with not less than 1 800 mm of flexible hose that can be used in a fixed position at a height of 1 200 mm and 2 030 mm and does not obstruct the use of the grab bars. |  | P/T Only | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.3.13.(3) | 3.8.3.13. Showers and Bathtubs | Individual showers that are provided for use by patients or residents in buildings of Group B, Division 2 or 3 occupancy shall conform to Sentence (2). |  | P/T Only | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.3.13.(5) | 3.8.3.13. Showers and Bathtubs | Where a barrier-free bathtub is provided, a clear floor space at least 900 mm wide and 1 500 mm long shall be provided along the full length of the bathtub |  | P/T Only | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.3.15.(5) | 3.8.3.15. Shelves or Counters for Telephones (See Appendix | Where more than one telephone is provided for public use in a normally occupied floor area that is not required by Article 3.8.2.1. to have a barrier-free path of travel, a built-in shelf or counter that conforms to Sentences (2), (3) and (4) shall be provided for at least one telephone. |  | P/T Only | Yes | Accessibility: Other
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.3.16.(4) | 3.8.3.16. Drinking Fountains (See Appendix A.) | Where more than one drinking fountain is provided in a normally occupied floor area that is not required by Article 3.8.2.1. to have a barrier-free path of travel, at least one shall be a barrier-free fountain that conforms to Sentences (2) and (3). |  | P/T Only | Yes | Accessibility: Other
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.3.17.(1) | 3.8.3.17. Platforms | A tactile attention indicator conforming to Article 3.8.3.18. shall be installed along any edge of a platform that is, not protected by a guard, and higher than 250 mm above the finished floor or ground or sloped steeper than 1 in 3. |  | P/T Only | Yes | Accessibility: Other
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.3.17.(2) | 3.8.3.17. Platforms | Sentence (1) does not apply to the front edges of stages. |  | P/T Only | Yes | Accessibility: Other
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.3.18.(2) | 3.8.3.18. Tactile Attention Indicators | The depth of the tactile attention indicator shall be not less than 300 mm and not more than 610 mm. |  | P/T Only | Yes | Accessibility: Other
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.3.18.(1) | 3.8.3.18. Tactile Attention Indicators | Where a tactile attention indicator is required, it shall conform to Sentence (2) and Clauses 4.1.1. and 4.1.2. of ISO 23599, "Assistive Products for Blind and Vision-Impaired Persons Ã¢â‚¬" Tactile Walking Surface Indicators". |  | P/T Only | Yes | Accessibility: Other
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.3.2.(4) | 3.8.3.2. Exterior Walks | Curb ramps described in Sentence (3) do not require handrails or guards |  | P/T Only | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.3.2.(3) | 3.8.3.2. Exterior Walks | The curb ramp permitted by Sentence (2) shall, (a) have a running slope conforming to Table 3.8.3.2., (b) have a width of not less than 1 500 mm exclusive of flared sides, (c) have a surface including flared sides that shall, (i) be slip-resistant, (ii) have a detectable warning surface that is colour- and texture-contrasted with the adjacent surfaces, and (iii) have a smooth transition from the ramp and adjacent surfaces, and (d) have flared sides with a slope of not more than 1:10 where pedestrians are likely to walk across them. |  | P/T Only | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.3.2.(2) | 3.8.3.2. Exterior Walks | Where a difference in elevation between levels in a walkway is not more than 200 mm, a curb ramp conforming to Sentences (3) and (4) may be provided. |  | P/T Only | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.3.3.(6) | 3.8.3.3. Doorways and Doors | A door shall be equipped with a power door operator where the door serves, (a) a washroom for public use required to be barrier-free, or (b) a Group A occupancy within a Group C major occupancy apartment building. |  | P/T Only | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.3.3.(19) | 3.8.3.3. Doorways and Doors | A normally occupied floor area that is not required by Article 3.8.2.1. to have a barrier-free path of travel shall comply with the following requirements: (a) all doorways in public corridors in the normally occupied floor area shall comply with Sentence (1), (b) door opening devices that are the only means of operation on doors in the normally occupied floor area shall comply with Sentence (3), (c) where a vision panel is provided in a door in the normally occupied floor area, the panel shall comply with Sentence (14), (d) doors consisting of a sheet of glass in the normally occupied floor area shall comply with Sentence (15), and (e) where a power door operator is installed for doors in the normally occupied floor area, the control for the power door operator shall comply with Sentence (17). |  | P/T Only | Yes | Accessibility: Other
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.3.3.(18) | 3.8.3.3. Doorways and Doors | A proximity scanning device that activates a power door shall be capable of detecting a person in a wheelchair. |  | P/T Only | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.3.3.(5) | 3.8.3.3. Doorways and Doors | Except as permitted by Sentence (12), where a barrier-free entrance required by Article 3.8.1.2. incorporates a vestibule, a door leading from the vestibule into the floor area shall be equipped with a power door operator in a building containing a Group A, Group B, Division 2 or 3, Group C, Group D of Group E occupancy. |  | P/T Only | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.3.3.(14) | 3.8.3.3. Doorways and Doors | Where a vision panel is provided in a door in a barrier-free path of travel, such panel shall be at least 75 mm in width and be located so that, the bottom of the panel is not more than 900 mm above the finished floor, and the edge of the panel closest to the latch is not more than 250 mm from the latch side of the door. |  | P/T Only | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.3.6.(2) | 3.8.3.6. Wheelchair Spaces and Adaptable Seating | Fixed seats designated for adaptable seating required by Sentence 3.8.2.1.(4) shall be, (a) located adjoining a barrier-free path of travel without infringing on egress from any row of seating or any aisle requirements, (b) equipped with a movable or removable armrest on the side of the seat adjoining the barrier-free path of travel, and (c) situated, as part of the designated seating plan, to provide a choice of viewing location and a clear view of the event taking place. |  | P/T Only | Yes | Accessibility: Other
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.3.6.(3) | 3.8.3.6. Wheelchair Spaces and Adaptable Seating | In an assembly occupancy with fixed seats, space shall be provided for the storage of wheelchairs and mobility assistive devices in accordance with the following requirements: (a) at least one storage space not less than 810 mm by 1 370 mm shall be provided where the assembly occupancy has not more than 200 fixed seats and at least two such storage spaces shall be provided where the assembly occupancy has more than 200 fixed seats, and (b) the storage space or spaces shall be located on the same level and in proximity to the spaces designated for wheelchair use and seats designated for adaptable seating. |  | P/T Only | Yes | Accessibility: Other
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.3.8.(9) | 3.8.3.8. Water Closet Stalls and Enclosures | A fold-down grab bar installed in accordance with Sentence (8) is permitted to encroach into, (a) the clear turning space described in Clause (1)(a), or (b) a clear transfer space described in Subclause (2)(a)(ii) or Clause (2)(b). |  | P/T Only | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.3.8.(5) | 3.8.3.8. Water Closet Stalls and Enclosures | A grab bar described in Clause (3)(a) shall, be continuous L-shaped with 750 mm long horizontal and vertical components, and be wall mounted with the horizontal component 750 mm above the finished floor and the vertical component 150 mm in front of the water closet. (See A-3.8.3.8.(3) and A-3.8.3.8.(5) in Appendix A.) |  | P/T Only | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.3.8.(6) | 3.8.3.8. Water Closet Stalls and Enclosures | A grab bar described in Clause (3)(c) or (4)(b) shall, be at least 600 mm in length, and be wall mounted horizontally from 840 mm to 920 mm above the finished floor and, where the water closet has a water tank, be wall mounted 150 mm above the tank. |  | P/T Only | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.3.8.(3) | 3.8.3.8. Water Closet Stalls and Enclosures | Where a water closet is located in accordance with Clause (2)(a), a grab bar conforming to Sentences (5) and (7) shall be provided on the side wall referred to in Subclause (2)(a)(i), a fold-down grab bar may be provided and, if one is provided, it shall conform to Sentence (8) and be provided on the side of the water closet opposite the grab bar described in Clause (a), and a grab bar conforming to Sentences (6) and (7) shall be provided on the wall behind the water closet. |  | P/T Only | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.3.8.(4) | 3.8.3.8. Water Closet Stalls and Enclosures | Where a water closet is located in accordance with Clause (2)(b), a fold-down grab bar conforming to Sentence (8) shall be provided on each side of the water closet, and a grab bar conforming to Sentences (6) and (7) shall be provided on the wall behind the water closet. |  | P/T Only | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.3.8.(10) | 3.8.3.8. Water Closet Stalls and Enclosures | Where an ambulatory water closet stall or enclosure is required by Sentence 3.8.2.3.(6), it shall, be at least 1 500 mm in depth and be not less than 890 mm and not more than 940 mm in width, be equipped with a door that shall, be capable of being latched from the inside with a mechanism that is operable using a closed fist, when the door is in an open position, have a clear opening of at least 810 mm, swing outward, unless the minimum dimensions in Clause (a) are not located within the door swing, be provided with spring-type or gravity hinges so that the door closes automatically, be provided with a door pull on both sides of the door, near the latch side of the door, located at a height not less than 900 mm and not more than 1 100 mm above the finished floor, and be capable of having the latch required by Subclause (i) released from the outside in the case of an emergency, be equipped with a water closet conforming to Article 3.8.3.9. and located so that its centre line is centred between the partition walls, be equipped on each side of the water closet with grab bars conforming to Clause (3)(a), and be equipped with a coat hook conforming to Clause (1)(e). |  | P/T Only | Yes | Accessibility: Washrooms
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.6.1.(1) | Application | The requirements of this Subsection apply to all food premises. |  | P/T Only | Yes | Food Premises
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.2.2.4.(3) | Buildings with Multiple Major Occupancies | For the purposes of Sentences (1) and (2), a retirement home is deemed to be a separate major occupancy. |  | P/T Only | Yes | Retirement Homes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.8.1.6.(1) | Illumination | All portions of a barrier-free path of travel shall be equipped to provide a level of illumination in accordance with Sentence 3.2.7.1.(1). |  | P/T Only | Yes | Accessibility: Barrier-Free Path of Travel
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.9 | Portable Classrooms | OBC only Section with 19 Sentences. |  | P/T Only | Yes | Portable Classrooms
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.6.2.(2) | Room Finishes | Carpeting may be used in areas where food is served. |  | P/T Only | Yes | Food Premises
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.7.6.2.(1) | Room Finishes | Except as provided in Sentence (2), floors and floor coverings shall be tight, smooth and non-absorbent in rooms where, (a) food or drink for human consumption, or an ingredient of food or drink for human consumption, is manufactured, processed, prepared, stored, displayed, handled, served, distributed, sold or offered for sale, (b) utensils are washed, or (c) washing fixtures or toilet fixtures are located. |  | P/T Only | Yes | Food Premises
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.6.2.9.(1) | Storage of Oxygen Containers | In a Group B, Division 2 or 3 occupancy or in a retirement home, a room for the storage of oxygen containers shall be, (a) separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h, (b) designed for the storage of oxygen containers only, (c) vapour tight, (d) lined with noncombustible finish, (e) separately exhausted to the exterior, and (f) equipped with racks to store the containers. |  | P/T Only | Yes | Fire Containment
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.4.9.(1) | Stud Wall Reinforcement | If wood wall studs or sheet steel wall studs enclose the main bathroom in a dwelling unit, reinforcement shall be installed to permit the future installation of the following: (a) for a water closet, a grab bar described in Clauses 3.8.3.8.(3)(a) and a grab bar described in Clause 3.8.3.8.(3)(c), (b) for a shower, grab bars described in Clause 3.8.3.13.(2)(g), and (c) for a bathtub, grab bars described in Clause 3.8.3.13.(4)(e). |  | P/T Only | Yes | Dwelling Units
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.4.6.8.(6) | 3.4.6.8. Treads and Risers | Reserved |  | P/T Only | No
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.3.2.3.(6) | 3.3.2.3. Fixed Seats | Seating arrangements that do not conform to the requirements of Sentences (3) to (5) are permitted provided the standard of safety is not reduced and the time required for egress is not increased. |  | P/T Only | Yes | Assembly Seating