## CCT Codes Comparison Import ON
Code Year | Province/Territory | Code Book | National Division | NationalSentenceNumber | National Article Title | National Sentence Text | P/T Document | P/T Division | P/TSentenceNumber | P/T Article Title | P/T Sentence Text | Difference Type | Variation | Variation Label | Text Difference Tracked | Exception | Comments | Difference Type Updated | Exception Updated | Variation Updated
2015 | ON | NBC | Div B | 3.6.5.1.(1) | Duct Materials | Except as permitted by Sentences (2) to (5) and Article 3.6.4.3., all ducts, duct connectors, associated fittings and plenums used in air duct systems shall be constructed of steel, aluminum alloy, copper, clay or other noncombustible material. | obc2019_divb | Div B | 6.2.3.2.(1) | 6.2.3.2. Materials in Air Duct Systems | Except as provided in Sentences (2) to (4) and in Article 3.6.4.3., all ducts, duct connectors, associated fittings and plenums used in air duct systems shall be constructed of steel, aluminum alloy, copper, clay or similar noncombustible material. | Common Sentence | No | Air Duct Systems
2015 | ON | NBC | Div B | 3.6.5.1.(2) | Duct Materials | Except as permitted by Sentence (3), ducts, associated fittings and plenums are permitted to contain combustible material provided they a) conform to the appropriate requirements for Class 1 duct materials in CAN/ULC-S110, “Test for Air Ducts,” b) conform to Article 3.1.5.18. in a building required to be of noncombustible construction, c) conform to Subsection 3.1.9., d) are used only in horizontal runs in a building required to be of noncombustible construction, e) are not used in vertical runs serving more than 2 storeys in a building permitted to be of combustible construction, and f) are not used in air duct systems in which the air temperature could be more than 120°C. | obc2019_divb | Div B | 6.2.3.2.(2) | 6.2.3.2. Materials in Air Duct Systems | Ducts, associated fittings and plenums are permitted to contain combustible material provided they, (a) conform to the appropriate requirements for Class 1 duct materials in CAN/ULC-S110, “Test for Air Ducts”, (b) conform to Article 3.1.5.15. in a building required to be of noncombustible construction, (c)conform to Subsection 3.1.9., (d)are used only in horizontal runs in a building required to be of noncombustible construction, (e)are not used in vertical runs serving more than 2 storeys in a building required to be of noncombustible construction, and (f)are not used in air duct systems in which the air temperature may exceed 120°C. | Common Sentence | No | Air Duct Systems
2015 | ON | NBC | Div B | 3.6.5.1.(4) | Duct Materials | Duct sealants shall have a flame-spread rating not more than 25 and a smoke developed classification not more than 50 | obc2019_divb | Div B | 6.2.3.2.(3) | 6.2.3.2. Materials in Air Duct Systems | Duct sealants shall have a flame-spread rating of not more than 25 and a smoke developed classification of not more than 50. | Common Sentence | No | Air Duct Systems
2015 | ON | NBC | Div B | 3.6.5.1.(5) | Duct Materials | Duct connectors that contain combustible materials and that are used between ducts and air outlet units shall a) conform to the appropriate requirements for Class 1 air duct materials in CAN/ULC-S110, “Test for Air Ducts,” b) be not more than 4 m long, c) be used only in horizontal runs, and d) not penetrate a required fire separation. | obc2019_divb | Div B | 6.2.3.2.(4) | 6.2.3.2. Materials in Air Duct Systems | Duct connectors that contain combustible materials and that are used between ducts and air outlet units shall, (a) conform to the appropriate requirements for Class 1 air duct materials in CAN/ULC-S110, “Test for Air Ducts”, (b) be limited to 4 m in length, (c) be used only in horizontal runs, and (d) not penetrate required fire separations. | Common Sentence | No | Air Duct Systems
2015 | ON | NBC | Div B | 3.6.5.4.(1) | Coverings, Linings, Adhesives and Insulation | Coverings, linings and associated adhesives and insulation for air ducts, plenums and other parts of air duct systems that would have an exposed surface temperature more than 120°C when exposed to heated air or radiation from heat sources shall be of noncombustible material. | obc2019_divb | Div B | 6.2.3.4.(1) | 6.2.3.4. Duct Coverings, Linings, Adhesives and Insulation | Coverings, linings and associated adhesives and insulation of air ducts, plenums and other parts of air duct systems shall be of noncombustible material when exposed to heated air or radiation from heat sources that would result in the exposed surface exceeding a temperature of 120°C. | Common Sentence | No | Air Duct Systems
2015 | ON | NBC | Div B | 3.6.5.4.(2) | Coverings, Linings, Adhesives and Insulation | Except as permitted by Sentence (3), combustible coverings and linings, including associated adhesives and insulation, shall have a) a flame-spread rating not more than 25 on any exposed surface or any surface that would be exposed by cutting through the material in any direction, and b) a smoke developed classification not more than 50. | obc2019_divb | Div B | 6.2.3.4.(2) | 6.2.3.4. Duct Coverings, Linings, Adhesives and Insulation | When combustible coverings and linings, including associated adhesives and insulation, are used, they shall have a flame-spread rating of not more than 25 on any exposed surface or any surface that would be exposed by cutting through the material in any direction, and a smoke developed classification of not more than 50, except that the outer covering of ducts, plenums and other parts of air duct systems used within an assembly of combustible construction may have an exposed surface flame-spread rating of not more than 75 and may have a smoke developed classification greater than 50. 6.2.3.5.(2) | Common Sentence | No | Air Duct Systems
2015 | ON | NBC | Div B | 3.6.5.4.(4) | Coverings, Linings, Adhesives and Insulation | Combustible coverings and linings referred to in Sentences (2) and (3) shall not flame, glow, smoulder or smoke when tested in accordance with the method of test in ASTM C 411, “Hot-Surface Performance of High-Temperature Thermal Insulation,” at the maximum temperature to which the coverings and linings are to be exposed in service. | obc2019_divb | Div B | 6.2.3.4.(3) | 6.2.3.4. Duct Coverings, Linings, Adhesives and Insulation | Combustible coverings and linings in Sentence (2) shall not flame, glow, smoulder or smoke when tested in accordance with the method of test in ASTM C411, "Hot-Surface Performance of High-Temperature Thermal Insulation" at the maximum temperature to which the coverings and linings are to be exposed in service. 6.2.3.5.(3) | Common Sentence | No | Air Duct Systems
2015 | ON | NBC | Div B | 3.6.5.4.(5) | Coverings, Linings, Adhesives and Insulation | 5) Except as permitted by Sentence (6), foamed plastic insulation shall not be used as part of an air duct system or for insulating an air duct. | obc2019_divb | Div B | 6.2.3.4.(4) | 6.2.3.4. Duct Coverings, Linings, Adhesives and Insulation | Except as provided in Sentence (5), foamed plastic insulation shall not be used as part of an air duct or for insulating an air duct. 6.2.3.5.(4) | Common Sentence | No | Air Duct Systems
2015 | ON | NBC | Div B | 3.6.5.4.(7) | Coverings, Linings, Adhesives and Insulation | Combustible coverings and linings of ducts, including associated adhesives and insulation, shall be interrupted where the duct penetrates a fire separation and at the immediate area of operation of heat sources in a duct system, including electric resistance heaters or fuel-burning heaters or furnaces. | obc2019_divb | Div B | 6.2.3.4.(6) | 6.2.3.4. Duct Coverings, Linings, Adhesives and Insulation | Combustible coverings and linings of ducts, including associated adhesives and insulation, shall be interrupted at the immediate area of operation of heat sources in a duct system, such as electric resistance heaters or fuel-burning heaters or furnaces, and where the duct penetrates a fire separation. | Common Sentence | Yes | Air Duct Systems
2015 | ON | NBC | Div B | 3.6.5.5.(1) | Insulation and Coverings | 1) Insulation and coverings on pipes in which the temperature of the fluid exceeds 120°C shall a) be made of noncombustible material, or b) not flame, glow, smoulder or smoke when tested in accordance with ASTM C 411, “Hot-Surface Performance of High-Temperature Thermal Insulation,” at the maximum temperature to which the insulation or covering is to be exposed in service. | obc2019_divb | Div B | 6.2.9.2.(2) | 6.2.9.2. Insulation and Coverings | Insulation and coverings on pipes in which the temperature of the fluid exceeds 120°C,(a) shall be made of noncombustible material, or (b) shall not flame, glow, smoulder or smoke when tested in accordance with ASTM C411, "Hot-Surface Performance of High-Temperature Thermal Insulation", at the maximum temperature to which such insulation or covering is to be exposed in service. | Common Sentence | No | Piping for Heating and Cooling Systems
2015 | ON | NBC | Div B | 3.6.5.5.(2) | Insulation and Coverings | Except as permitted by Sentence (5), where combustible insulation is used on piping in a horizontal service space or a vertical service space, the insulation and coverings on that piping shall have a flame-spread rating, on any exposed surface and on any surface that would be exposed by cutting through the material in any direction, a) not more than 25 in a building required to be of noncombustible construction, or b) not more than 75 in a building permitted to be of combustible construction. | obc2019_divb | Div B | 6.2.9.2.(3) | 6.2.9.2. Insulation and Coverings | Except as provided in Sentence (7), where combustible insulation is used on piping in a horizontal or vertical service space, the insulation and coverings on such pipes shall have a flame-spread rating throughout the material of not more than 25 in buildings of noncombustible construction and not more than 75 in buildings of combustible construction. | Common Sentence | Yes | Piping for Heating and Cooling Systems
2015 | ON | NBC | Div B | 3.6.5.5.(3) | Insulation and Coverings | Except as permitted by Sentence (5), insulation and coverings on piping located in rooms and spaces other than the service spaces described in Sentence (2) shall have a flame-spread rating not more than that required for the interior finish of the ceiling of the room or space. | obc2019_divb | Div B | 6.2.9.2.(4) | 6.2.9.2. Insulation and Coverings | Except as provided in Sentence (7), insulation and coverings on piping located in rooms and spaces other than the service spaces described in Sentence (3) shall have a flame-spread rating of not more than that required for the interior finish for the ceiling of the room or space. | Common Sentence | No | Piping for Heating and Cooling Systems
2015 | ON | NBC | Div B | 3.6.5.5.(4) | Insulation and Coverings | Except as permitted by Sentence (5), combustible insulation and covering used on piping in a building within the scope of Subsection 3.2.6. shall have a smoke developed classification not more than 100. | obc2019_divb | Div B | 6.2.9.2.(5) | 6.2.9.2. Insulation and Coverings | Except as provided in Sentence (7), where combustible insulation and covering is used on piping in buildings described in Subsection 3.2.6., they shall have a smoke developed classification of not more than 100. | Common Sentence | No | Piping for Heating and Cooling Systems
2015 | ON | NBC | Div B | 3.6.5.5.(5) | Insulation and Coverings | No flame-spread rating or smoke developed classification limits are required for combustible insulation and coverings used on piping located within a a) concealed space in a wall, b) floor slab, or c) noncombustible enclosure. | obc2019_divb | Div B | 6.2.9.2.(7) | 6.2.9.2. Insulation and Coverings | No flame-spread rating or smoke developed classification limitations are required where combustible insulation and coverings are used on piping when such piping is, (a) located within a concealed space in a wall, (b) located in a floor slab, or (c) enclosed in a noncombustible raceway or conduit. | Common Sentence | No | Piping for Heating and Cooling Systems
2015 | ON | NBC | Div B | 3.6.5.8.(1) | Return-Air System | Except as required by Sentences 3.6.5.8.(2)and 3.6.5.8.(3), return ducts shall be constructed of material having a flame-spread rating not more than 150. | obc2019_divb | Div B | 6.2.4.7.(2) | 6.2.4.7. Return-Air System | Except as provided in Sentences (3) and (4), return ducts shall be constructed of material having a surface flame-spread rating of not more than 150. | Common Sentence | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 4.1.1.3.(1) | Design Requirements | Buildings and their structural members and connections, including formwork and falsework, shall be designed to have sufficient structural capacity and structural integrity to safely and effectively resist all loads, effects of loads and influences that may reasonably be expected, having regard to the expected service life of buildings, and shall in any case satisfy the requirements of this Section. (See Note A-4.1.1.3.(1).) | obc2019_divb | Div B | 4.1.1.3.(1) | 4.1.1.3. Design Requirements | Buildings and their structural members and connections including formwork and falsework shall be designed to have sufficient structural capacity and structural integrity to safely and effectively resist all loads, effects of loads and influences that may reasonably be expected, having regard to the expected service life of buildings, and shall in any case satisfy the requirements of this Section. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.1.3.(2) | Design Requirements | Buildings and their structural members shall be designed for serviceability, in accordance with Articles 4.1.3.4. , 4.1.3.5. and 4.1.3.6. (See Note A-4.1.1.3.(2).) | obc2019_divb | Div B | 4.1.1.3.(2) | 4.1.1.3. Design Requirements | Buildings and their structural members shall be designed for serviceability, in accordance with Articles 4.1.3.4. to 4.1.3.6. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.1.3.(3) | Design Requirements | All permanent and temporary structural members, including the formwork and falsework of a building, shall be protected against loads exceeding the specified loads during the construction period except when, as verified by analysis or test, temporary overloading of a structural member would result in no impairment of that member or any other member. | obc2019_divb | Div B | 4.1.1.3.(3) | 4.1.1.3. Design Requirements | All permanent and temporary structural members, including formwork and falsework of a building, shall be protected against loads exceeding the specified loads during the construction period except when, as verified by analysis or test, temporary overloading of a structural member would result in no impairment of that member or any other member. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.1.3.(5) | Design Requirements | Precautions shall be taken during all phases of construction to ensure that the building is not damaged or distorted due to loads applied during construction. | obc2019_divb | Div B | 4.1.1.3.(4) | 4.1.1.3. Design Requirements | Precautions shall be taken during all stages of construction to ensure that the building is not damaged or distorted due to loads applied during construction. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.1.5.(1) | Design Basis | Except as provided in Sentence (2), buildings and their structural members shall be designed in conformance with the procedures and practices provided in this Part. | obc2019_divb | Div B | 4.1.1.4.(1) | 4.1.1.4. Design Basis | Except as provided in Sentence (2), buildings and their structural members shall be designed in conformance with the procedures and practices provided in this Part. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.1.5.(2) | Design Basis | Provided the design is carried out by a person especially qualified in the specific methods applied and provided the design demonstrates a level of safety and performance in accordance with the requirements of Part 4, buildings and their structural components falling within the scope of Part 4 that are not amenable to analysis using a generally established theory may be designed by a) evaluation of a full-scale structure or a prototype by a loading test, or b) studies of model analogues. (See Note A-4.1.1.5.(2).) | obc2019_divb | Div B | 4.1.1.4.(2) | 4.1.1.4. Design Basis | Provided the design is carried out by a person especially qualified in the specific methods applied and provided the design demonstrates a level of safety and performance in accordance with the requirements of this Part, buildings and their structural components falling within the scope of this Part that are not amenable to analysis using a generally established theory may be designed by, (a) evaluation of a full-scale structure or a prototype by a loading test, or (b) studies of model analogues. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.2.1.(1) | Loads and Effects | Except as provided in Article 4.1.2.2., the following categories of loads, specified loads and effects shall be taken into consideration in the design of a building and its structural members and connections: D ................... dead load –a permanent load due to the weight of building components, as specified in Subsection 4.1.4., E ................... earthquake load and effects – a rare load due to an earthquake, as specified in Subsection 4.1.8., H ................... a permanent load due to lateral earth pressure, including groundwater, L ................... live load –a variable load due to intended use and occupancy (including loads due to cranes and the pressure of liquids in containers), as specified in Subsection 4.1.5., LXC ................ live load exclusive of crane loads, C ................... live load due to cranes including self weight, Cd ................. self weight of all cranes positioned for maximum effects, C7 .................. crane bumper impact load, P ................... permanent effects caused by pre-stress, S ................... variable load due to snow, including ice and associated rain, as specified in Article 4.1.6.2., or due to rain, as specified in Article 4.1.6.4., T ................... effects due to contraction, expansion, or deflection caused by temperature changes, shrinkage, moisture changes, creep, ground settlement, or a combination thereof (see Note A-4.1.2.1.(1)),and W .................. wind load – a variable load due to wind, as specified in Subsection 4.1.7., where a) load means the imposed deformations (i.e. deflections, displacements or motions that induce deformations and forces in the structure),forces and pressures applied to the building structure, b) permanent load is a load that changes very little once it has been applied to the structure, except during repair, c) variable load is a load that frequently changes in magnitude, direction or location, and d) rare load is a load that occurs infrequently and for a short time only. | obc2019_divb | Div B | 4.1.2.1.(1) | 4.1.2.1. Loads and Effects | Except as provided in Article 4.1.2.2., the categories of loads, specified loads and effects set out in Table 4.1.2.1.A. shall be taken into consideration in the design of a building and its structural members and connections. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.2.1.(2) | Loads and Effects | Minimum specified values of the loads described in Sentence (1), as set forth in Subsections 4.1.4.to 4.1.8.,shall be increased to account for dynamic effects where applicable. | obc2019_divb | Div B | 4.1.2.1.(2) | 4.1.2.1. Loads and Effects | Minimum specified values of the loads described in Sentence (1), as set forth in Subsections 4.1.4. to 4.1.8., shall be increased to account for dynamic effects where applicable. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.2.1.(3) | Loads and Effects | For the purpose of determining specified loads S, W or E in Subsections 4.1.6., 4.1.7.and 4.1.8., buildings shall beassigned an Importance Category based on intended use and occupancy,in accordance with Table 4.1.2.1.(See Note A-4.1.2.1.(3).) | obc2019_divb | Div B | 4.1.2.1.(3) | 4.1.2.1. Loads and Effects | For the purpose of determining specified loads S, W or E in Subsections 4.1.6. to 4.1.8., buildings shall be assigned an Importance Category based on intended use and occupancy, in accordance with Table 4.1.2.1.B. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.2.2.(1) | Load Not Listed | Where a building or structural member can be expected to be subjected to loads, forces or other effects not listed in Article 4.1.2.1., such effects shall be taken into account in the design based on the most appropriate information available. | obc2019_divb | Div B | 4.1.2.2.(1) | 4.1.2.2 Load Not Listed | Where a building or structural member can be expected to be subjected to loads, forces or other effects not listed in Article 4.1.2.1., such effects shall be taken into account in the design based on the most appropriate information available. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.3.1.(1) | Definitions | In this Subsection, the term limit states means those conditions of a building structure that result in the building ceasing to fulfill the function for which it was designed (those limit states concerning safety are called ultimate limit states (ULS) and include exceeding the load-carrying capacity, overturning, sliding and fracture; those limit states that restrict the intended use and occupancy of the building are called serviceability limit states (SLS) and include deflection, vibration, permanent deformation and local structural damage such as cracking; and those limit states that represent failure under repeated loading are called fatigue limit states), specified loads (C, D, E, H, L, P, S, T and W) means those loads defined in Article 4.1.2.1., principal load means the specified variable load or rare load that dominates in a given load combination, companion load means a specified variable load that accompanies the principal load in a given load combination, service load means a specified load used for the evaluation of a serviceability limit state, principal-load factor means a factor applied to the principal load in a load combination to account for the variability of the load and load pattern and the analysis of its effects, companion-load factor means a factor that, when applied to a companion load in the load combination, gives the probable magnitude of a companion load acting simultaneously with the factored principal load, importance factor, I, means a factor applied in Subsections 4. , 4. and 4. to obtain the specified load and take into account the consequences of failure as related to the limit state and the use and occupancy of the building, factored load means the product of a specified load and its principal-load factor or companion-load factor, effects refers to forces, moments, deformations or vibrations that occur in the structure, nominal resistance, R, of a member, connection or structure, is based on the geometry and on the specified properties of the structural materials, resistance factor, ?, means a factor applied to a specified material property or to the resistance of a member, connection or structure, and that, for the limit state under consideration, takes into account the variability of dimensions and material properties, workmanship, type of failure and uncertainty in the prediction of resistance, and factored resistance, ?R, means the product of nominal resistance and the applicable resistance factor. | obc2019_divb | Div B | 4.1.3.1.(1) | 4.1.3.1. Definitions | In this Part, the term, (a) "limit states" means those conditions of a building structure that result in the building ceasing to fulfill the function for which it was designed. (Those limit states concerning safety are called ultimate limit states (ULS) and include exceeding the load-carrying capacity, overturning, sliding and fracture; those limit states that restrict the intended use and occupancy of the building are called serviceability limit states (SLS) and include deflection, vibration, permanent deformation and local structural damage such as cracking; and those limit states that represent failure under repeated loading are called fatigue limit states), (b) "specified loads (C, D, E, H, L, P, S, T and W)" mean those loads set out in Table 4.1.2.1.A., (c) "principal load" means the specified variable load or rare load that dominates in a given load combination, (d) "companion load" means a specified variable load that accompanies the principal load in a given load combination, (e) "service load" means a specified load used for the evaluation of a serviceability limit state, (f) "principal-load factor" means a factor applied to the principal load in a load combination to account for the variability of the load and load pattern and the analysis of its effects, (g) "companion-load factor" means a factor that, when applied to a companion load in the load combination, gives the probable magnitude of a companion load acting simultaneously with the factored principal load, (h) "importance factor, I," means a factor applied in Subsections 4.1.6. to 4.1.8. to obtain the specified load and take into account the consequences of failure as related to the limit state and the use and occupancy of the building, (i) "factored load" means the product of a specified load and its principal-load factor or companion-load factor, (j) "effects" refers to forces, moments, deformations or vibrations that occur in the structure, (k) "nominal resistance, R," of a member, connection or structure, is based on the geometry and on the specified properties of the structural materials, (l) "resistance factor, ÃŽÂ¦," means a factor applied to a specified material property or to the resistance of a member, connection or structure, and that, for the limit state under consideration, takes into account the variability of dimensions and material properties, workmanship, type of failure and uncertainty in the prediction of resistance, and (m) "factored resistance, ÃŽÂ¦R," means the product of nominal resistance and the applicable resistance factor. | Common Sentence | Yes | Limit States Design
2015 | ON | NBC | Div B | 4.1.3.2.(1) | Strength and Stability | A building and its structural components shall be designed to have sufficient strength and stability so that the factored resistance, fR, is greater than or equal to the effect of factored loads, which shall be determined in accordance with Sentence (2). | obc2019_divb | Div B | 4.1.3.2.(1) | 4.1.3.2. Strength and Stability | A building and its structural components shall be designed to have sufficient strength and stability so that the factored resistance, fR, is greater than or equal to the effect of factored loads, which shall be determined in accordance with Sentence (2). | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.3.2.(10) | Strength and Stability | Earthquake load, E, in load combination cases 5 of Table 4.1.3.2.-A and 6 of Table 4.1.3.2.-B includes horizontal earth pressure due to earthquake determined in accordance with Sentence 4.1.8.16.(7). | obc2019_divb | Div B | 4.1.3.2.(10) | 4.1.3.2. Strength and Stability | Earthquake load, E, in load combination case 5 of Table 4.1.3.2.A. and case 6 of Table 4.1.3.2.B. includes horizontal earth pressure due to earthquake determined in accordance with Sentence 4.1.8.16.(4). | Common Sentence | Yes | Limit States Design
2015 | ON | NBC | Div B | 4.1.3.2.(11) | Strength and Stability | Provision shall be made to ensure adequate stability of the structure as a whole and adequate lateral, torsional and local stability of all structural parts. | obc2019_divb | Div B | 4.1.3.2.(11) | 4.1.3.2. Strength and Stability | Provision shall be made to ensure adequate stability of the structure as a whole and adequate lateral, torsional and local stability of all structural parts. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.3.2.(12) | Strength and Stability | Sway effects produced by vertical loads acting on the structure in its displaced configuration shall be taken into account in the design of buildings and their structural members. | obc2019_divb | Div B | 4.1.3.2.(12) | 4.1.3.2. Strength and Stability | Sway effects produced by vertical loads acting on the structure in its displaced configuration shall be taken into account in the design of buildings and their structural members. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.3.2.(2) | Strength and Stability | Except as provided in Sentence (3), the effect of factored loads for a building or structural component shall be determined in accordance with the requirements of this Article and the following load combination cases, the applicable combination being that which results in the most critical effect: (a) for load cases without crane loads, the load combinations listed in Table 4.1.3.2.-A., and (b) for load cases with crane loads, the load combinations listed in Table 4.1.3.2.-B. that which results in the most critical effect: for load cases without crane loads, the load combinations listed in Table 4.1.3.2.-A, and for load cases with crane loads, the load combinations listed in Table 4.1.3.2.-B. | obc2019_divb | Div B | 4.1.3.2.(2) | 4.1.3.2. Strength and Stability | Except as provided in Sentence (3), the effect of factored loads for a building or structural component shall be determined in accordance with the requirements of this Article and the following load combination cases, the applicable combination being that which results in the most critical effect: (a) for load cases without crane loads, the load combinations listed in Table 4.1.3.2.A., and (b) for load cases with crane loads, the load combinations listed in Table 4.1.3.2.B. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.3.2.(3) | Strength and Stability | Other load combinations that must also be considered are the principal loads acting with the companion loads taken as zero. | obc2019_divb | Div B | 4.1.3.2.(3) | 4.1.3.2. Strength and Stability | Other load combinations that must also be considered are the principal loads acting with the companion loads taken as zero. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.3.2.(4) | Strength and Stability | Where the effects due to lateral earth pressure, H, restraint effects from pre-stress, P, and imposed deformation, T, affect the structural safety, they shall be taken into account in the calculations, with load factors of 1.5, 1.0 and 1.25 assigned to H, P and T respectively. (See Note A-4.1.3.2.(4).) | obc2019_divb | Div B | 4.1.3.2.(4) | 4.1.3.2. Strength and Stability | Where the effects due to lateral earth pressure, H, restraint effects from pre-stress, P, and imposed deformation, T, affect the structural safety, they shall be taken into account in the calculations, with load factors of 1.5, 1.0 and 1.25 assigned to H, P and T respectively. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.3.2.(5) | Strength and Stability | Except as provided in Sentence 4.1.8.16.(2), the counteracting factored dead load - 0.9D in load combination cases 2, 3 and 4 and 1.0D in load combination case 5 in Table 4.1.3.2.-A, and 0.9D in load combination cases 1 to 5 and 1.0D in load combination case 6 in Table 4.1.3.2.- shall be used when the dead load acts to resist overturning, uplift, sliding, failure due to stress reversal, and to determine anchorage requirements and the factored resistance of members. (See Note A-4.1.3.2.(5).) | obc2019_divb | Div B | 4.1.3.2.(5) | 4.1.3.2. Strength and Stability | Except as provided in Sentence 4.1.8.16.(1), the counteracting factored dead load, 0.9D in load combination cases 2, 3 and 4 and 1.0D in load combination case 5 of Table 4.1.3.2.A. and 0.9D in load combination cases 1 to 5 and 1.0D in load combination case 6 of Table 4.1.3.2.B., shall be used when the dead load acts to resist overturning, uplift, sliding, failure due to stress reversal, and to determine anchorage requirements and the factored resistance of members. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.3.2.(6) | Strength and Stability | The principal-load factor 1.5 for live loads, L in Table 4.1.3.2.-A. and LXC in Table 4.1.3.2.-B. may be reduced to 1.25 for liquids in tanks. | obc2019_divb | Div B | 4.1.3.2.(6) | 4.1.3.2. Strength and Stability | The principal-load factor 1.5 for live loads, L in Table 4.1.3.2.A. and LXC in Table 4.1.3.2.B. may be reduced to 1.25 for liquids in tanks. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.3.2.(7) | Strength and Stability | The companion-load factor for live loads L in Table 4.1.3.2.-A and LXC in Table 4.1.3.2.-B shall be increased by 0.5 for storage areas, and equipment areas and service rooms referred to in Table 4.1.5.3. | obc2019_divb | Div B | 4.1.3.2.(7) | 4.1.3.2. Strength and Stability | The companion-load factor for live loads, L in Table 4.1.3.2.A. and LXC in Table 4.1.3.2.B. shall be increased by 0.5 for storage areas and for equipment areas and service rooms referred to in Table 4.1.5.3. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.3.2.(8) | Strength and Stability | Except as provided in Sentence (9), the load factor 1.25 for dead load, D, for soil, superimposed earth, plants and trees given in Tables 4.1.3.2.-A and 4.1.3.2.-B shall be increased to 1.5, except that when the soil depth exceeds 1.2 m, the factor may be reduced to 1 + 0.6/hs but not less than 1.25, where hs is the depth of soil in metres supported by the structure. | obc2019_divb | Div B | 4.1.3.2.(8) | 4.1.3.2. Strength and Stability | Except as provided in Sentence (9), the load factor 1.25 for dead load, D, for soil, superimposed earth, plants and trees given in Tables 4.1.3.2.A. and 4.1.3.2.B. shall be increased to 1.5, except that when the soil depth exceeds 1.2 m, the factor may be reduced to 1 + 0.6/hs but not less than 1.25, where hs is the depth of soil in metres supported by the structure. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.3.2.(9) | Strength and Stability | A principal-load factor of 1.5 shall be applied to the weight of saturated soil used in load combination case 1 of Table 4.1.3.2.-A. | obc2019_divb | Div B | 4.1.3.2.(9) | 4.1.3.2. Strength and Stability | A principal-load factor of 1.5 shall be applied to the weight of saturated soil used in load combination case 1 of Table 4.1.3.2.A. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.3.3.(1) | Fatigue | A building and its structural components, including connections, shall be checked for fatigue failure under the effect of the cyclical loads, as required in the standards listed in Section 4.3. (See Note A-4.1.3.3.(1).) | obc2019_divb | Div B | 4.1.3.3.(1) | 4.1.3.3. Fatigue | A building and its structural components, including connections, shall be checked for fatigue failure under the effect of the cyclical loads, as required in the standards listed in Section 4.3. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.3.3.(2) | Fatigue | Where vibration effects, such as resonance and fatigue resulting from machinery and equipment, are likely to be significant, a dynamic analysis shall be carried out. (See Note A-4.1.3.3.(2).) | obc2019_divb | Div B | 4.1.3.3.(2) | 4.1.3.3. Fatigue | Where vibration effects, such as resonance and fatigue resulting from machinery and equipment, are likely to be significant, a dynamic analysis shall be carried out. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.3.4.(1) | Serviceability | A building and its structural components shall be checked for serviceability limit states as defined in Sentence 4.1.3.1.(1) under the effect of service loads for serviceability criteria specified or recommended in Articles 4.1.3.5. and 4.1.3.6. and in the standards listed in part 4. (See Note A-4.1.3.4.(1).) | obc2019_divb | Div B | 4.1.3.4.(1) | 4.1.3.4. Serviceability | A building and its structural components shall be checked for serviceability limit states as defined in Clause 4.1.3.1.(1)(a) under the effect of service loads for serviceability criteria specified or recommended in Articles 4.1.3.5. and 4.1.3.6. and in the standards listed in Section 4.3. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.3.5.(1) | Deflection | In proportioning structural members to limit serviceability problems resulting from deflections, consideration shall be given to (a) the intended use of the building or member, (b) limiting damage to non-structural members made of materials whose physical properties are known at the time of design, (c) limiting damage to the structure itself, and (d) creep, shrinkage, temperature changes and pre-stress. (See Note A-4.1.3.5.(1).) | obc2019_divb | Div B | 4.1.3.5.(1) | 4.1.3.5. Deflection | In proportioning structural members to limit serviceability problems resulting from deflections, consideration shall be given to, (a) the intended use of the building or member, (b) limiting damage to non-structural members made of materials whose physical properties are known at the time of design, (c) limiting damage to the structure itself, and (d) creep, shrinkage, temperature changes and prestress. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.3.5.(2) | Deflection | The lateral deflection of buildings due to service wind and gravity loads shall be checked to ensure that structural elements and non-structural elements whose nature is known at the time the structural design is carried out will not be damaged. | obc2019_divb | Div B | 4.1.3.5.(2) | 4.1.3.5. Deflection | The lateral deflection of buildings due to service wind and gravity loads shall be checked to ensure that structural elements and non-structural elements whose nature is known at the time the structural design is carried out will not be damaged. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.3.5.(3) | Deflection | Except as provided in Sentence (4), the total drift per storey under service wind and gravity loads shall not exceed 1/500 of the storey height unless other drift limits are specified in the design standards referenced in part 4. (See Note A-4.1.3.5.(3).) | obc2019_divb | Div B | 4.1.3.5.(3) | 4.1.3.5. Deflection | Except as provided in Sentence (4), the total drift per storey under service wind and gravity loads shall not exceed 1/500 of the storey height unless other drift limits are specified in the design standards referenced in Section 4.3. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.3.5.(4) | Deflection | The deflection limits required in Sentence 4.1.3.5.(3) do not apply to industrial buildings or sheds if experience has proven that greater movement will have no significant adverse effects on the strength and function of the building. | obc2019_divb | Div B | 4.1.3.5.(4) | 4.1.3.5. Deflection | The deflection limits required in Sentence (3) do not apply to industrial buildings or sheds if experience has proven that greater movement will have no significant adverse effects on the strength and function of the building. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.3.5.(5) | Deflection | The building structure shall be designed for lateral deflection due to E, in accordance with Article 4.1.8.13. | obc2019_divb | Div B | 4.1.3.5.(5) | 4.1.3.5. Deflection | The building structure shall be designed for lateral deflection due to E, in accordance with Article 4.1.8.13. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.3.6.(1) | Vibration | Floor systems susceptible to vibration shall be designed so that vibrations will have no significant adverse effects on the intended occupancy of the building. (See Note A-4.1.3.6.(1).) | obc2019_divb | Div B | 4.1.3.6.(1) | 4.1.3.6. Vibration | Floor systems susceptible to vibration shall be designed so that vibrations will have no significant adverse effects on the intended occupancy of the building. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.3.6.(2) | Vibration | Where the fundamental vibration frequency of a structural system supporting an assembly occupancy used for rhythmic activities, such as dancing, concerts, jumping exercises or gymnastics, is less than 6 Hz, the effects of resonance shall be investigated by means of a dynamic analysis. (See Note A-4.1.3.6.(2) .) | obc2019_divb | Div B | 4.1.3.6.(2) | 4.1.3.6. Vibration | Where the fundamental vibration frequency of a structural system supporting an assembly occupancy used for rhythmic activities, such as dancing, concerts, jumping exercises or gymnastics, is less than 6 Hz, the effects of resonance shall be investigated by means of a dynamic analysis. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.3.6.(3) | Vibration | A building susceptible to lateral vibration under wind load shall be designed in accordance with Article 4.1.7.1. so that the vibrations will have no significant adverse effects on the intended use and occupancy of the building. (See Note A-4.1.3.6.(3).) | obc2019_divb | Div B | 4.1.3.6.(3) | 4.1.3.6. Vibration | A building susceptible to lateral vibration under wind load shall be designed in accordance with Article 4.1.7.2. so that the vibrations will have no significant adverse effects on the intended use and occupancy of the building. (See Appendix A.) | Common Sentence | Yes | Limit States Design
2015 | ON | NBC | Div B | 4.1.4.1.(1) | Dead Loads | The specified dead load for a structural member consists of (a) the weight of the member itself, (b) the weight of all materials of construction incorporated into the building to be supported permanently by the member,( c) the weight of partitions, (d) the weight of permanent equipment, and (e) the vertical load due to earth, plants and trees. | obc2019_divb | Div B | 4.1.4.1.(1) | 4.1.4.1. Dead Loads | The specified dead load for a structural member consists of, (a) the weight of the member itself, (b) the weight of all materials of construction incorporated into the building to be supported permanently by the member, (c) the weight of partitions, (d) the weight of permanent equipment, and (e) the vertical load due to earth, plants and trees. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.4.1.(2) | Dead Loads | Except as provided in Sentence (5), in areas of a building where partitions, other than permanent partitions are shown on the drawings, or where partitions might be added in the future, allowance shall be made for the weight of such partitions. | obc2019_divb | Div B | 4.1.4.1(2) | 4.1.4.1. Dead Loads | Except as provided in Sentence (5), in areas of a building where partitions other than permanent partitions are shown on the drawings, or where partitions might be added in the future, allowance shall be made for the weight of such partitions. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.4.1.(3) | Dead Loads | The partition weight allowance referred to in Sentence (2) shall be determined from the actual or anticipated weight of the partitions placed in any probable position, but shall be not less than 1 kPa over the area of floor being considered. | obc2019_divb | Div B | 4.1.4.1.(3) | 4.1.4.1. Dead Loads | The partition weight allowance in Sentence (2) shall be determined from the actual or anticipated weight of the partitions placed in any probable position, but shall be not less than 1 kPa over the area of floor being considered. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.4.1.(5) | Dead Loads | In cases where the dead load of the partition is counteractive, the load allowances referred to in Sentences (2) and (3) shall not be included in the design calculations. | obc2019_divb | Div B | 4.1.4.1.(5) | 4.1.4.1. Dead Loads | In cases where the dead load of the partition is counteractive, the load allowances referred to in Sentences (2) and (3) shall not be included in the design calculations. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.4.1.(6) | Dead Loads | Except for structures where the dead load of soil is part of the load-resisting system, where the dead load due to soil, superimposed earth, plants and trees is counteractive, it shall not be included in the design calculations. (See Note A-4.1.4.1.(6).) | obc2019_divb | Div B | 4.1.4.1.(6) | 4.1.4.1. Dead Loads | Except for structures where the dead load of soil is part of the load-resisting system, where the dead load due to soil, superimposed earth, plants and trees is counteractive, it shall not be included in the design calculations. (See Appendix‚ A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.5.1.(1) | Loads Due to Use of Floors and Roofs | Except as provided in Sentence (2), the specified live load on an area of floor or roof depends on the intended use and occupancy, and shall not be less than either the uniformly distributed load patterns listed in Article 4.1.5.3., the loads due to the intended use and occupancy, or the concentrated loads listed in Article 4.1.5.9., whichever produces the most critical effect. (See Note A-4.1.5.1.(1).) | obc2019_divb | Div B | 4.1.5.1.(1) | 4.1.5.1. Loads Due to Use of Floors and Roofs | Except as provided in Sentence (2), the specified live load on an area of floor or roof depends on the intended use and occupancy, and shall not be less than whichever of the following loads produces the most critical effect: (a) the uniformly distributed load patterns listed in Article 4.1.5.3., (b) the loads due to the intended use and occupancy, or (c) the concentrated loads listed in Article 4.1.5.9. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.5.1.(2) | Loads Due to Use of Floors and Roofs | For buildings in the Low Importance Category as described in Table 4.1.2.1., a factor of 0.8 may be applied to the live load. | obc2019_divb | Div B | 4.1.5.1.(2) | 4.1.5.1. Loads Due to Use of Floors and Roofs | For buildings in the Low Importance Category as described in Table 4.1.2.1.B., a factor of 0.8 may be applied to the live load. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.5.1.(2) | Loads Due to Use of Floors and Roofs | For buildings in the Low Importance Category as described in Table 4.1.2.1., a factor of 0.8 may be applied to the live load. | obc2019_divb | Div B | 4.1.5.2.(2) | 4.1.5.2. Uses Not Stipulated | For buildings in the Low Importance Category as described in Table 4.1.2.1.B., a factor of 0.8 may be applied to the live load. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.5.10.(1) | Sway Forces in Assembly Occupancies | The floor assembly and other structural elements that support fixed seats in any building used for assembly occupancies accommodating large numbers of people at one time, such as grandstands, stadia and theatre balconies, shall be designed to resist a horizontal force equal to not less than 0.3 kN for each metre length of seats acting parallel to each row of seats, and not less than 0.15 kN for each metre length of seats acting at right angles to each row of seats, based on the assumption that these forces are acting independently of each other. | obc2019_divb | Div B | 4.1.5.10.(1) | 4.1.5.10. Sway Forces in Assembly Occupancies | The floor assembly and other structural elements that support fixed seats in any building used for assembly occupancies accommodating large numbers of people at one time, such as grandstands, stadia and theatre balconies, shall be designed to resist a horizontal force equal to not less than 0.3 kN for each metre length of seats acting parallel to each row of seats, and not less than 0.15 kN for each metre length of seats acting at right angles to each row of seats, based on the assumption that these forces are acting independently of each other. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.5.11.(1) | Crane-Supporting Structures and Impact of Machinery and Equipment | The minimum specified load due to equipment, machinery or other objects that may produce impact shall be the sum of the weight of the equipment or machinery and its maximum lifting capacity, multiplied by an appropriate factor listed in Table 4.1.5.11. | obc2019_divb | Div B | 4.1.5.11.(1) | 4.1.5.11. Crane-Supporting Structures and Impact of Machinery and Equipment | The minimum specified load due to equipment, machinery or other objects that may produce impact shall be the sum of the weight of the equipment or machinery and its maximum lifting capacity, multiplied by an appropriate factor listed in Table 4.1.5.11. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.5.11.(2) | Crane-Supporting Structures and Impact of Machinery and Equipment | Crane-supporting structures shall be designed for the appropriate load combinations listed in Article 4.1.3.2. | obc2019_divb | Div B | 4.1.5.11.(2) | 4.1.5.11. Crane-Supporting Structures and Impact of Machinery and Equipment | Crane-supporting structures shall be designed for the appropriate load combinations listed in Article 4.1.3.2. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.5.11.(3) | Crane-Supporting Structures and Impact of Machinery and Equipment | Crane runway structures shall be designed to resist a horizontal force applied normal to the top of the rails equal to not less than 20% of the sum of the weights of the lifted load and the crane trolley (excluding other parts of the crane). | obc2019_divb | Div B | 4.1.5.11.(3) | 4.1.5.11. Crane-Supporting Structures and Impact of Machinery and Equipment | Crane runway structures shall be designed to resist a horizontal force applied normal to the top of the rails equal to not less than 20% of the sum of the weights of the lifted load and the crane trolley, excluding other parts of the crane. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.5.11.(4) | Crane-Supporting Structures and Impact of Machinery and Equipment | The force described in Sentence (3) shall be equally distributed on each side of the runway and shall be assumed to act in either direction. | obc2019_divb | Div B | 4.1.5.11.(4) | 4.1.5.11. Crane-Supporting Structures and Impact of Machinery and Equipment | The force described in Sentence (3) shall be equally distributed on each side of the runway and shall be assumed to act in either direction. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.5.11.(5) | Crane-Supporting Structures and Impact of Machinery and Equipment | Crane runway structures shall be designed to resist a horizontal force applied parallel to the top of the rails equal to not less than 10% of the maximum wheel loads of the crane. | obc2019_divb | Div B | 4.1.5.11.(5) | 4.1.5.11. Crane-Supporting Structures and Impact of Machinery and Equipment | Crane runway structures shall be designed to resist a horizontal force applied parallel to the top of the rails equal to not less than 10% of the maximum wheel loads of the crane. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.5.12.(1) | Bleachers | Bleacher seats shall be designed for a uniformly distributed live load of 1.75 kN for each linear metre or for a concentrated load of 2.2 kN distributed over a length of 0.75 m, whichever produces the most critical effect on the supporting members. | obc2019_divb | Div B | 4.1.5.12.(1) | 4.1.5.12. Bleachers | Bleacher seats shall be designed for a uniformly distributed live load of 1.75 kN for each linear metre or for a concentrated load of 2.2 kN distributed over a length of 750 mm, whichever produces the most critical effect on the supporting members. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.5.12.(2) | Bleachers | Bleachers shall be checked by the erector after erection to ensure that all structural members, including bracing specified in the design, have been installed. | obc2019_divb | Div B | 4.1.5.12.(2) | 4.1.5.12. Bleachers | Bleachers shall be checked by the erector after erection to ensure that all structural members, including bracing specified in the design, have been installed. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.5.12.(3) | Bleachers | Telescopic bleachers shall be provided with locking devices to ensure stability while in use. | obc2019_divb | Div B | 4.1.5.12.(3) | 4.1.5.12. Bleachers | Telescopic bleachers shall be provided with locking devices to ensure stability while in use. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.5.13.(1) | Helicopter Landing Areas | Helicopter landing areas on roofs shall be constructed in conformance with the requirements for heliports contained in TC SOR/96-433 "Canadian Aviation Regulations - Part III" | obc2019_divb | Div B | 4.1.5.13.(1) | 4.1.5.13. Helicopter Landing Areas | Helicopter landing areas on roofs shall be constructed in conformance with the requirements for heliports contained in Part III of the Canadian Aviation Regulations made under the Aeronautics Act (Canada). | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.5.14.(1) | Loads on Guards and Handrails (See Note A-4.1.5.14. and 4.1.5.15.(1).) | The minimum specified horizontal load applied outward at the minimum required height of every required guard shall be, a) 3.0 kN/m for open viewing stands without fixed seats and for means of egress in grandstands, stadia, bleachers and arenas, b) a concentrated load of 1.0 kN applied at any point so as to produce the most critical effect, for access ways to equipment platforms, contiguous stairs and similar areas where the gathering of many people is improbable, and c) 0.75 kN/m or a concentrated load of 1.0 kN applied at any point so as to produce the most critical effect, whichever governs for locations other than those described in Clauses (a) and (b). | obc2019_divb | Div B | 4.1.5.14.(1) | 4.1.5.14. Loads on Guards and Handrails | The minimum specified horizontal load applied outward at the minimum required height of every required guard shall be, (a) 3.0 kN/m for open viewing stands without fixed seats and for means of egress in grandstands, stadia, bleachers and arenas, (b) a concentrated load of 1.0 kN applied at any point so as to produce the most critical effect, for access ways to equipment platforms, contiguous stairs and similar areas where the gathering of many people is improbable, and (c) 0.75 kN/m or a concentrated load of 1.0 kN applied at any point so as to produce the most critical effect, whichever governs for locations other than those described in Clauses (a) and (b). | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.5.14.(2) | Loads on Guards and Handrails (See Note A-4.1.5.14. and 4.1.5.15.(1).) | The minimum specified horizontal load applied inward at the minimum required height of every required guard shall be half that specified in Sentence (1). | obc2019_divb | Div B | 4.1.5.14.(2) | 4.1.5.14. Loads on Guards and Handrails | The minimum specified horizontal load applied inward at the minimum required height of every required guard shall be half that specified in Sentence (1). | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.5.14.(3) | Loads on Guards and Handrails (See Note A-4.1.5.14. and 4.1.5.15.(1).) | Individual elements within the guard, including solid panels and pickets, shall be designed for a load of 0.5 kN applied outward over an area of 100 mm by 100 mm located at any point in the element or elements so as to produce the most critical effect. | obc2019_divb | Div B | 4.1.5.14.(3) | 4.1.5.14. Loads on Guards and Handrails | Individual elements within the guard, including solid panels and pickets, shall be designed for a load of 0.5 kN applied outward over an area of 100 mm by 100 mm located at any point in the element or elements so as to produce the most critical effect. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.5.14.(4) | Loads on Guards and Handrails (See Note A-4.1.5.14. and 4.1.5.15.(1).) | The size of the opening between any two adjacent vertical elements within a guard shall not exceed the limits required by Part 3 when each of these elements is subjected to a specified live load of 0.1 kN applied in opposite directions in the in-plane direction of the guard so as to produce the most critical effect. | obc2019_divb | Div B | 4.1.5.14.(4) | 4.1.5.14. Loads on Guards and Handrails | The size of the opening between any two adjacent vertical elements within a guard shall not exceed the limits required by Part 3 when each of these elements is subjected to a specified live load of 0.1 kN applied in opposite directions in the in-plane direction of the guard so as to produce the most critical effect. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.5.14.(6) | Loads on Guards and Handrails | The minimum specified load applied vertically at the top of every required guard shall be 1.5 kN/m and need not be considered to act simultaneously with the horizontal load provided for in Sentence (1). | obc2019_divb | Div B | 4.1.5.14.(6) | 4.1.5.14. Loads on Guards and Handrails | The minimum specified load applied vertically at the top of every required guard shall be 1.5 kN/m and need not be considered to act simultaneously with the horizontal load provided for in Sentence (1). | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.5.14.(7) | Loads on Guards and Handrails | Handrails and their supports shall be designed and constructed to withstand the following loads, which need not be considered to act simultaneously: a) a concentrated load not less than 0.9 kN applied at any point and in any direction for all handrails, and b) a uniform load not less than 0.7 kN/m applied in any direction to handrails not located within dwelling units. | obc2019_divb | Div B | 4.1.5.14.(7) | 4.1.5.14. Loads on Guards and Handrails | Handrails and their supports shall be designed and constructed to withstand the following loads, which need not be considered to act simultaneously: (a) a concentrated load not less than 0.9 kN applied at any point and in any direction for all handrails, and (b) a uniform load not less than 0.7 kN/m applied in any direction to handrails not located within dwelling units. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.5.15.(1) | Loads on Vehicle Guardrails | Vehicle guardrails shall be designed for a concentrated load of 22 kN applied horizontally outward at any point 500 mm above the floor surface so as to produce the most critical effect. (See Note A-4.1.5.14..) | obc2019_divb | Div B | 4.1.5.15.(1) | 4.1.5.15. Loads on Vehicle Guardrails | Vehicle guardrails shall be designed for a concentrated load of 22 kN applied horizontally outward at any point 500 mm above the floor surface. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.5.15.(2) | Loads on Vehicle Guardrails | The loads required in Sentence (1) need not be considered to act simultaneously with the loads provided for in Article 4.1.5.14. | obc2019_divb | Div B | 4.1.5.15.(2) | 4.1.5.15. Loads on Vehicle Guardrails | The loads described in Sentence (1) need not be considered to act simultaneously with the loads provided for in Article 4.1.5.14. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.5.15.(2) | Loads on Vehicle Guardrails | The loads required in Sentence (3) need not be considered to act simultaneously with the loads provided for in Sentences (1), (2) and (6). | obc2019_divb | Div B | 4.1.5.14.(5) | 4.1.5.14. Loads on Guards and Handrails | The loads required in Sentence (3) need not be considered to act simultaneously with the loads provided for in Sentences (1), (2) and (6). | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.5.16.(1) | Loads on Walls Acting As Guards | Where the floor elevation on one side of a wall, including a wall around a shaft, is more than 600 mm higher than the elevation of the floor or ground on the other side, the wall shall be designed to resist the appropriate outward lateral design loads prescribed elsewhere in Subsection 4.1.15. or 0.5 kPa acting outward, whichever produces the more critical effect. | obc2019_divb | Div B | 4.1.5.16.(1) | 4.1.5.16. Loads on Walls Acting As Guards | Where the floor elevation on one side of a wall, including a wall around a shaft, is more than 600 mm higher than the elevation of the floor or ground on the other side, the wall shall be designed to resist the appropriate outward lateral design loads prescribed elsewhere in this Subsection or 0.5 kPa acting outward, whichever produces the more critical effect. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.5.17.(1) | Firewalls (See Note A-4.1.5.17.) | Firewalls shall be designed to resist the maximum effect due to a) the appropriate lateral design loads prescribed elsewhere in this Section, or b) a factored lateral load of 0.5 kPa under fire conditions, as described in Sentence (2). | obc2019_divb | Div B | 4.1.5.17.(1) | 4.1.5.17. Firewalls | Firewalls shall be designed to resist the maximum effect due to, (a) the appropriate lateral design loads prescribed elsewhere in this Section, or (b) a factored lateral load of 0.5 kPa under fire conditions, as described in Sentence (2). | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.5.17.(2) | Firewalls (See Note A-4.1.5.17.) | Under fire conditions, where the fire-resistance rating of the structure is less than that of the firewall, a) lateral support shall be assumed to be provided by the structure on one side only, or b) another structural support system capable of resisting the loads imposed by a fire on either side of the firewall shall be provided. | obc2019_divb | Div B | 4.1.5.17.(2) | 4.1.5.17. Firewalls | Under fire conditions, where the fire-resistance rating of the structure is less than that of the firewall, (a) lateral support shall be assumed to be provided by the structure on one side only, or (b) another structural support system capable of resisting the loads imposed by a fire on either side of the firewall shall be provided. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.5.2.(1) | Uses Not Stipulated | Except as provided in Sentence (2), where the use of an area of floor or roof is not provided for in Article 4.1.5.3., the specified live loads due to the use and occupancy of the area shall be determined from an analysis of the loads resulting from the weight of a) the probable assembly of persons, b) the probable accumulation of equipment and furnishings, and c) the probable storage of materials. | obc2019_divb | Div B | 4.1.5.2.(1) | 4.1.5.2. Uses Not Stipulated | Except as provided in Sentence (2), where the use of an area of floor or roof is not provided for in Article 4.1.5.3., the specified live loads due to the use and occupancy of the area shall be determined from an analysis of the loads resulting from the weight of, (a) the probable assembly of persons, (b) the probable accumulation of equipment and furnishings, and (c) the probable storage of materials. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.5.3.(1) | Full and Partial Loading | The uniformly distributed live load shall be not less than the value listed in Table 4.1.5.3., which may be reduced as provided in Article 4.1.5.8., applied uniformly over the entire area, or on any portions of the area, whichever produces the most critical effects in the members concerned. | obc2019_divb | Div B | 4.1.5.3.(1) | 4.1.5.3. Full and Partial Loading | The uniformly distributed live load shall be not less than the value listed in Table 4.1.5.3., which may be reduced as provided in Article 4.1.5.8., applied uniformly over the entire area, or on any portions of the area, whichever produces the most critical effects in the members concerned. | Common Sentence | Yes | Loads
2015 | ON | NBC | Div B | 4.1.5.4.(1) | Loads for Occupancy Served | The following shall be designed to carry not less than the specified load required for the occupancy they serve, provided they cannot be used by an assembly of people as a viewing area: a) corridors, lobbies and aisles not more than 1 200 mm wide, b) all corridors above the first storey of residential areas of apartments, hotels and motels, and c) interior balconies and mezzanines. | obc2019_divb | Div B | 4.1.5.4.(1) | 4.1.5.4. Loads for Occupancy Served | The following shall be designed to carry not less than the specified load required for the occupancy they serve, provided they cannot be used by an assembly of people as a viewing area: (a) corridors, lobbies and aisles not more than 1 200 mm wide, (b) all corridors above the first storey of residential areas of apartments, hotels and motels, and (c) interior balconies and mezzanines. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.5.5.(1) | Loads on Exterior Areas (See Note A-4.1.5.5.) | Exterior areas accessible to vehicular traffic shall be designed for their intended use, including the weight of firefighting equipment, but not for less than the snow and rain loads prescribed in Subsection 4.1.6. | obc2019_divb | Div B | 4.1.5.5.(1) | 4.1.5.5. Loads on Exterior Areas | Exterior areas accessible to vehicular traffic shall be designed for their intended use, including the weight of firefighting equipment, but not for less than the snow and rain loads prescribed in Subsection 4.1.6. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.5.5.(2) | Loads on Exterior Areas (See Note A-4.1.5.5.) | Except as provided in Sentences (3) and (4), roofs shall be designed for either the uniform live loads specified in Table 4.1.5.3., the concentrated live loads listed in Table 4.1.5.9., or the snow and rain loads prescribed in Subsection 4.1.6., whichever produces the most critical effects in the members concerned. | obc2019_divb | Div B | 4.1.5.5.(2) | 4.1.5.5. Loads on Exterior Areas | Except as provided in Sentences (3) and (4), roofs shall be designed for the uniform live loads specified in Table 4.1.5.3., the concentrated live loads listed in Table 4.1.5.9., or the snow and rain loads prescribed in Subsection 4.1.6., whichever produces the most critical effects in the members concerned. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.5.5.(3) | Loads on Exterior Areas (See Note A-4.1.5.5.) | Exterior areas accessible to pedestrian traffic, but not vehicular traffic, shall be designed for their intended use, but not for less than the greater of, (a) the live load prescribed for assembly areas in Table 4.1.5.3., or (b) the snow and rain loads prescribed in Subsection 4.1.6. | obc2019_divb | Div B | 4.1.5.5.(3) | 4.1.5.5. Loads on Exterior Areas | Exterior areas accessible to pedestrian traffic, but not vehicular traffic, shall be designed for their intended use, but not for less than the greater of, (a) the live load prescribed for assembly areas in Table 4.1.5.3., or (b) the snow and rain loads prescribed in Subsection 4.1.6. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.5.5.(4) | Loads on Exterior Areas (See Note A-4.1.5.5.) | Roof parking decks shall be designed for either the uniformly distributed live loads specified in Table 4.1.5.3., the concentrated live loads listed in Table 4.1.5.9., or the roof snow load, whichever produces the most critical effect in the members concerned. | obc2019_divb | Div B | 4.1.5.5.(4) | 4.1.5.5. Loads on Exterior Areas | Roof parking decks shall be designed for the uniformly distributed live loads specified in Table 4.1.5.3., the concentrated live loads listed in Table 4.1.5.9., or the roof snow load, whichever produces the most critical effect in the members concerned. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.5.6.(1) | Loads for Dining Areas | The minimum specified live load listed in Table 4.1.5.3. for dining areas may be reduced to 2.4 kPa for areas in buildings that are being converted to dining areas, provided that the floor area does not exceed 100 m2 and the dining area will not be used for other assembly purposes, including dancing. | obc2019_divb | Div B | 4.1.5.6.(1) | 4.1.5.6. Loads for Dining Areas | The minimum specified live load listed in Table 4.1.5.3. for dining areas may be reduced to 2.4 kPa for areas in buildings that are being converted to dining areas, provided that the floor area does not exceed 100 m2 and the dining area will not be used for other assembly purposes, including dancing. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.5.7.(1) | More Than One Occupancy | Where an area of floor or roof is intended for 2 or more occupancies at different times, the value to be used from Table 4.1.5.3. shall be the greatest value for any of the occupancies concerned. | obc2019_divb | Div B | 4.1.5.7.(1) | 4.1.5.7. More Than One Occupancy | Where an area of floor or roof is intended for 2 or more occupancies at different times, the value to be used from Table 4.1.5.3. shall be the greatest value for any of the occupancies concerned. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.5.8.(1) | Variation with Tributary Area | An area used for assembly occupancies designed for a live load of less than 4.8 kPa and roofs designed for the minimum loading specified in Table 4.1.5.3. shall have no reduction for tributary area. | obc2019_divb | Div B | 4.1.5.8.(1) | 4.1.5.8. Variation with Tributary Area | An area used for assembly occupancies designed for a live load of less than 4.8 kPa and roofs designed for the minimum loading specified in Table 4.1.5.3. shall have no reduction for tributary area. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.5.8.(2) | Variation with Tributary Area | Where a structural member supports a tributary area of a floor or a roof, or a combination of them, that is greater than 80 m² and either used for assembly occupancies designed for a live load of 4.8 kPa or more, or used for storage, manufacturing, retail stores, garages or as a footbridge, the specified live load due to use and occupancy is the load specified in Article 4.1.5.3. multiplied by 0.5+ (20/A)0.5 where, A is the tributary area in square metres for this type of use and occupancy. | obc2019_divb | Div B | 4.1.5.8.(2) | 4.1.5.8. Variation with Tributary Area | Where a structural member supports a tributary area of a floor or a roof, or a combination of them, that is greater than 80 m² and either used for assembly occupancies designed for a live load of 4.8 kPa or more, or used for storage, manufacturing, retail stores, garages or as a footbridge, the specified live load due to use and occupancy is the load specified in Article 4.1.5.3. multiplied by, 0.5+ (20/A)0.5 where, “A” is the tributary area in square metres for this type of use and occupancy. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.5.8.(3) | Variation with Tributary Area | Where a structural member supports a tributary area of a floor or a roof or a combination of them, that is greater than 20 m² and used for any use or occupancy other than assembly occupancies and those indicated in Sentences (1) and (2), the specified live load due to use and occupancy, is the load specified in Article 4.1.5.3. multiplied by 0.3+ (9.8/B)0.5 where, B is the tributary area in square metres for this type of use and occupancy. | obc2019_divb | Div B | 4.1.5.8.(3) | 4.1.5.8. Variation with Tributary Area | Where a structural member supports a tributary area of a floor or a roof or a combination of them, that is greater than 20 m² and used for any use or occupancy other than assembly occupancies and those indicated in Sentences (1) and (2), the specified live load due to use and occupancy, is the load specified in Article 4.1.5.3. multiplied by, 0.3+ (9.8/B)0.5 where, “B” is the tributary area in square metres for this type of use and occupancy. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.5.8.(4) | Variation with Tributary Area | Where the specified live load for a floor is reduced in accordance with Sentence (2) or (3), the structural drawings shall indicate that a live load reduction factor for tributary area has been applied. | obc2019_divb | Div B | 4.1.5.8.(4) | 4.1.5.8. Variation with Tributary Area | Where the specified live load for a floor is reduced in accordance with Sentence (2) or (3), the structural drawings shall indicate that a live load reduction factor for tributary area has been applied. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.5.9.(1) | Concentrated Loads | The specified live load due to possible concentrations of load resulting from the use of an area of floor or roof shall not be less than that listed in Table 4.1.5.9. applied over the loaded area noted and located so as to cause maximum effects, except that for occupancies not listed in Table 4.1.5.9., the concentrations of load shall be determined in accordance with Article 4.1.5.2. | obc2019_divb | Div B | 4.1.5.9.(1) | 4.1.5.9. Concentrated Loads | The specified live load due to possible concentrations of load resulting from the use of an area of floor or roof shall not be less than that listed in Table 4.1.5.9. applied over the loaded area noted in Table 4.1.5.9. and located so as to cause maximum effects, except that for occupancies not listed in Table 4.1.5.9., the concentrations of load shall be determined in accordance with Article 4.1.5.2. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.1.(1) | Specified Load Due to Rain or to Snow and Associated Rain | The specified load on a roof or any other building surface subject to snow and associated rain shall be the snow load specified in Article 4.1.6.2., or the rain load specified in Article 4.1.6.4., whichever produces the more critical effect. | obc2019_divb | Div B | 4.1.6.1.(1) | 4.1.6.1. Specified Load Due to Rain or to Snow and Associated Rain | The specified load on a roof or any other building surface subject to snow and associated rain shall be the snow load specified in Article 4.1.6.2., or the rain load specified in Article 4.1.6.4., whichever produces the more critical effect. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.10.(1) | Arch Roofs, Curved Roofs and Domes | For all arch roofs, curved roofs and domes, the full and partial load cases defined in Article 4.1.6.3. shall be considered. | obc2019_divb | Div B | 4.1.6.10.(1) | 4.1.6.10. Arch Roofs, Curved Roofs and Domes | For all arch roofs, curved roofs and domes, the full and partial load cases defined in Article 4.1.6.3. shall be considered. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.10.(2) | Arch Roofs, Curved Roofs and Domes | For arch roofs, curved roofs and domes with a rise-to-span ratio h/b > 0.05 (see Figure 4.1.6.10.-A), the load cases provided in Sentences (3) to (7) shall also be considered. | obc2019_divb | Div B | 4.1.6.10.(2) | 4.1.6.10. Arch Roofs, Curved Roofs and Domes | For arch roofs, curved roofs and domes with rise-to-span ratio h/b > 0.05 as shown in Figure 4.1.6.10.A., the load cases provided in Sentences (3) to (7) shall also be considered. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.10.(3) | Arch Roofs, Curved Roofs and Domes | For arch roofs with a slope at the edge ae < =30° (see Figure 4.1.6.10.-A and Table 4.1.6.10.)., Ca shall be, (a) taken as 0 on the upwind side of the peak, and (b) on the downwind side of the peak, taken as, Ca = xh/(0.03Cbb2) for 0.05 < h/b <= 0.12 and Ca = 4x/(Cbb) for h/b > 0.12 where, x = horizontal distance from the roof peak, h = height of arch, and b = width of arch. | obc2019_divb | Div B | 4.1.6.10.(3) | 4.1.6.10. Arch Roofs, Curved Roofs and Domes | For arch roofs with a slope at the edge ae < =30° as shown in Figure 4.1.6.10.A. and as described in Table 4.1.6.10., Ca shall be, (a) taken as 0 on the upwind side of the peak, and (b) on the downwind side of the peak, taken as, Ca = xh/(0.03Cbb2) for 0.05 < h/b <= 0.12 and Ca = 4x/(Cbb) for h/b > 0.12 where, x = horizontal distance from the roof peak, h = height of arch, and b = width of arch. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.10.(4) | Arch Roofs, Curved Roofs and Domes | For arch roofs with a slope at the edge ae > 30° (see Figure 4.1.6.10.-A and Table 4.1.6.10.), Ca shall be, (a) taken as 0 on the upwind side of the peak, and (b) on the downwind side of the peak, (i) for the part of the roof between the peak and point where the slope ? = 30°, taken as Ca = xh/(0.06Cbx30b) for 0.05 < h/b <= 0.12, and Ca = 2x/(Cbx30) for h/b < 0.12 where, x, h, b = as specified in Sentence (2), and x30 = value of x where the slope ? = 30°, and (ii) for the part of the roof where the slope ? > 30°, taken as Ca = h/(0.06Cbb) for 0.05 < h/b <= 0.12, and Ca = 2/Cb for h/b > 0.12 | obc2019_divb | Div B | 4.1.6.10.(4) | 4.1.6.10. Arch Roofs, Curved Roofs and Domes | For arch roofs with a slope at the edge ae > 30° as shown in Figure 4.1.6.10.A. and as described in Table 4.1.6.10., Ca shall be, (a) taken as 0 on the upwind side of the peak, and (b) on the downwind side of the peak, (i) for the part of the roof between the peak and point where the slope ? = 30°, taken as, Ca = xh/(0.06Cbx30b) for 0.05 < h/b <= 0.12, and Ca = 2x/(Cbx30) for h/b < 0.12 where, x, h, b = as specified in Sentence (2), and x30 = value of x where the slope ? = 30°, and (ii) for the part of the roof where the slope ? > 30°, taken as, Ca = h/(0.06Cbb) for 0.05 < h/b <= 0.12, and Ca = 2/Cb for h/b > 0.12 | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.10.(5) | Arch Roofs, Curved Roofs and Domes | Except as provided in Sentence (6), Ca for curved roofs shall be determined in accordance with the requirements for arch roofs stated in Sentences (3) and (4). | obc2019_divb | Div B | 4.1.6.10.(5) | 4.1.6.10. Arch Roofs, Curved Roofs and Domes | Except as provided in Sentence (6), Ca for curved roofs shall be determined in accordance with the requirements for arch roofs stated in Sentences (3) and (4). | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.10.(6) | Arch Roofs, Curved Roofs and Domes | Where the slope, a, of a curved roof at its peak is greater than 10°, Ca shall be determined in accordance with the requirements for gable roofs described in Article 4.1.6.9. using a slope equal to the mean slope of the curved roof. | obc2019_divb | Div B | 4.1.6.10.(6) | 4.1.6.10. Arch Roofs, Curved Roofs and Domes | Where the slope, a, of a curved roof at its peak is greater than 10°, Ca shall be determined in accordance with the requirements for gable roofs described in Article 4.1.6.9. using a slope equal to the mean slope of the curved roof. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.10.(7) | Arch Roofs, Curved Roofs and Domes | For domes of circular plan form (see Figure 4.1.6.10.-B), Ca shall, (a) along the central axis parallel to the wind, vary in the same way as for an arch roof with the same rise-to-span ratio, h/b, and (b) off this axis, vary according to Ca(x,y) = Ca(x,0)(1-y/r) where Ca(x,y) = value of Ca at location (x,y), Ca(x,0) = value of Ca on the central axis parallel to the wind, x = distance along the central axis parallel to the wind, y = horizontal coordinate normal to the x direction, and r = radius of dome. | obc2019_divb | Div B | 4.1.6.10.(7) | 4.1.6.10. Arch Roofs, Curved Roofs and Domes | For domes of circular plan form as shown in Figure 4.1.6.10.B., Ca shall, (a) along the central axis parallel to the wind, vary in the same way as for an arch roof with the same rise-to-span ratio, h/b, and (b) off this axis, vary according to, Ca(x,y) = Ca(x,0)(1-y/r) where, Ca(x,y) = value of Ca at location (x,y), Ca(x,0) = value of Ca on the central axis parallel to the wind, x = distance along the central axis parallel to the wind, y = horizontal coordinate normal to the x direction, and r = radius of dome. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.10.(8) | Arch Roofs, Curved Roofs and Domes | For all arch roofs, curved roofs and domes, the slope factor, Cs, shall be as prescribed in Sentences 4.1.6.2.(5) and (6). | obc2019_divb | Div B | 4.1.6.10.(8) | 4.1.6.10. Arch Roofs, Curved Roofs and Domes | For all arch roofs, curved roofs and domes, the slope factor, Cs, shall be as prescribed in Sentences 4.1.6.2.(5) and (6). | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.10.(9) | Arch Roofs, Curved Roofs and Domes | For all arch roofs, curved roofs and domes, the wind exposure factor, Cw, shall be as prescribed in Table 4.1.6.10. | obc2019_divb | Div B | 4.1.6.10.(9) | 4.1.6.10. Arch Roofs, Curved Roofs and Domes | For all arch roofs, curved roofs and domes, the wind exposure factor, Cw, shall be as prescribed in Table 4.1.6.10. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.11.(1) | Snow Loads Due to Sliding | Except as provided in Sentence (2), where an upper roof, or part thereof, slopes downwards with a slope a > 0 towards a lower roof, the snow load, S, on the lower roof, determined in accordance with Articles 4.1.6.2. and 4.1.6.5., shall be augmented in accordance with Sentence (3) to account for the additional load resulting from sliding snow. | obc2019_divb | Div B | 4.1.6.11.(1) | 4.1.6.11. Snow Loads Due to Sliding | Except as provided in Sentence (2), where an upper roof, or part thereof, slopes downwards with a slope a > 0 towards a lower roof, the snow load, S, on the lower roof, determined in accordance with Articles 4.1.6.2. and 4.1.6.5., shall be augmented in accordance with Sentence (3) to account for the additional load resulting from sliding snow. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.11.(2) | Snow Loads Due to Sliding | Sentence (1) need not apply where (a) snow from the upper roof is prevented from sliding by a parapet or other effective means, or (b) the upper roof is not considered slippery and has a slope less than 20°. | obc2019_divb | Div B | 4.1.6.11.(2) | 4.1.6.11. Snow Loads Due to Sliding | Sentence (1) need not apply where, (a) snow from the upper roof is prevented from sliding by a parapet or other effective means, or (b) the upper roof is not considered slippery and has a slope less than 20°. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.11.(3) | Snow Loads Due to Sliding | The total weight of additional snow resulting from sliding shall be taken as half the total weight of snow resulting from the uniform load case prescribed in Article 4.1.6.2. with (a) the accumulation factor Ca = 1.0 for the relevant part of the upper roof, (b) the slope factor, Cs, based on the slope of the lower roof, as prescribed in Sentences 4.1.6.2.(5) and (6), and (c) the sliding snow distributed on the lower roof such that it is a maximum for x = 0 and decreases linearly to 0 at x‚ = xd, as shown in Figure 4.1.6.11., where x and xd are as defined in Article 4.1.6.5. | obc2019_divb | Div B | 4.1.6.11.(3) | 4.1.6.11. Snow Loads Due to Sliding | The total weight of additional snow resulting from sliding shall be taken as half the total weight of snow resulting from the uniform load case prescribed in Article 4.1.6.2. with, (a) the accumulation factor Ca = 1.0 for the relevant part of the upper roof, (b) the slope factor, Cs, based on the slope of the lower roof, as prescribed in Sentences 4.1.6.2.(5) and (6), and (c) the sliding snow distributed on the lower roof such that it is a maximum for x = 0 and decreases linearly to 0 at x‚ = xd, as shown in Figure 4.1.6.11., where x and xd are as defined in Article 4.1.6.5. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.12.(1) | Valleys in Curved or Sloped Roofs | For valleys in curved or sloped roofs with a slope a > 10°, in addition to the full and partial load cases defined in Article 4.1.6.3., the non-uniform load Cases II and III described in Sentences (2) and (3) shall be considered to account for sliding, creeping and movement of meltwater. | obc2019_divb | Div B | 4.1.6.12.(1) | 4.1.6.12. Valleys in Curved or Sloped Roofs | For valleys in curved or sloped roofs with a slope a > 10°, in addition to the full and partial load cases defined in Article 4.1.6.3., the non-uniform load Cases II and III described in Sentences (2) and (3) shall be considered to account for sliding, creeping and movement of meltwater. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.12.(2) | Valleys in Curved or Sloped Roofs | For Case II (see Figure 4.1.6.12.), the accumulation factor, Ca, shall be calculated as follows: Ca = 1/Cb for 0 < x <= b/4, and Ca = 0.5/Cb for b/4 < x <= b/2 where x = horizontal distance from the bottom of the valley, and b = twice the horizontal distance between the bottom of the valley and the peak of the roof surface in question. | obc2019_divb | Div B | 4.1.6.12.(2) | 4.1.6.12. Valleys in Curved or Sloped Roofs | For Case II as shown in Figure 4.1.6.12., the accumulation factor, Ca, shall be calculated as follows: Ca = 1/Cb for 0 < x <= b/4, and Ca = 0.5/Cb for b/4 < x <= b/2 where, x = horizontal distance from the bottom of the valley, and b = twice the horizontal distance between the bottom of the valley and the peak of the roof surface under consideration. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.12.(3) | Valleys in Curved or Sloped Roofs | For Case III (see Figure 4.1.6.12.), Ca shall be calculated as follows: Ca = 1.5/Cb for 0 < x <= b/8, and Ca = 0.5/Cb for b/8 < x <= b/2 where x, b = as specified in Sentence (2). | obc2019_divb | Div B | 4.1.6.12.(3) | 4.1.6.12. Valleys in Curved or Sloped Roofs | For Case III as shown in Figure 4.1.6.12., Ca shall be calculated as follows: Ca = 1.5/Cb for 0 < x <= b/8, and Ca = 0.5/Cb for b/8 < x <= b/2 where, x, b = as specified in Sentence (2). | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.13.(1) | Specific Weight of Snow | For the purposes of calculating snow loads in drifts, the specific weight of snow, g, shall be taken as 4.0 kN/m3 and 0.43Ss + 2.2 kN/m3, whichever is lesser. | obc2019_divb | Div B | 4.1.6.13.(1) | 4.1.6.13. Specific Weight of Snow | For the purposes of calculating snow loads in drifts, the specific weight of snow, g, shall be taken as the lesser of 4.0 kN/m3 and 0.43Ss + 2.2 kN/m3. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.14.(1) | Snow Removal | Snow removal by mechanical, thermal, manual or other means shall not be used as a rationale to reduce design snow loads. | obc2019_divb | Div B | 4.1.6.14.(1) | 4.1.6.14. Snow Removal | Snow removal by mechanical, thermal, manual or other means shall not be used as a rationale to reduce design snow loads. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.15.(1) | Ice Loading of Structures | For lattice structures connected to the building, and other building components or appurtenances involving small width elements subject to significant ice accretion, the weight of ice accretion and the effective area presented to wind shall be as prescribed in CSA S37, "Antennas, Towers, and Antenna-Supporting Structures". | obc2019_divb | Div B | 4.1.6.15.(1) | 4.1.6.15. Ice Loading of Structures | For lattice structures connected to the building, and other building components or appurtenances involving small width elements subject to significant ice accretion, the weight of ice accretion and the effective area presented to wind shall be as prescribed in CSA S37, "Antennas, Towers, and Antenna-Supporting Structures". | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.2.(1) | Specified Snow Load | The specified load, S, due to snow and associated rain accumulation on a roof or any other building surface subject to snow accumulation shall be calculated from the formula, S = Is [Ss (CbCwCsCa) + Sr] where, Is = importance factor for snow load as provided in Table 4.1.6.2.-A., Ss = 1-in-50-year ground snow load, in kPa, determined in accordance with Subsection 1.1.3., Cb = basic roof snow load factor in Sentence (2), Cw = wind exposure factor in Sentences (3) and (4), Cs = slope factor in Sentences (5), (6) and (7), Ca = accumulation factor in Sentence (8), and Sr = 1-in-50-year associated rain load, in kPa, determined in accordance with Subsection 1.1.3., but not greater than Ss(CbCwCsCa). | obc2019_divb | Div B | 4.1.6.2.(1) | 4.1.6.2. Specified Snow Load | The specified load, S, due to snow and associated rain accumulation on a roof or any other building surface subject to snow accumulation shall be calculated from the formula, S = Is [Ss (CbCwCsCa) + Sr] where, Is = importance factor for snow load as provided in Table 4.1.6.2.A, Ss = 1-in-50-year ground snow load, in kPa, determined in accordance with Subsection 1.1.2., Cb = basic roof snow load factor in Sentence (2), Cw = wind exposure factor in Sentences (3) and (4), Cs = slope factor in Sentences (5), (6) and (7), Ca = accumulation factor in Sentence (8), and Sr = 1-in-50-year associated rain load, in kPa, determined in accordance with Subsection 1.1.2., but not greater than Ss(CbCwCsCa). | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.2.(2) | Specified Snow Load | The basic roof snow load factor, Cb, shall a) be determined as follows: (i) Cb = 0.8 for for lc<= (70/C2w), and (b) 1/Cw [1 - (1 - 0.8Cw) exp (- (lcC2w-70)/100)] for for lc> (70/C2w) where, lc = characteristic length of the upper or lower roof, defined as 2w-w²/l, in m, w = smaller plan dimension of the roof, in m, and l =larger plan dimension of the roof, in m, or b) conform to Table 4.1.6.2.-B., using linear interpolation for intermediate values of lcC2w | obc2019_divb | Div B | 4.1.6.2.(2) | 4.1.6.2. Specified Snow Load | The basic roof snow load factor, Cb, shall be, (a) for lc<= (70/C2w), 0.8, and (b) for lc> (70/C2w), (i) calculated using the following formula: 1/Cw [1 - (1 - 0.8Cw) exp (- (lcC2w-70)/100)] where, lc = characteristic length of the upper or lower roof, defined as 2w-w²/l, in metres, w = smaller plan dimension of the roof, in metres, and l =larger plan dimension of the roof, in metres, or (ii) determined in accordance with Table 4.1.6.2.B., using linear interpolation for intermediate values of lcC2w | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.2.(3) | Specified Snow Load | Except as provided for in Sentence (4), the wind exposure factor, Cw, shall be 1.0. | obc2019_divb | Div B | 4.1.6.2.(3) | 4.1.6.2. Specified Snow Load | Except as provided for in Sentence (4), the wind exposure factor, Cw, shall be 1.0. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.2.(4) | Specified Snow Load | For buildings in the Low and Normal Importance Categories as set out in Table 4.1.2.1., the wind exposure factor given in Sentence (3) may be reduced to 0.75 in rural areas, or to 0.5 in exposed areas north of the treeline, where, a) the building is exposed on all sides to wind over open terrain as defined in Clause 4.1.7.3.(5)(a), and is expected to remain so during its life, b) the area of roof under consideration is exposed to the wind on all sides with no significant obstructions on the roof, such as parapet walls, within a distance of at least 10 times the difference between the height of the obstruction and CbCwSs/g metres, where g is the unit weight of snow on roofs as specified in Article 4.1.6.13., and c) the loading does not involve the accumulation of snow due to drifting from adjacent surfaces. | obc2019_divb | Div B | 4.1.6.2.(4) | 4.1.6.2. Specified Snow Load | For buildings in the Low and Normal Importance Categories as set out in Table 4.1.2.1.B., the wind exposure factor given in Sentence (3) may be reduced to 0.75 in rural areas, or to 0.5 in exposed areas north of the treeline, where, (a) the building is exposed on all sides to wind over open terrain as defined in Clause 4.1.7.1.(5)(a), and is expected to remain so during its life, (b) the area of roof under consideration is exposed to the wind on all sides with no significant obstructions on the roof, such as parapet walls, within a distance of at least 10 times the difference between the height of the obstruction and CbCwSs/g metres, where g is the unit weight of snow on roofs as specified in Article 4.1.6.13., and (c) the loading does not involve the accumulation of snow due to drifting from adjacent surfaces. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.2.(5) | Specified Snow Load | Except as provided for in Sentences (6) and (7), the slope factor, Cs, shall be, a) 1.0 where the roof slope, a, is equal to or less than 30°, b) (70° - a)/40° where a is greater than 30° but not greater than 70°, and c) 0 where a exceeds 70°. | obc2019_divb | Div B | 4.1.6.2.(5) | 4.1.6.2. Specified Snow Load | Except as provided for in Sentences (6) and (7), the slope factor, Cs, shall be, (a) 1.0 where the roof slope, a, is equal to or less than 30°, (b) (70° - a)/40° where a is greater than 30° but not greater than 70°, and (c) 0 where a exceeds 70°. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.2.(6) | Specified Snow Load | The slope factor, Cs, for unobstructed slippery roofs where snow and ice can slide completely off the roof shall be a) 1.0 when the roof slope, a, is equal to or less than 15°, b) (60° - a) /45° when a is greater than 15°, but not greater than 60°, and c) 0 when a exceeds 60°. | obc2019_divb | Div B | 4.1.6.2.(6) | 4.1.6.2. Specified Snow Load | The slope factor, Cs, for unobstructed slippery roofs where snow and ice can slide completely off the roof shall be, (a) 1.0 when the roof slope, a, is equal to or less than 15°, (b) (60° - a) /45° when a is greater than 15°, but not greater than 60°, and (c) 0 when a exceeds 60°. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.2.(7) | Specified Snow Load | Unless otherwise stated in this Subsection, the slope factor, Cs, shall be 1.0 when used in conjunction with accumulation factors for increased snow loads. | obc2019_divb | Div B | 4.1.6.2.(7) | 4.1.6.2. Specified Snow Load | Except as otherwise provided in this Subsection, the slope factor, Cs, shall be 1.0 when used in conjunction with accumulation factors for increased snow loads. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.2.(8) | Specified Snow Load | The accumulation factor, Ca, shall be 1.0, which corresponds to the uniform snow load case, except that where appropriate for the shape of the roof, it shall be assigned other values that account for a) increased non-uniform snow loads due to snow drifting onto a roof that is at a level lower than other parts of the same building or at a level lower than another building within 5 m of it horizontally, as prescribed in Articles 4.1.6.5., 4.1.6.6. and 4.1.6.8., b) increased non-uniform snow loads on areas adjacent to roof projections, such as penthouses, large chimneys and equipment, as prescribed in Articles 4.1.6.7. and 4.1.6.8., c) non-uniform snow loads on gable, arch or curved roofs and domes, as prescribed in Article 4.1.6.9. and 4.1.6.10., d) increased snow or ice loads due to snow sliding, as prescribed in Article 4.1.6.11., e) increased snow loads in roof valleys, as prescribed in Article 4.1.6.12., and f) increased snow or ice loads due to meltwater draining from adjacent building elements and roof projections. | obc2019_divb | Div B | 4.1.6.2.(8) | 4.1.6.2. Specified Snow Load | The accumulation factor, Ca, shall be 1.0, which corresponds to the uniform snow load case, except that where appropriate for the shape of the roof, it shall be assigned other values that account for, (a) increased non-uniform snow loads due to snow drifting onto a roof that is at a level lower than other parts of the same building or at a level lower than another building within 5 m of it horizontally, as prescribed in Articles 4.1.6.5., 4.1.6.6. and 4.1.6.8., (b) increased non-uniform snow loads on areas adjacent to roof projections, such as penthouses, large chimneys and equipment, as prescribed in Articles 4.1.6.7. and 4.1.6.8., (c) non-uniform snow loads on, (i) gable roofs, as prescribed in Article 4.1.6.9., and (ii) arched roofs, curved roofs and domes, as prescribed in Article 4.1.6.10., (d) increased snow or ice loads due to snow sliding, as prescribed in Article 4.1.6.11., (e) increased snow loads in roof valleys, as prescribed in Article 4.1.6.12., and (f) increased snow or ice loads due to meltwater draining from adjacent building elements and roof projections. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.2.(9) | Specified Snow Load | For shapes not addressed in Sentence (8), Ca corresponding to the non-uniform snow load case shall be established based on applicable field observations, special analyses including local climatic effects, appropriate model tests or a combination of these methods. | obc2019_divb | Div B | 4.1.6.2.(9) | 4.1.6.2. Specified Snow Load | For shapes not addressed in Sentence (8), Ca corresponding to the non-uniform snow load case shall be established based on applicable field observations, special analyses including local climatic effects, appropriate model tests or a combination of these methods. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.3.(1) | Full and Partial Loading | A roof or other building surface and its structural members subject to loads due to snow accumulation shall be designed for the specified load given in Sentence 4.1.6.2.(1), distributed over the entire loaded area. | obc2019_divb | Div B | 4.1.6.3.(1) | 4.1.6.3. Full and Partial Loading | A roof or other building surface and its structural members subject to loads due to snow accumulation shall be designed for the specified load in Sentence 4.1.6.2.(1), distributed over the entire loaded area. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.3.(2) | Full and Partial Loading | In addition to the distribution in Sentence (1), flat roofs and shed roofs, gable roofs of 15° slope or less, and arched or curved roofs shall be designed for the specified uniform snow load indicated in Sentence 4.1.6.2.(1), which shall be calculated using Ca = 1.0, distributed on any one portion of the loaded area, and half of this load on the remainder of the loaded area, in such a way as to produce the most critical effects on the member concerned. (See Note A-4.1.6.3.(2).) | obc2019_divb | Div B | 4.1.6.3.(2) | 4.1.6.3. Full and Partial Loading | In addition to the distribution in Sentence (1), flat roofs and shed roofs, gable roofs of 15° slope or less, and arched or curved roofs shall be designed for the specified uniform snow load indicated in Sentence 4.1.6.2.(1), which shall be calculated using Ca = 1.0, distributed on any one portion of the loaded area, and half of this load on the remainder of the loaded area, in such a way as to produce the most critical effects on the member concerned. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.4.(1) | Specified Rain Load | Except as provided in Sentence (4), the specified load, S, due to the accumulation of rainwater on a surface whose position, shape and deflection under load make such an accumulation possible, is that resulting from the one-day rainfall determined in conformance with Subsection 1.1.3. and applied over the horizontal projection of the surface and all tributary surfaces. (See Note A-4.1.6.4.(1).) | obc2019_divb | Div B | 4.1.6.4.(1) | 4.1.6.4. Specified Rain Load | Except as provided in Sentence (4), the specified load, S, due to the accumulation of rainwater on a surface whose position, shape and deflection under load make such an accumulation possible, is that resulting from the one-day rainfall determined in conformance with Subsection 1.1.2. and applied over the horizontal projection of the surface and all tributary surfaces. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.4.(2) | Specified Rain Load | The provisions of Sentence (1) apply whether or not the surface is provided with a means of drainage, such as rainwater leaders. | obc2019_divb | Div B | 4.1.6.4.(2) | 4.1.6.4. Specified Rain Load | The provisions of Sentence (1) apply whether or not the surface is provided with a means of drainage, such as rainwater leaders. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.4.(3) | Specified Rain Load | Except as provided in Sentence 4.1.6.2.(1), loads due to rain need not be considered to act simultaneously with loads due to snow. (See Note A-4.1.6.4.(3).) | obc2019_divb | Div B | 4.1.6.4.(3) | 4.1.6.4. Specified Rain Load | Except as provided for in Sentence 4.1.6.2.(1), loads due to rain need not be considered to act simultaneously with loads due to snow. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.4.(4) | Specified Rain Load | Where scuppers are provided and where the position, shape and deflection of the loaded surface make an accumulation of rainwater possible, the loads due to rain shall be the lesser of either the one-day rainfall determined in conformance with Subsection 1.1.3. or a depth of rainwater equal to 30 mm above the level of the scuppers, applied over the horizontal projection of the surface and tributary areas. | obc2019_divb | Div B | 4.1.6.4.(4) | 4.1.6.4. Specified Rain Load | Where scuppers are provided and where the position, shape and deflection of the loaded surface make an accumulation of rainwater possible, the loads due to rain shall be the lesser of either the one-day rainfall determined in conformance with Subsection 1.1.2. or a depth of rainwater equal to 30 mm above the level of the scuppers, applied over the horizontal projection of the surface and tributary areas. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.5.(1) | Multi-level Roofs | The drifting load of snow on a roof adjacent to a higher roof shall be taken as trapezoidal, as shown in Figure 4.1.6.5.-A., and the accumulation factor, Ca, shall be determined as follows: Ca = Ca0 ¬ (Ca0 ¬ 1)(x/xd), for 0< x <= xd or Ca = 1.0, for x > xd where, Ca0 = peak value of Ca at x = 0 as specified in Sentences (3) and (4) and as shown in Figure 4.1.6.5.-B., x = distance from roof step as shown in Figure 4.1.6.5.-A., and xd = length of drift as specified in Sentence (2) and as shown in Figure 4.1.6.5.-A. | obc2019_divb | Div B | 4.1.6.5.(1) | 4.1.6.5. Multi-Level Roofs | The drifting load of snow on a roof adjacent to a higher roof shall be taken as trapezoidal, as shown in Figure 4.1.6.5.A., where the accumulation factor, Ca, is, Ca = Ca0 ¬ (Ca0 ¬ 1)(x/xd), for 0< x <= xd or Ca = 1.0, for x > xd where, Ca0 = peak value of Ca at x = 0 as specified in Sentences (3) and (4) and as shown in Figure 4.1.6.5.A., x = distance from roof step as shown in Figure 4.1.6.5.A., and xd = length of drift as specified in Sentence (2) and as shown in Figure 4.1.6.5.A. | Common Sentence | Yes | Loads
2015 | ON | NBC | Div B | 4.1.6.5.(1) | Multi-level Roofs | The length of the drift, xd, shall be calculated as follows: xd = 5 (CbSs / g) (Ca0 - 1) where, g = specific weight of snow as specified in Article 4.1.6.13. | obc2019_divb | Div B | 4.1.6.5.(2) | 4.1.6.5. Multi-Level Roofs | The length of the drift, xd, shall be calculated as follows: xd = 5 (CbSs / g) (Ca0 - 1) where, g = specific weight of snow as specified in Article 4.1.6.13. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.5.(3) | Multi-level Roofs | The value of Ca0 for each of Cases I, II and III shall be the lesser of, Ca0 = bgh/(CbSs) and Ca0 = F/Cb, where, ? = 1.0 for Case I and 0.67 for Cases II and III, h = difference in elevation between the lower roof surface and the top of the parapet on the upper roof as shown in Figure 4.1.6.5.A., and F = 0.35b(g(lcs - 5h'p)/Ss)0.5 + Cb, but F <= 5 for Cws = 1.0 where, Cws = value for Cw applicable to the source of drifting, lcs = the characteristic length of the source area for drifting, defined as lcs=2ws - w2s/ls, where ws and ls are respectively the shorter and longer dimensions of the relevant source areas for snow drifting shown in Figure 4.1.6.5.B. for Cases I, II and III, and where, h'p = hp - (0.8Ss/g), but 0<=h'p <=(lcs/5) where hp = height of the roof perimeter parapet of the source area, to be taken as zero unless all the roof edges of the source area have parapets. | obc2019_divb | Div B | 4.1.6.5.(3) | 4.1.6.5. Multi-Level Roofs | The value of Ca0 for each of Cases I, II and III shall be the lesser of, Ca0 = bgh/(CbSs) and Ca0 = F/Cb, where, ? = 1.0 for Case I and 0.67 for Cases II and III, h = difference in elevation between the lower roof surface and the top of the parapet on the upper roof as shown in Figure 4.1.6.5.A., and F = 0.35b(g(lcs - 5h'p)/Ss)0.5 + Cb, but F <= 5 for Cws = 1.0 where, Cws = value for Cw applicable to the source of drifting, lcs = the characteristic length of the source area for drifting, defined as lcs=2ws - w2s/ls, where ws and ls are respectively the shorter and longer dimensions of the relevant source areas for snow drifting shown in Figure 4.1.6.5.B. for Cases I, II and III, and where, h'p = hp - (0.8Ss/g), but 0<=h'p <=(lcs/5) where hp = height of the roof perimeter parapet of the source area, to be taken as zero unless all the roof edges of the source area have parapets. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.5.(4) | Multi-level Roofs | The value of Ca0 shall be the highest of Cases I, II and III, considering the different roof source areas for drifting snow, as specified in Sentence (3) and Figure 4.1.6.5-B. | obc2019_divb | Div B | 4.1.6.5.(4) | 4.1.6.5. Multi-Level Roofs | The value of Ca0 shall be the highest of Cases I, II and III, considering the different roof source areas for drifting snow, as specified in Sentence (3) and Figure 4.1.6.5.B. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.6.(1) | Horizontal Gap between a Roof and a Higher Roof | Where the roof of one building is separated by a distance, a, from an adjacent building with a higher roof as shown in Figure 4.1.6.5.-A., the influence of the adjacent building on the value of the accumulation factor, Ca, for the lower roof shall be determined as follows: (a) if a > 5 m, the influence of the adjacent building on Ca for the lower roof xan be ignored, and (b) if a < 5 m, Ca for the lower roof shall be calculated in accordance with Article 4.1.6.5. for values of x >= a. | obc2019_divb | Div B | 4.1.6.6.(1) | 4.1.6.6. Horizontal Gap Between a Roof and a Higher Roof | Where the roof of one building is separated by a distance, a, from an adjacent building with a higher roof as shown in Figure 4.1.6.5.A., the influence of the adjacent building on the value of the accumulation factor, Ca, for the lower roof shall be determined as follows: (a) if a > 5 m, the influence of the adjacent building on Ca need not be considered, and (b) if a < 5 m, Ca for the lower roof shall be calculated in accordance with Article 4.1.6.5. for values of x >= a. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.7.(1) | Areas Adjacent to Roof Projections | Except as provided in Sentences (2) and (3), the accumulation factor, Ca, for areas adjacent to roof-mounted vertical projections shall be calculated in accordance with Sentence 4.1.6.5.(1) using the following values for the peak accumulation factor, Ca0, and the drift length, xd: a) Ca0 shall be taken as the lesser of 0.67gh/(CbSs) and gl0/(7.5CbSs) +1, b) xd shall be taken as the lesser of, (i) 3.35h, and (ii) (2/3)l0, where, h = height of the projection, and l0 = longest horizontal dimension of the projection. (See Note A-4.1.6.7.(1).) | obc2019_divb | Div B | 4.1.6.7.(1) | 4.1.6.7. Areas Adjacent to Roof Projections | Except as provided in Sentences (2) and (3), the accumulation factor, Ca, for areas adjacent to roof-mounted vertical projections shall be calculated in accordance with Sentence 4.1.6.5.(1) using the following values for the peak accumulation factor, Ca0, and the drift length, xd: (a) Ca0 shall be taken as the lesser of 0.67gh/(CbSs) and gl0/(7.5CbSs) +1, (b) xd shall be taken as the lesser of, (i) 3.35h, and (ii) (2/3)l0, where, h = height of the projection, and l0 = longest horizontal dimension of the projection. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.7.(2) | Areas Adjacent to Roof Projections | Ca is permitted to be calculated in accordance with Article 4.1.6.5. for larger projections. (See Note A-4.1.6.7.(2).) | obc2019_divb | Div B | 4.1.6.7.(2) | 4.1.6.7. Areas Adjacent to Roof Projections | Ca is permitted to be calculated in accordance with Article 4.1.6.5. for larger projections. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.7.(3) | Areas Adjacent to Roof Projections | Where the longest horizontal dimension of the roof projection, l0, is less than 3 m, the drift surcharge adjacent to the projection need not be considered. | obc2019_divb | Div B | 4.1.6.7.(3) | 4.1.6.7. Areas Adjacent to Roof Projections | Where the longest horizontal dimension of the roof projection, l0, is less than 3 m, the drift surcharge adjacent to the projection need not be considered. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.8.(1) | Snow Drift at Corners | The drift loads on the lower level roof against the two faces of an outside corner of an upper level roof or roof obstruction shall be extended radially around the corner as shown in Figure 4.1.6.8.-A and may be taken as the least severe of the drift loads lying against the two faces of the corner. | obc2019_divb | Div B | 4.1.6.8.(1) | 4.1.6.8. Snow Drift at Corners | The drift loads on the lower level roof against the two faces of an outside corner of an upper level roof or roof obstruction shall be extended radially around the corner as shown in Figure 4.1.6.8.A. and may be taken as the least severe of the drift loads lying against the two faces of the corner. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.8.(2) | Snow Drift at Corners | The drift loads on the lower level roof against the two faces of an inside corner of an upper level roof or a parapet shall be calculated for each face and applied as far as the bisector of the corner angle as shown in Figure 4.1.6.8.-B. | obc2019_divb | Div B | 4.1.6.8.(2) | 4.1.6.8. Snow Drift at Corners | The drift loads on the lower level roof against the two faces of an inside corner of an upper level roof or a parapet shall be calculated for each face and applied as far as the bisector of the corner angle as shown in Figure 4.1.6.8.B. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.9.(1) | Gable Roofs (See Note A-4.1.6.9.) | For all gable roofs, the full and partial load cases defined in Article 4.1.6.3. shall be considered. | obc2019_divb | Div B | 4.1.6.9.(1) | 4.1.6.9. Gable Roofs | For all gable roofs, the full and partial load cases defined in Article 4.1.6.3. shall be considered. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.9.(2) | Gable Roofs (See Note A-4.1.6.9.) | For gable roofs with a slope of a > 15°, the unbalanced load case shall also be considered by setting the values of the accumulation factor, Ca, as follows: (a) on the upwind side of the roof peak, Ca shall be taken as 0, and (b) on the downwind side of the roof peak, Ca shall be taken as, (i) 0.25 + a/20, where 15° <= a <= 20°, and (ii) 1.25, where 20° < a <= 90°. | obc2019_divb | Div B | 4.1.6.9.(2) | 4.1.6.9. Gable Roofs | For gable roofs with a slope of a > 15°, the unbalanced load case shall also be considered by setting the values of the accumulation factor, Ca, as follows: (a) on the upwind side of the roof peak, Ca shall be taken as 0, and (b) on the downwind side of the roof peak, Ca shall be taken as, (i) 0.25 + a/20, where 15° <= a <= 20°, and (ii) 1.25, where 20° < a <= 90°. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.9.(3) | Gable Roofs | For all gable roofs, the slope factor, Cs, shall be as prescribed in Sentences 4.1.6.2.(5) and (6). | obc2019_divb | Div B | 4.1.6.9.(3) | 4.1.6.9. Gable Roofs | For all gable roofs, the slope factor, Cs, shall be as prescribed in Sentences 4.1.6.2.(5) and (6). | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.6.9.(4) | Gable Roofs | For all gable roofs, the wind exposure factor, Cw, shall be, (a) as prescribed in Sentences 4.1.6.2.(3) and (4) for the full and partial load cases, and (b) 1.0 for the unbalanced load case referred to in Sentence (2). | obc2019_divb | Div B | 4.1.6.9.(4) | 4.1.6.9. Gable Roofs | For all gable roofs, the wind exposure factor, Cw, shall be, (a) as prescribed in Sentences 4.1.6.2.(3) and (4) for the full and partial load cases, and (b) 1.0 for the unbalanced load case referred to in Sentence (2). | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.1.(1) | Specified Wind Load | The specified wind loads for a building and its components shall be determined using the Static, Dynamic or Wind Tunnel Procedure as provided in Sentences (2) to (5). | obc2019_divb | Div B | 4.1.7.1.(1) | 4.1.7.1. Specified Wind Load | The specified wind loads for a building and its components shall be determined using the Static, Dynamic or Wind Tunnel Procedure as provided in Sentences (2) to (5). | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.1.(2) | Specified Wind Load | For the design of buildings that are not dynamically sensitive, as defined in Sentence 4.1.7.2.(1), one of the following procedures shall be used to determine the specified wind loads: (a) the Static Procedure described in Article 4.1.7.3., (b) the Dynamic Procedure described in Article 4.1.7.8., or (c) the Wind Tunnel Procedure described in Article 4.1.7.12. | obc2019_divb | Div B | 4.1.7.1.(2) | 4.1.7.1. Specified Wind Load | For the design of buildings that are not classified as dynamically sensitive in accordance with Sentence 4.1.7.2.(1), one of the following procedures shall be used to determine the specified wind loads: (a) the Static Procedure described in Article 4.1.7.3., (b) the Dynamic Procedure described in Article 4.1.7.8., or (c) the Wind Tunnel Procedure described in Article 4.1.7.12. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.1.(3) | Specified Wind Load | For the design of buildings that are dynamically sensitive, as defined in Sentence 4.1.7.2.(2), one of the following procedures shall be used to determine the specified wind loads: (a) the Dynamic Procedure described in Article 4.1.7.8., or (b) the Wind Tunnel Procedure described in Article 4.1.7.12. | obc2019_divb | Div B | 4.1.7.1.(3) | 4.1.7.1. Specified Wind Load | For the design of buildings that are classified as dynamically sensitive in accordance with Sentence 4.1.7.2.(2), one of the following procedures shall be used to determine the specified wind loads: (a) the Dynamic Procedure described in Article 4.1.7.8., or (b) the Wind Tunnel Procedure described in Article 4.1.7.12. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.1.(4) | Specified Wind Load | For the design of buildings that may be subject to wake buffeting or channelling effects from nearby buildings, or that are very dynamically sensitive, as defined in Sentence 4.1.7.2.(3), the Wind Tunnel Procedure described in Article 4.1.7.12., shall be used to determine the specified wind loads. | obc2019_divb | Div B | 4.1.7.1.(4) | 4.1.7.1. Specified Wind Load | For the design of buildings that may be subject to wake buffeting or channelling effects from nearby buildings, or that are classified as very dynamically sensitive in accordance with Sentence 4.1.7.2.(3), the Wind Tunnel Procedure described in Article 4.1.7.12. shall be used to determine the specified wind loads. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.1.(5) | Specified Wind Load | For the design of cladding and secondary structural members, one of the following procedures shall be used to determine the specified wind loads: (a) the Static Procedure described in Article 4.1.7.3., or (b) the Wind Tunnel Procedure described in Article 4.1.7.12. | obc2019_divb | Div B | 4.1.7.1.(5) | 4.1.7.1. Specified Wind Load | For the design of cladding and secondary structural members, one of the following procedures shall be used to determine the specified wind loads: (a) the Static Procedure described in Article 4.1.7.3., or (b) the Wind Tunnel Procedure described in Article 4.1.7.12. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.1.(6) | Specified Wind Load | Computational fluid dynamics shall not be used to determine the specified wind loads for a building and its components. (See Note A-4.1.7.1.(6).) | obc2019_divb | Div B | 4.1.7.1.(6) | 4.1.7.1. Specified Wind Load | Computational fluid dynamics shall not be used to determine the specified wind loads for a building and its components. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.10.(1) | Interior Walls and Partitions | In the design of interior walls and partitions, due consideration shall be given to differences in air pressure on opposite sides of the wall or partition that may result from a) pressure differences between the windward and leeward sides of a building, b) stack effects due to a difference in air temperature between the exterior and interior of the building, and c) air pressurization by the mechanical services of the building. | obc2019_divb | Div B | 4.1.7.10.(1) | 4.1.7.10. Interior Walls and Partitions | In the design of interior walls and partitions, due consideration shall be given to differences in air pressure on opposite sides of the wall or partition that may result from, (a) pressure differences between the windward and leeward sides of a building, (b) stack effects due to a difference in air temperature between the exterior and interior of the building, and (c) air pressurization by the mechanical services of the building. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.11.(1) | Exterior Ornamentations, Equipment and Appendages | The effects of wind loads on exterior ornamentations, equipment and appendages, including the increase in exposed area as a result of ice buildup as described in CSA S37, "Antennas, Towers, and Antenna-Supporting Structures", shall be considered in the structural design of the connections and the building. | obc2019_divb | Div B | 4.1.7.11.(1) | 4.1.7.11. Exterior Ornamentations, Equipment and Appendages | The effects of wind loads on exterior ornamentations, equipment and appendages, including the increase in exposed area as a result of ice buildup as described in CSA S37, "Antennas, Towers, and Antenna-Supporting Structures", shall be considered in the structural design of the connections and the building. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.11.(2) | Exterior Ornamentations, Equipment and Appendages | Where there are a number of similar components, the net increase in force is permitted to be based on the total area for all similar components as opposed to the summation of forces of individual elements. | obc2019_divb | Div B | 4.1.7.11.(2) | 4.1.7.11. Exterior Ornamentations, Equipment and Appendages | Where there are a number of similar components, the net increase in force is permitted to be based on the total area for all similar components as opposed to the summation of forces of individual elements. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.12.(1) | Wind Tunnel Procedure | Except as provided in Sentences (2) and (3), wind tunnel tests on scale models to determine wind loads on buildings shall be conducted in accordance with ASCE/SEI 49, "Wind Tunnel Testing for Buildings and Other Structures". | obc2019_divb | Div B | 4.1.7.12.(1) | 4.1.7.12. Wind Tunnel Procedure | Except as provided in Sentences (2) and (3), wind tunnel tests on scale models to determine wind loads on buildings shall be conducted in accordance with ASCE/SEI 49, "Wind Tunnel Testing for Buildings and Other Structures". | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.12.(2) | Wind Tunnel Procedure | Where an adjacent building provides substantial sheltering effect, the wind loads for the main structural system shall be no lower than 80% of the loads determined from tests described in Sentence (1) with the effect of the sheltering building removed as applied to (a) the base shear force for buildings with ratio of height to minimum effective width, as described in Sentence 4.1.7.2.(2), less than or equal to 1.0, or (b) the base moment for buildings with a ratio of height to minimum effective width greater than 1.0. | obc2019_divb | Div B | 4.1.7.12.(2) | 4.1.7.12. Wind Tunnel Procedure | Where an adjacent building provides substantial sheltering effect, the wind loads for the main structural system shall be no lower than 80% of the loads determined from tests described in Sentence (1) with the effect of the sheltering building removed as applied to, (a) the base shear force for buildings with ratio of height to minimum effective width, as described in Sentence 4.1.7.2.(2), less than or equal to 1.0, or (b) the base moment for buildings with a ratio of height to minimum effective width greater than 1.0. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.12.(3) | Wind Tunnel Procedure | For the design of cladding and secondary structural members, the exterior wind loads determined from the wind tunnel tests shall be no less onerous than those determined by analysis in accordance with Article 4.1.7.3. using the following assumptions: (a) Cp = ±0.72 and Cg= 2.5, where the buildings height is greater than 20 m or greater than its minimum effective width, and (b) CpCg = 80% of the values for zones w and r provided in Article 4.1.7.6., where the buildingâ€™s height is less than or equal to 20 m and no greater than its minimum effective width. | obc2019_divb | Div B | 4.1.7.12.(3) | 4.1.7.12. Wind Tunnel Procedure | For the design of cladding and secondary structural members, the exterior wind loads determined from the wind tunnel tests shall be no less onerous than those determined by analysis in accordance with Article 4.1.7.3. using the following assumptions: (a) Cp = Ã‚Â±0.72 and Cg = 2.5, where the height of the building is greater than 20 m or greater than its minimum effective width, and (b) CpCg = 80% of the values for zones w and r provided in Article 4.1.7.6., where the height of the building is less than or equal to 20 m and no greater than its minimum effective width. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.2.(1) | Classification of Buildings | Except as provided in Sentences (2) and (3), a building is permitted to be classified as not dynamically sensitive. | obc2019_divb | Div B | 4.1.7.2.(1) | 4.1.7.2. Classification of Buildings | Except as provided in Sentences (2) and (3), a building is permitted to be classified as not dynamically sensitive. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.2.(2) | Classification of Buildings | A building shall be classified as dynamically sensitive if (a) its lowest natural frequency is less than 1 Hz and greater than 0.25 Hz, (b) its height is greater than 60 m, or (c) its height is greater than 4 times its minimum effective width, where the effective width, w, of a building shall be taken as EQUATION where the summations are over the height of the building for a given wind direction, hi is the height above grade to level i, and wi is the width normal to the wind direction at height hi; the minimum effective width is the lowest value of the effective width considering all wind directions. | obc2019_divb | Div B | 4.1.7.2.(2) | 4.1.7.2. Classification of Buildings | A building shall be classified as dynamically sensitive if, (a) its lowest natural frequency is less than 1 Hz and greater than 0.25 Hz, (b) its height is greater than 60 m, or (c) its height is greater than 4 times its minimum effective width considering all wind directions, where the effective width, w, of a building shall be taken as, EQUATION where, the summations are over the height of the building for a given wind direction, hi = the height above grade to level i, and wi = the width normal to the wind direction at height hi. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.2.(3) | Classification of Buildings | A building shall be classified as very dynamically sensitive if (a) its lowest natural frequency is less than or equal to 0.25 Hz, or(b) its height is more than 6 times its minimum effective width as defined in Clause (2)(c). | obc2019_divb | Div B | 4.1.7.2.(3) | 4.1.7.2. Classification of Buildings | A building shall be classified as very dynamically sensitive if, (a) its lowest natural frequency is less than or equal to 0.25 Hz, or (b) its height is more than 6 times its minimum effective width, where the minimum effective width is determined in accordance with Clause (2)(c). | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.3.(1) | Static Procedure | The specified external pressure or suction due to wind on part or all of a surface of a building shall be calculated as follows: EQUATION where p = specified external pressure acting statically and in a direction normal to the surface, considered positive when the pressure acts towards the surface and negative when it acts away from the surface, Iw = importance factor for wind load, as provided in Table 4.1.7.3., q= reference velocity pressure, as provided in Sentence (4), Ce = exposure factor, as provided in Sentences (5) and (7), Ct = topographic factor, as provided in Article 4.1.7.4., Cg = gust effect factor, as provided in Sentence (8), and Cp = external pressure coefficient, as provided in Articles 4.1.7.5. and 4.1.7.6. | obc2019_divb | Div B | 4.1.7.3.(1) | 4.1.7.3. Static Procedure | The specified external pressure or suction due to wind on part or all of a surface of a building shall be calculated using the following formula: EQUATION where, p = specified external pressure acting statically and in a direction normal to the surface, considered positive when the pressure acts towards the surface and negative when it acts away from the surface, Iw = importance factor for wind load, as provided in Table 4.1.7.3., q = reference velocity pressure, as provided in Sentence (4), Ce = exposure factor, as provided in Sentences (5) and (7), Ct = topographic factor, as provided in Article 4.1.7.4., Cg = gust effect factor, as provided in Sentence (8), and Cp = external pressure coefficient, as provided in Articles 4.1.7.5. and 4.1.7.6. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.3.(10) | Static Procedure | The internal gust effect factor, Cgi, shall be 2.0, except it is permitted to be calculated using the following equation for large structures enclosing a single large unpartitioned volume that does not have numerous overhead doors or openings: EQUATION where, V0 = internal volume in m3, and A = total area of all exterior openings of the volume in m2. (See Note A-4.1.7.3.(10).) | obc2019_divb | Div B | 4.1.7.3.(10) | 4.1.7.3. Static Procedure | The internal gust effect factor, Cgi, shall be 2.0, except it is permitted to be calculated using the following equation for large structures enclosing a single large unpartitioned volume that does not have numerous overhead doors or openings: EQUATION where, V0 = internal volume in m3, and A = total area of all exterior openings of the volume in m2. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.3.(2) | Static Procedure | The net wind load for the building as a whole shall be the algebraic difference of the loads on the windward and the leeward surfaces, and in some cases may be calculated as the sum of the products of the external pressures or suctions and the areas of the surfaces over which they are averaged as provided in Sentence (1). | obc2019_divb | Div B | 4.1.7.3.(2) | 4.1.7.3. Static Procedure | The net wind load for the building as a whole shall be the algebraic difference of the loads on the windward and the leeward surfaces, and in some cases may be calculated as the sum of the products of the external pressures or suctions and the areas of the surfaces over which they are averaged as provided in Sentence (1). | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.3.(3) | Static Procedure | The net specified pressure due to wind on part or all of a surface of a building shall be the algebraic difference, such as to produce the most critical effect, of the external pressure or suction calculated in accordance with Sentence (1) and the specified internal pressure or suction due to wind calculated as follows: EQUATION where pi = specified internal pressure acting statically and in a direction normal to the surface, either as a pressure directed towards the surface or as a suction directed away from the surface, Iw, q, Ct = as defined in Sentence (1), Cei = exposure factor for internal pressure, as provided in Sentence (7), Cgi = internal gust effect factor, as provided in Sentence (10), and Cpi = internal pressure coefficient, as provided in Article 4.1.7.7. | obc2019_divb | Div B | 4.1.7.3.(3) | 4.1.7.3. Static Procedure | The net specified pressure due to wind on part or all of a surface of a building shall be the algebraic difference, such as to produce the most critical effect, of the external pressure or suction calculated in accordance with Sentence (1) and the specified internal pressure or suction due to wind calculated as follows: EQUATION where, pi = specified internal pressure acting statically and in a direction normal to the surface, either as a pressure directed toward the surface or as a suction directed away from the surface, Iw = importance factor for wind load, as defined in Sentence (1), q = reference velocity pressure, as defined in Sentence (1), Cei = exposure factor for internal pressure, as provided in Sentence (7), Ct = topographic factor, as defined in Sentence (1), Cgi = internal gust effect factor, as provided in Sentence (10), and Cpi = internal pressure coefficient, as provided in Article 4.1.7.7. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.3.(4) | Static Procedure | The reference velocity pressure, q, shall be the appropriate value determined in conformance with Subsection 1.1.3. based on a probability of being exceeded in any one year of 1-in-50. | obc2019_divb | Div B | 4.1.7.3.(4) | 4.1.7.3. Static Procedure | The reference velocity pressure, q, shall be the appropriate value determined in conformance with Subsection 1.1.2. based on a probability of being exceeded in any one year of 1-in-50. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.3.(5) | Static Procedure | The exposure factor, Ce, shall be based on the reference height, h, determined in accordance with Sentence (6), for the surface or part of the surface under consideration and shall be a) (h/10)0.2 but not less than 0.9 for open terrain, where open terrain is level terrain with only scattered buildings, trees or other obstructions, open water or shorelines thereof, b) 0.7(h/12)0.3 but not less than 0.7 for rough terrain, where rough terrain is suburban, urban or wooded terrain extending upwind from the building uninterrupted for at least 1 km or 20 times the height of the building, whichever is greater, or c) an intermediate value between the two exposures defined in Clauses (a) and (b) in cases where the site is less than 1 km or 20 times the height of the building from a change in terrain conditions, whichever is greater, provided an appropriate interpolation method is used (see Note A-4.1.7.3.(5)(c)). | obc2019_divb | Div B | 4.1.7.3.(5) | 4.1.7.3. Static Procedure | The exposure factor Ce, shall be based on the reference height, h, determined in accordance with Sentence (6) for the surface or part of the surface under consideration and shall be, (a) (h/10)0.2 but not less than 0.9 for open terrain, where open terrain is level terrain with only scattered buildings, trees or other obstructions, open water or shorelines thereof, (b) 0.7(h/12)0.3 but not less than 0.7 for rough terrain, where rough terrain is suburban, urban or wooded terrain extending upwind from the building uninterrupted for at least 1 km or 20 times the height of the building, whichever is greater, or (c) an intermediate value between the two exposures defined in Clauses (a) and (b) in cases where the site is less than 1Ã‚ km or 20 times the height of the building from a change in terrain conditions, whichever is greater, provided an appropriate interpolation method is used. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.3.(6) | Static Procedure | The reference height, h, shall be determined as follows: (a) for buildings whose height is less than or equal to 20 m and less than the smaller plan dimension, h shall be the mid-height of the roof above grade, but not less than 6 m, (b) for other buildings, h shall be (i) the actual height above grade of the point on the windward wall for which external pressures are being calculated, (ii) the mid-height of the roof for pressures on surfaces parallel to the wind direction, and (iii) the mid-height of the building for pressures on the leeward wall, and (c) for any structural element exposed to wind, h shall be the mid-height of the element above the ground. | obc2019_divb | Div B | 4.1.7.3.(6) | 4.1.7.3. Static Procedure | The reference height, h, shall be determined as follows: (a) for buildings with height less than or equal to 20 m and less than the smaller plan dimension, h shall be the mid-height of the roof above grade, but shall not be less than 6 m, (b) for other buildings, h shall be, (i) the actual height above grade of the point on the windward wall for which external pressures are being calculated, (ii) the mid-height of the roof for pressures on surfaces parallel to the wind direction, and (iii) the mid-height of the building for pressures on the leeward wall, and (c) for any structural element exposed to wind, h shall be the mid-height of the element above the ground. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.3.(7) | Static Procedure | The exposure factor for internal pressure, Cei, shall be determined as follows: (a) for buildings whose height is greater than 20 m and that have a dominant opening, Cei shall be equal to the exposure factor for external pressures, Ce, calculated at the mid-height of the dominant opening, and (b) for other buildings, Cei shall be the same as the exposure factor for external pressures, Ce, calculated for a reference height, h, equal to the mid-height of the building or 6 m, whichever is greater. | obc2019_divb | Div B | 4.1.7.3.(7) | 4.1.7.3. Static Procedure | The exposure factor for internal pressure, Cei, shall be determined as follows: (a) for buildings whose height is greater than 20 m and that have a dominant opening, Cei shall be equal to the exposure factor for external pressures, Ce, calculated at the mid-height of the dominant opening, and (b) for other buildings, Cei shall be the same as the exposure factor for external pressures, Ce, calculated for a reference height, h, equal to the mid-height of the building or 6 m, whichever is greater. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.3.(8) | Static Procedure | Except as provided in Sentences (9) and 4.1.7.6.(1), the gust effect factor, Cg, shall be one of the following values: (a) 2.0 for the building as a whole and main structural members, or (b) 2.5 for external pressures and suctions on secondary structural members including cladding. | obc2019_divb | Div B | 4.1.7.3.(8) | 4.1.7.3. Static Procedure | Except as provided in Sentences (9) and 4.1.7.6.(1), the gust effect factor, Cg, shall be one of the following values: (a) 2.0 for the building as a whole and main structural members, or (b) 2.5 for external pressures and suctions on secondary structural members including cladding. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.3.(9) | Static Procedure | For cases where Cg and Cp are combined into a single product, CpCg, as provided in Article 4.1.7.6., the values Cp and Cg need not be independently specified. (See Article 4.1.7.6.) | obc2019_divb | Div B | 4.1.7.3.(9) | 4.1.7.3. Static Procedure | For cases where Cg and Cp are combined into a single product, CpCg, as provided in Article 4.1.7.6., the values Cp and Cg need not be independently specified. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.4.(1) | Topographic Factor | Except as provided in Sentence (2), the topographic factor, Ct, shall be taken as 1.0. | obc2019_divb | Div B | 4.1.7.4.(1) | 4.1.7.4. Topographic Factor | Except as provided in Sentence (2), the topographic factor, Ct, shall be taken as 1.0. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.4.(2) | Topographic Factor | For buildings on hills or escarpments with slope, Hh/(2Lh), greater than 0.1 (see Figure 4.1.7.4)., the topographic factor, Ct, shall be calculated as follows: EQUATION1 where, EQUATION2 where, DSmax = applicable values from Table 4.1.7.4., x‚ = horizontal distance from the peak of the hill or escarpment, Lh = horizontal distance upwind from the peak to the point where the ground surface lies at half the height of the hill or escarpment, or 2Hh (where Hh is the height of the hill or escarpment), whichever is greater, Z = height above ground, and k and a = applicable constants from Table 4.1.7.4. based on shape of hill or escarpment. | obc2019_divb | Div B | 4.1.7.4.(2) | 4.1.7.4. Topographic Factor | For buildings on hills or escarpments with slope, Hh/(2Lh), greater than 0.1 as shown in Figure 4.1.7.4., the topographic factor, Ct, shall be calculated as follows: EQUATION1 where, EQUATION2 where, DSmax = applicable values from Table 4.1.7.4., x‚ = horizontal distance from the peak of the hill or escarpment, Lh = horizontal distance upwind from the peak to the point where the ground surface lies at half the height of the hill or escarpment, or 2Hh where Hh is the height of the hill or escarpment, whichever is greater, Z = height above ground, and k and a = applicable constants from Table 4.1.7.4. based on shape of hill or escarpment. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.5.(1) | External Pressure Coefficients | Applicable values of external pressure coefficients, Cp, are provided in, (a) Sentences (2) to (5), and (b) Article 4.1.7.6. for certain shapes of low buildings. | obc2019_divb | Div B | 4.1.7.5.(1) | 4.1.7.5. External Pressure Coefficients | Applicable values of external pressure coefficients, Cp, are provided in, (a) Sentences (2) to (5), and (b) Article 4.1.7.6. for certain shapes of low buildings. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.5.(2) | External Pressure Coefficients | For the design of the main structural system, the value of Cp shall be established as follows, where H is the height of the building and D is the width of the building parallel to the wind direction: (a) on the windward face, Cp‚ = 0.6 for H/D < 0.25 = 0.27(H/D + 2) for 0.25 <= H/D < 1.0 = 0.8 for H/D >= 1.0, (b) on the leeward face, Cp‚ = -0.3 for H/D < 0.25 = -0.27(H/D + 0.88) for 0.25 <= H/D < 1.0 = -0.5 for H/D > 1.0, and (c) on the walls parallel to the wind, Cp = ¬0.7. (See Note A-4.1.7.5.(2) and (3).) | obc2019_divb | Div B | 4.1.7.5.(2) | 4.1.7.5. External Pressure Coefficients | For the design of the main structural system, the value of Cp shall be established as follows, where H is the height of the building and D is the width of the building parallel to the wind direction: (a) on the windward face, Cp‚ = 0.6 for H/D < 0.25 = 0.27(H/D + 2) for 0.25 <= H/D < 1.0 = 0.8 for H/D >= 1.0, (b) on the leeward face, Cp‚ = -0.3 for H/D < 0.25 = -0.27(H/D + 0.88) for 0.25 <= H/D < 1.0 = -0.5 for H/D > 1.0, and (c) on the walls parallel to the wind, Cp = ¬0.7. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.5.(3) | External Pressure Coefficients | For the design of roofs, the value of Cp shall be established as follows, where x is the distance from the upwind edge of the roof: a) for H/D >= 1.0, Cp = ¬1.0, and b) for H/D < 1.0, Cp = ¬1.0 for x < H = ¬0.5 for x > H (See Note A-4.1.7.5.(2) and (3).) | obc2019_divb | Div B | 4.1.7.5.(3) | 4.1.7.5. External Pressure Coefficients | For the design of roofs, the value of Cp shall be established as follows, where x is the distance from the upwind edge of the roof: (a) for H/D >= 1.0, Cp = ¬1.0, and (b) for H/D < 1.0, Cp = ¬1.0 for x < H = ¬0.5 for x > H (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.5.(4) | External Pressure Coefficients | For the design of the cladding and of secondary structural elements supporting the cladding, the value of Cp shall be established as follows, where W and D are the widths of the building: a) on walls, Cp shall be taken as ±0.9, except that within a distance equal to the larger of 0.1D and 0.1W from a building corner, the negative value of Cp shall be taken as -1.2, b) on walls where vertical ribs deeper than 1 m are placed on the facade, Cp shall be taken as ±0.9, except that, within a distance equal to the larger of 0.2D and 0.2W from a building corner, the negative value of Cp shall be taken a s-1.4, and c) on roofs, Cp shall be taken as -1.0, except that i) within a distance equal to the larger of 0.1D and 0.1W from a roof edge, Cp shall be taken as- 1.5, ii) in a zone that is within a distance equal to the larger of 0.2W and 0.2D from a roof corner, Cp shall be taken as -2.3 but is permitted to be taken as -2.0 for roofs with perimeter parapets that are higher than 1 m, and iii) on lower levels of flat stepped roofs, positive pressure coefficients established for the walls of the steps apply for a distance b (see Article 4.1.7.6. for the definition of b). | obc2019_divb | Div B | 4.1.7.5.(4) | 4.1.7.5. External Pressure Coefficients | For the design of the cladding and of secondary structural elements supporting the cladding, the value of Cp shall be established as follows, where W and D are the widths of the building: (a) on walls, Cp shall be taken as ±0.9, except that within a distance equal to the larger of 0.1D and 0.1W from a building corner the negative value of Cp shall be taken as ¬1.2, (b) on walls where vertical ribs deeper than 1 m are placed on the facade, Cp shall be taken as ±0.9, except that within a distance equal to the larger of 0.2D and 0.2W from a building corner the negative value of Cp shall be taken as¬1.4, and (c) on roofs, Cp shall be taken as‚¬1.0, except that, (i) within a distance equal to the larger of 0.1D and 0.1W from a roof edge, Cp shall be taken as ¬1.5, (ii) in a zone that is within a distance equal to the larger of 0.2D and 0.2W from a roof corner, Cp shall be taken as -2.3 but is permitted to be taken as -2.0 for roofs with perimeter parapets that are higher than 1 m, and (iii) on lower levels of flat stepped roofs, positive pressure coefficients established for the walls of the steps apply for a distance b as shown in Figure 4.1.7.6.D. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.5.(5) | External Pressure Coefficients | For the design of balcony guards, the internal pressure coefficient, Cpi, shall be taken as zero and the value of Cp shall be taken as Â±0.9, except that within a distance equal to the larger of 0.1W and 0.1D from a building corner, Cp shall be taken as Â±1.2. | obc2019_divb | Div B | 4.1.7.5.(5) | 4.1.7.5. External Pressure Coefficients | For the design of balcony guards, the internal pressure coefficient, Cpi, shall be taken as zero and the value of Cp shall be taken as Ã‚Â±0.9, except that within a distance equal to the larger of 0.1D and 0.1W from a building corner, Cp shall be taken as Ã‚Â±1.2. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.6.(1) | External Pressure Coefficients for Low Buildings | For the design of buildings with a height, H, that is both less than or equal to 20 m and less than the smaller plan dimension, the values of the product of the pressure coefficient and gust factor, CpCg, provided in Sentences (2) to (9) are permitted to be used. | obc2019_divb | Div B | 4.1.7.6.(1) | 4.1.7.6. External Pressure Coefficients for Low Buildings | For the design of buildings with a height, H, that is less than or equal to 20 m and less than the smaller plan dimension, the values of the product of the pressure coefficient and gust factor, CpCg, provided in Sentences (2) to (9) are permitted to be used. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.6.(2) | External Pressure Coefficients for Low Buildings | For the design of the main structural system of the building, which is affected by wind pressures on more than one surface, the values of CpCg are provided in Figure 4.1.7.6.-A. | obc2019_divb | Div B | 4.1.7.6.(2) | 4.1.7.6. External Pressure Coefficients for Low Buildings | For the design of the main structural system of the building, which is affected by wind pressures on more than one surface, the values of CpCg are provided in Figure 4.1.7.6.A. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.6.(3) | External Pressure Coefficients for Low Buildings | For the design of individual walls and wall cladding, the values of CpCg are provided in Figure 4.1.7.6.-B. | obc2019_divb | Div B | 4.1.7.6.(3) | 4.1.7.6. External Pressure Coefficients for Low Buildings | For the design of individual walls and wall cladding, the values of CpCg are provided in Figure 4.1.7.6.B. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.6.(4) | External Pressure Coefficients for Low Buildings | For the design of roofs with a slope less than or equal to 7°, the values of CpCg are provided inFigure 4.1.7.6.-C. | obc2019_divb | Div B | 4.1.7.6.(4) | 4.1.7.6. External Pressure Coefficients for Low Buildings | For the design of roofs with a slope less than or equal to 7°, the values of CpCg are provided in Figure 4.1.7.6.C. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.6.(5) | External Pressure Coefficients for Low Buildings | For the design of flat roofs with steps in elevation, the values of CpCg are provided in Figure 4.1.7.6.-D. | obc2019_divb | Div B | 4.1.7.6.(5) | 4.1.7.6. External Pressure Coefficients for Low Buildings | For the design of flat roofs with steps in elevation, the values of CpCg are provided in Figure 4.1.7.6.D. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.6.(6) | External Pressure Coefficients for Low Buildings | For the design of gabled or hipped, single-ridge roofs with slope greater than 7°, the values of CpCg are provided in Figure 4.1.7.6.-E. | obc2019_divb | Div B | 4.1.7.6.(6) | 4.1.7.6. External Pressure Coefficients for Low Buildings | For the design of gabled or hipped, single-ridge roofs with slope greater than 7°, the values of CpCg are provided in Figure 4.1.7.6.E. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.6.(7) | External Pressure Coefficients for Low Buildings | For the design of gabled, multi-ridge roofs, the values of CpCg are provided in (a) Figure 4.1.7.6.-C. for roofs with slope less than or equal to 10°, and (b) Figure 4.1.7.6.-F. for roofs with slope greater than 10°. | obc2019_divb | Div B | 4.1.7.6.(7) | 4.1.7.6. External Pressure Coefficients for Low Buildings | For the design of gabled, multi-ridge roofs, the values of CpCg are provided in, (a) Figure 4.1.7.6.C. for roofs with slope less than or equal to 10°, and (b) Figure 4.1.7.6.F. for roofs with slope greater than 10°. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.6.(8) | External Pressure Coefficients for Low Buildings | For monosloped roofs, the values of CpCg are provided in (a) Figure 4.1.7.6.-C. for roofs with a slope less than or equal to 3°, and (b) Figure 4.1.7.6.-G. for roofs with a slope greater than 3° and less than or equal to 30° | obc2019_divb | Div B | 4.1.7.6.(8) | 4.1.7.6. External Pressure Coefficients for Low Buildings | For monosloped roofs, the values of CpCg are provided in, (a) Figure 4.1.7.6.C. for roofs with a slope less than or equal to 3°, and (b) Figure 4.1.7.6.G. for roofs with a slope greater than 3° and less than or equal to 30° | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.6.(9) | External Pressure Coefficients for Low Buildings | For sawtooth roofs, the values of CpCg are provided in (a) Figure 4.1.7.6.-C. for roofs with a slope less than or equal to 10°, and (b) Figure 4.1.7.6.-H. for roofs with a slope greater than 10°. | obc2019_divb | Div B | 4.1.7.6.(9) | 4.1.7.6. External Pressure Coefficients for Low Buildings | For sawtooth roofs, the values of CpCg are provided in, (a) Figure 4.1.7.6.C. for roofs with a slope less than or equal to 10°, and (b) Figure 4.1.7.6.H. for roofs with a slope greater than 10°. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.7.(1) | Internal Pressure Coefficient | The internal pressure coefficient, Cpi, shall be as prescribed in Table 4.1.7.7. | obc2019_divb | Div B | 4.1.7.7.(1) | 4.1.7 7 Internal Pressure Coefficient | The internal pressure coefficient, Cpi, shall be as prescribed in Table 4.1.7.7. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.7.(2) | Internal Pressure Coefficient | Uniformly distributed small openings amounting to less than 0.1% of the total surface area of the building | obc2019_divb | Div B | 4.1.7.7.(2) | 4.1.7.7. Internal Pressure Coefficient | Uniformly distributed small openings amounting to less than 0.1% of the total surface area | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.8.(1) | Dynamic Procedure | For the application of the Dynamic Procedure, the provisions of Article 4.1.7.3. shall be followed, except that the exposure factor, Ce, shall be as prescribed in Sentences (2) and (3), and the gust effect factor, Cg, shall be as prescribed in Sentence (4), when determining the wind loads on the main structural system. | obc2019_divb | Div B | 4.1.7.8.(1) | 4.1.7.8. Dynamic Procedure | For the application of the Dynamic Procedure, the provisions of Article 4.1.7.3. shall be followed, except that the exposure factor, Ce, shall be as prescribed in Sentences (2) and (3), and the gust effect factor, Cg, shall be as prescribed in Sentence (4), when determining the wind loads on the main structural system. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.8.(2) | Dynamic Procedure | For buildings in open terrain, as defined in Sentence 4.1.7.3.(5), the value of Ce for the design of the main structural system shall be calculated as follows: Ce=h10 0.28,but1.0?C e?2.5 | obc2019_divb | Div B | 4.1.7.8.(2) | 4.1.7.8. Dynamic Procedure | For buildings in open terrain as described in Clause 4.1.7.3.(5)(a), the value of Ce for the design of the main structural system shall be calculated as follows:Ce = (h/10)0.28, but 1.0 Ã¢â€°Â¤ Ce Ã¢â€°Â¤ 2.5 (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.8.(3) | Dynamic Procedure | For buildings in rough terrain, as defined in Sentence 4.1.7.3.(5), the value of Ce for the design of the main structural system shall be calculated as follows: Ce=0.5h12.7 0.50,but0.5?Ce ?2.5 | obc2019_divb | Div B | 4.1.7.8.(3) | 4.1.7.8. Dynamic Procedure | For buildings in rough terrain as described in Clause 4.1.7.3.(5)(b), the value of Ce for the design of the main structural system shall be calculated as follows:Ce = 0.5(h/12.7)0.50, but 0.5 Ã¢â€°Â¤ Ce Ã¢â€°Â¤ 2.5 (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.8.(4) | Dynamic Procedure | For the design of the main structural system, Cg shall be calculated as follows: Cg=1+gpsmwheregp = peak factor calculated as 2lnnT +0.5772lnnT, and ?/? =KCeHB+ sFb, where?= average fluctuation rate calculated as fnDsFsF+bB, T= 3 600 s, K= 0.08 for open terrain and 0.10 for rough terrain, CeH = exposure factor evaluated at reference height h = H, B = background turbulence factor, a function of w/H determined from Article 4.1.7.8., s= size reduction factor calculated as p311 +8fnH3VH11+10fnWV H, F = gust energy ratio calculated as x201+x2 04/3, where x0 = (1 220 fn/VH), and ?= damping ratio, which shall be determined by a rational method, or may be taken to be 0.01 for steel structures, 0.02 for concrete structures, and 0.015 for composite structures, wherefnD = natural frequency of vibration of the building in the along-wind direction, in Hz, fn = lowest natural frequency of the building, in Hz, as defined in Sentences 4.1.7.2.(2) and 4.1.7.2.(3), H= height of the building, w= effective width of windward face of the building calculated as hiwihi, where wi = width normal to wind direction at height hi, and VH = mean wind speed at the top of the structure, in m/s, calculated as V? CeH, where V? = reference wind speed at a height of 10 m, in m/s, calculated as 2?IW?qr, whereIW = importance factor, q= reference velocity pressure, in Pa, and ?= air density = 1.2929 kg/m3. | obc2019_divb | Div B | 4.1.7.8.(4) | 4.1.7.8. Dynamic Procedure | For the design of the main structural system, Cg shall be calculated as follows:Cg = 1 + gp( /ÃŽÂ¼) where, gpÃ‚ = peak factor calculated as , and /ÃŽÂ¼ = , where, Ãâ€¦Ã‚ = average fluctuation rate calculated as , TÃ‚ = 3 600 s, KÃ‚ = 0.08 for open terrain and 0.10 for rough terrain, CeHÃ‚ = exposure factor evaluated at reference height h = H, BÃ‚ = background turbulence factor, a function of w/H determined from Figure 4.1.7.8., sÃ‚ = size reduction factor calculated as , FÃ‚ = gust energy ratio calculated as , where x0 = (1 220 fn/VH), and ÃŽÂ²Ã‚ = damping ratio, which shall be determined by a rational method or may be taken to be 0.01 for steel structures, 0.02 for concrete structures and 0.015 for composite structures, where, fnDÃ‚ = natural frequency of vibration of the building in the along-wind direction, in Hz, fnÃ‚ = lowest natural frequency of the building, in Hz, as described in Sentences 4.1.7.2.(2) and (3), HÃ‚ = height of the building, wÃ‚ = effective width of windward face of the building calculated as, where wi = width normal to wind direction at height hi, and VHÃ‚ = mean wind speed at the top of the structure, in m/s, calculated as , where, Ã‚ = reference wind speed at a height of 10 m, in m/s, calculated as , where, IwÃ‚ = importance factor, qÃ‚ = reference velocity pressure, in Pa, and ÃÂ±Ã‚ = air density = 1.2929 kg/m3. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.7.9.(1) | Full and Partial Wind Loading | Except where the wind loads are derived from the combined CpCg values determined in accordance with Article 4.1.7.6., buildings and structural members shall be capable of withstanding the effects of the following laods, (a) the full wind loads acting along each of the two principal horizontal axes considered separately, (b) the wind loads as described in Clause (a) but with 100% of the load removed from any one portion of the area, (c) the wind loads as described in Clause (a) but with both axes considered simultaneously at 75% of their full value, and (d) the wind loads as described in Clause (c) but with 50% of these loads removed from any portion of the area. (See Note A-4.1.7.9.(1).) | obc2019_divb | Div B | 4.1.7.9.(1) | 4.1.7.9. Full and Partial Wind Loading | Except where the wind loads are derived from the combined CpCg values determined in accordance with Article 4.1.7.6., buildings and structural members shall be capable of withstanding the effects of, (a) the full wind loads acting along each of the two principal horizontal axes considered separately, (b) the wind loads as described in Clause (a) but with 100% of the load removed from any one portion of the area, (c) the wind loads as described in Clause (a) but with both axes considered simultaneously at 75% of their full value, and (d) the wind loads as described in Clause (c) but with 50% of these loads removed from any portion of the area. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.1.(1) | Analysis | Except as permitted in Sentence (2), the deflections and specified loading due to earthquake motions shall be determined according to the requirements of Articles 4.1.8.2. to 4.1.8.22. | obc2019_divb | Div B | 4.1.8.2.(1) | 4.1.8.1. Analysis | Except as permitted in Sentence (2), the deflections and specified loading due to earthquake motions shall be determined according to the requirements of Articles 4.1.8.2. to 4.1.8.22. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.1.(11) | Analysis | The deflections referred to in Sentence 4.1.8.1.(10) shall be used to calculate the largest interstorey deflection, which shall not exceed (a) 0.01hs for post-disaster buildings, (b) 0.02hs for High Importance Category buildings, and (c) 0.025hs for all other buildings, | obc2019_divb | Div B | 4.1.8.2.(11) | 4.1.8.1. Analysis | The deflections described in Sentence (10) shall be used to calculate the largest interstorey deflection, which shall not exceed, (a) 0.01hs for post-disaster buildings, (b) 0.02hs for High Importance Category buildings, and (c) 0.025hs for all other buildings, where hs is the interstorey height as defined in Article 4.1.8.2. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.1.(12) | Analysis | When earthquake forces are calculated using Rs = 1.5, the following elements in the SFRS shall have their design forces due to earthquake effects increased by 33%: (a) diaphragms and their chords, connections, struts and collectors, (d) tie downs in wood or drywall shear walls, (c) connections and anchor bolts in steel- and wood-braced frames, (d) connections in precast concrete, and (e) connections in steel moment frames. | obc2019_divb | Div B | 4.1.8.2.(12) | 4.1.8.1. Analysis | When earthquake forces are calculated using Rs = 1.5, the following elements in the SFRS shall have their design forces due to earthquake effects increased by 33%: (a) diaphragms and their chords, connections, struts and collectors, (b) tie downs in wood or drywall shear walls, (c) connections and anchor bolts in steel- and wood-braced frames, (d) connections in precast concrete, and (e) connections in steel moment frames. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.1.(13) | Analysis | Except as provided in Sentence (14), where cantilever parapet walls, other cantilever walls, exterior ornamentation and appendages, towers, chimneys or penthouses are connected to or form part of a building, they shall be designed, along with their connections, for a lateral force, Vsp, distributed according to the distribution of mass of the element and acting in the lateral direction that results in the most critical loading for design using the following equation:Vsp = 0.1FsIEWp where Wp is the weight of a portion of a structure as defined in Article 4.1.8.2. | obc2019_divb | Div B | 4.1.8.2.(13) | 4.1.8.1. Analysis | Except as provided in Sentence (14), where cantilever parapet walls, other cantilever walls, exterior ornamentation and appendages, towers, chimneys or penthouses are connected to or form part of a building, they shall be designed, along with their connections, for a lateral force, Vsp, distributed according to the distribution of mass of the element and acting in the lateral direction that results in the most critical loading for design using the following equation:Vsp = 0.1FsIEWp where Wp is the weight of a portion of a structure as defined in Article 4.1.8.2. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.1.(15) | Analysis | Structures designed in accordance with this Article need not comply with the seismic requirements stated in the applicable design standard referenced in Section 4.3. | obc2019_divb | Div B | 4.1.8.2.(15) | 4.1.8.1. Analysis | Structures designed in accordance with this Article need not comply with the seismic requirements stated in the applicable design standard referenced in Section 4.3. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.1.(2) | Analysis | Where IEFsSa(0.2) and IEFsSa(2.0) are less than 0.16 and 0.03 respectively, the deflections and specified loading due to earthquake motions are permitted to be determined in accordance with Sentences 4.1.8.1.(3) to 4.1.8.1.(15), where (a) IE is the earthquake importance factor and has a value of 0.8, 1.0, 1.3 and 1.5 for buildings of Low, Normal, High and Post-Disaster importance respectively, (b) Fs is the site coefficient based on the average N? 60 or su, as defined in Article 4.1.8.2., for the top 30 m of soil below the footings, pile caps, or mat foundations and has a value of (i) 1.0 for rock sites or when N? 60 > 50 or su > 100 kPa, (ii) 1.6 when 15 ? N? 60 ? 50 or 50 kPa ? su ? 100 kPa, and (iii) 2.8 for all other cases, and Sa(T) is the 5% damped spectral response acceleration value for period T, determined in accordance with part 1. | obc2019_divb | Div B | 4.1.8.2.(2) | 4.1.8.1. Analysis | Where IEFsSa(0.2) and IEFsSa(2.0) are less than 0.16 and 0.03 respectively, the deflections and specified loading due to earthquake motions are permitted to be determined in accordance with Sentences (3) to (15), where, (a) IE is the earthquake importance factor and has a value of 0.8, 1.0, 1.3 and 1.5 for buildings of Low, Normal, High and Post-Disaster importance respectively, (b) Fs is the site coefficient based on the averageor su, as defined in Article 4.1.8.2., for the top 30 m of soil below the footings, pile caps or mat foundations and has a value of, (i) 1.0 for rock sites or when> 50 or su > 100 kPa, (ii) 1.6 when 15 Ã¢â€°Â¤ Ã¢â€°Â¤ 50 or 50 kPa Ã¢â€°Â¤ su Ã¢â€°Â¤ 100 kPa, and (iii) 2.8 for all other cases, and (c) Sa(T) is the 5% damped spectral response acceleration value for period T, determined in accordance with Subsection 1.1.2. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.1.(3) | Analysis | The structure shall have a clearly defined (a) Seismic Force Resisting System (SFRS) to resist the earthquake loads and their effects, and (b) load path (or paths) that will transfer the inertial forces generated by the earthquake to the foundations and supporting ground. | obc2019_divb | Div B | 4.1.8.2.(3) | 4.1.8.1. Analysis | The structure shall have a clearly defined, (a) SFRS, as defined in Article 4.1.8.2., to resist the earthquake loads and their effects, and (b) load path or paths that will transfer the inertial forces generated by the earthquake to the foundations and supporting ground. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.1.(4) | Analysis | An unreinforced masonry SFRS shall not be permitted where (a) IE is greater than 1.0, or (b) the height above grade is greater than or equal to 30 m. | obc2019_divb | Div B | 4.1.8.2.(4) | 4.1.8.1. Analysis | An unreinforced masonry SFRS shall not be permitted where, (a) IE is greater than 1.0, or (b) the height above grade is greater than or equal to 30 m. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.1.(5) | Analysis | The height above grade of SFRS designed in accordance with CSA S136-16 North American Specification for the Design of Cold-Formed Steel Structural Members (using the Appendix B provisions applicable to Canada) shall be less than 15 m. | obc2019_divb | Div B | 4.1.8.2.(5) | 4.1.8.1. Analysis | The height above grade of SFRS designed in accordance with CSA S136, "North American Specification for the Design of Cold-Formed Steel Structural Members", shall be less than 15 m. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.1.(7) | Analysis | The minimum lateral earthquake design force, Vs, at the base of the structure in the direction under consideration shall be calculated as follows: Vs=FsSaTsIEWt/RswhereSa(Ts)= value of Sa at Ts determined by linear interpolation between the value of Sa at 0.2 s, 0.5 s, and 1.0 s, and = Sa(0.2) for Ts ? 0.2 s, Wt = sum of Wi over the height of the building, where Wi is defined in Article 4.1.8.2., and Rs = 1.5, except Rs = 1.0 for structures where the storey strength is less than that in the storey above and for an unreinforced masonry SFRS, whereTs = fundamental lateral period of vibration of the building, as defined in Article 4.1.8.2., = 0.085(hn)Â¾ for steel moment frames, = 0.075(hn)Â¾ for concrete moment frames, = 0.1 N for other moment frames, = 0.025hn for braced frames, and = 0.05(hn)Â¾ for shear walls and other structures, where hn = height above the base, in m, as defined in Article 4.1.8.2., except that Vs shall not be less than FsSa(1.0)IEWt/Rs and, in cases where Rs =1.5, Vs need not be greater than FsSa(0.5)IEWt/Rs . | obc2019_divb | Div B | 4.1.8.2.(7) | 4.1.8.1. Analysis | The minimum lateral earthquake design force, Vs, at the base of the structure in the direction under consideration shall be calculated as follows:Vs = Fs Sa(Ts) IE Wt / Rs where, Sa(Ts)Ã‚ = value of Sa at Ts determined by linear interpolation between the value of Sa at 0.2 s, 0.5 s and 1.0 s, and = Sa(0.2) for Ts Ã¢â€°Â¤ 0.2 s, WtÃ‚ = sum of Wi over the height of the building, where Wi is defined in Article 4.1.8.2., and RsÃ‚ = 1.5 except Rs = 1.0 for structures where the storey strength is less than that in the storey above and for an unreinforced masonry SFRS, where, TsÃ‚ = fundamental lateral period of vibration of the building, as defined in Article 4.1.8.2., = 0.085(hn)Ã‚Â¾ for steel moment frames, = 0.075(hn)Ã‚Â¾ for concrete moment frames, = 0.1 N for other moment frames, = 0.025hn for braced frames, and = 0.05(hn)Ã‚Â¾ for shear walls and other structures, where, hnÃ‚ = height above the base, in m, as defined in Article 4.1.8.2., except that Vs shall not be less than FsSa(1.0)IEWt/Rs and, in cases where Rs = 1.5, Vs need not be greater than FsSa(0.5)IEWt/Rs. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.1.(8) | Analysis | The total lateral earthquake design force, Vs, shall be distributed over the height of the building in accordance with the following formula: Fx=VsWxhx/i=1nWihiwhereFx = force applied through the centre of mass at level x, Wx, Wi portion of W that is located at or is assigned to level x or i respectively, and hx, hi = height, in m, above the base of level x and level i as per Article 4.1.8.2. | obc2019_divb | Div B | 4.1.8.2.(8) | 4.1.8.1. Analysis | The total lateral earthquake design force, Vs, shall be distributed over the height of the building in accordance with the following formula:where, FxÃ‚ = force applied through the centre of mass at level x, Wx,WiÃ‚ = portion of W that is located at or is assigned to level x or level i respectively, and hx, hiÃ‚ = height, in m, above the base of level x and level i as described in Article 4.1.8.2. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.1.(9) | Analysis | Accidental torsional effects applied concurrently with Fx shall be considered by applying torsional moments about the vertical axis at each level for each of the following cases considered separately: (a) +0.1DnxFx, and (b) -0.1DnxFx. | obc2019_divb | Div B | 4.1.8.2.(9) | 4.1.8.1. Analysis | Accidental torsional effects applied concurrently with Fx shall be considered by applying torsional moments about the vertical axis at each level for each of the following cases considered separately: (a) +0.1DnxFx, and (b) Ã¢â‚¬"0.1DnxFx. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.10.(1) | Additional System Restrictions | Except as required by Clause (2)(b), structures with a Type 6 irregularity, Discontinuity in Capacity – Weak Storey, as described in Table 4.1.8.6., are not permitted unless IEFaSa(0.2) is less than 0.2 and the forces used for design of the SFRS are multiplied by RdRo. | obc2019_divb | Div B | 4.1.8.10.(1) | 4.1.8.10. Additional System Restrictions | Except as required by Clause (2)(b), structures with a Type 6 irregularity, Discontinuity in Capacity Ã¢â‚¬" Weak Storey, as described in Table 4.1.8.6., are not permitted unless IEFaSa(0.2) is less than 0.2 and the forces used for design of the SFRS are multiplied by RdRo. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.10.(2) | Additional System Restrictions | Post-disaster buildings shall not have any irregularities conforming to Types 1, 3, 4, 5, 7 and 9 as described in Table 4.1.8.6., in cases where IEFaSa(0.2) is equal to or greater than 0.35, not have a Type 6 irregularity as described in Table 4.1.8.6., have an SFRS with an Rd of 2.0 or greater, and have no storey with a lateral stiffness that is less than that of the storey above it. | obc2019_divb | Div B | 4.1.8.10.(2) | 4.1.8.10. Additional System Restrictions | Post-disaster buildings shall, (a) not have any irregularities conforming to Types 1, 3, 4, 5 and 7 as described in Table 4.1.8.6., in cases where IEFaSa(0.2) is equal to or greater than 0.35, (b) not have a Type 6 irregularity as described in Table 4.1.8.6., (c) have an SFRS with an Rd of 2.0 or greater, and (d) have no storey with a lateral stiffness that is less than that of the storey above it. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.10.(3) | Additional System Restrictions | For buildings having fundamental lateral periods, Ta, of 1.0 s or greater and where IEFvSa(1.0) is greater than 0.25, shear walls that are other than wood-based and form part of the SFRS shall be continuous from their top to the foundation and shall not have irregularities of Type 4 or 5 as described in Table 4.1.8.6. | obc2019_divb | Div B | 4.1.8.10.(3) | 4.1.8.10. Additional System Restrictions | For buildings having fundamental lateral periods, Ta, of 1.0 s or greater and where IEFvSa(1.0) is greater than 0.25, shear walls that are other than wood-based and form part of the SFRS shall be continuous from their top to the foundation and shall not have irregularities of Type 4 or 5 as described in Table 4.1.8.6. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.10.(4) | Additional System Restrictions | For buildings constructed with more than 4 storeys of continuous wood construction and where IEFaSa(0.2) is equal to or greater than 0.35, timber SFRS consisting of shear walls with wood-based panels or of braced or moment-resisting frames as defined in Table 4.1.8.9. within the continuous wood construction shall not have Type 4 or Type 5 irregularities as described in Table 4.1.8.6. (See Note A-4.1.8.10.(4).) | obc2019_divb | Div B | 4.1.8.10.(4) | 4.1.8.10. Additional System Restrictions | For buildings constructed with more than 4 storeys of continuous wood construction and where IEFaSa(0.2) is equal to or greater than 0.35, timber SFRS of shear walls with wood-based panels, braced frames or moment-resisting frames as defined in Table 4.1.8.9. within the continuous wood construction shall not have irregularities of Type 4 or 5 as described in Table 4.1.8.6. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.10.(5) | Additional System Restrictions | The ratio, ?, for Type 9 irregularity as described in Table 4.1.8.6. shall be determined independently for each orthogonal direction using the following equation: ? = QG / Qy where, QG = gravity-induced lateral demand on the SFRS at the critical level of the yielding system, and Qy = the resistance of the yielding mechanism required to resist the minimum earthquake loads, which need not be taken less than Ro multiplied by the minimum lateral earthquake force as determined in Article 4.1.8.11. or 4.1.8.12, as appropriate. (See Note A-4.1.8.10.(5).) | obc2019_divb | Div B | 4.1.8.10.(5) | 4.1.8.10. Additional System Restrictions | The ratio, ÃŽÂ±, for Type 9 irregularity as described in Table 4.1.8.6. shall be determined independently for each orthogonal direction using the following equation:Ã°?â€ºÂ¼ = QG / Qy where, QG = gravity-induced lateral demand on the SFRS at the critical level of the yielding system, and Qy = the resistance of the yielding mechanism required to resist the minimum earthquake loads, which need not be taken less than Ro multiplied by the minimum lateral earthquake force as determined in Article 4.1.8.11. or 4.1.8.12, as appropriate. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.10.(6) | Additional System Restrictions | For buildings with a Type 9 irregularity as described in Table 4.1.8.6. and where IEFaSa(0.2) is equal to or greater than 0.5, deflections determined in accordance with Article 4.1.8.13. shall be multiplied by 1.2. | obc2019_divb | Div B | 4.1.8.10.(6) | 4.1.8.10. Additional System Restrictions | For buildings with a Type 9 irregularity as described in Table 4.1.8.6. and where IEFaSa(0.2) is equal to or greater than 0.5, deflections determined in accordance with Article 4.1.8.13. shall be multiplied by 1.2. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.10.(7) | Additional System Restrictions | Structures where the value of ?, as determined in accordance with Sentence 4.1.8.10.(5), exceeds twice the limits specified in Table 4.1.8.6. for a Type 9 irregularity, and where IEFaSa(0.2) is equal to or greater than 0.5 are not permitted unless determined to be acceptable based on non-linear dynamic analysis studies. (See Note A-4.1.8.10.(7).) | obc2019_divb | Div B | 4.1.8.10.(7) | 4.1.8.10. Additional System Restrictions | Structures where the value of ÃŽÂ±, as determined in accordance with Sentence (5), exceeds twice the limits in Table 4.1.8.6. for a Type 9 irregularity, and where IEFaSa(0.2) is equal to or greater than 0.5 are not permitted unless determined to be acceptable based on non-linear dynamic analysis studies. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.11.(1) | Equivalent Static Force Procedure for Structures | The static loading due to earthquake motion shall be determined according to the procedures given in this Article. | obc2019_divb | Div B | 4.1.8.11.(1) | 4.1.8.11. Equivalent Static Force Procedure for Structures | The static loading due to earthquake motion shall be determined according to the procedures given in this Article. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.11.(10) | Equivalent Static Force Procedure for Structures Satisfying | Torsional sensitivity shall be determined by calculating the ratio Bx for each level x according to the following equation for each orthogonal direction determined independently: Bx=dmax/dave whereB= maximum of all values of Bx in both orthogonal directions, except that the Bx for one-storey penthouses with a weight less than 10% of the level below need not be considered, ?max = maximum storey displacement at the extreme points of the structure, at level x in the direction of the earthquake induced by the equivalent static forces acting at distances Â± 0.10 Dnx from the centres of mass at each floor, and ?ave = average of the displacements at the extreme points of the structure at level x produced by the above-mentioned forces. | obc2019_divb | Div B | 4.1.8.11.(10) | 4.1.8.11. Equivalent Static Force Procedure for Structures | Torsional sensitivity shall be determined by calculating the ratio Bx for each level x according to the following equation for each orthogonal direction determined independently:Bx = ÃŽÂ´max / ÃŽÂ´ave where, B = maximum of all values of Bx in both orthogonal directions, except that the Bx for one-storey penthouses with a weight less than 10% of the level below need not be considered, ÃŽÂ´max = maximum storey displacement at the extreme points of the structure, at level x in the direction of the earthquake induced by the equivalent static forces acting at distances Ã‚Â± 0.10 Dnx from the centres of mass at each floor, and ÃŽÂ´ave = average of the displacements at the extreme points of the structure at level x produced by the above-mentioned forces. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.11.(11) | Equivalent Static Force Procedure for Structures Satisfying | Torsional effects shall be accounted for as follows: for a building with B ? 1.7 or where IEFaSa(0.2) is less than 0.35, by applying torsional moments about a vertical axis at each level throughout the building, derived for each of the following load cases considered separately: Tx = Fx(ex + 0.10 Dnx), and Tx = Fx(ex - 0.10 Dnx) for a building with B > 1.7, in cases where IEFaSa(0.2) is equal to or greater than 0.35, by a Dynamic Analysis Procedure as specified in Article 4.1.8.12. | obc2019_divb | Div B | 4.1.8.11.(11) | 4.1.8.11. Equivalent Static Force Procedure for Structures | Torsional effects shall be accounted for as follows: (a) for a building with B Ã¢â€°Â¤ 1.7 or where IEFaSa(0.2) is less than 0.35, by applying torsional moments about a vertical axis at each level throughout the building, derived for each of the following load cases considered separately, (i) Tx = Fx(ex + 0.10 Dnx), and (ii) Tx = Fx(ex Ã¢â‚¬" 0.10 Dnx) where Fx is the lateral force at each level determined according to Sentence (6) and where each element of the building is designed for the most severe effect of the above load cases, or (b) for a building with B > 1.7, in cases where IEFaSa(0.2) is equal to or greater than 0.35, by a Dynamic Analysis Procedure as specified in Article 4.1.8.12. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.11.(12) | Equivalent Static Force Procedure for Structures Satisfying | Where the fundamental lateral period, Ta, is determined in accordance with Clause (3)(d) and the building is constructed with more than 4 storeys of continuous wood construction and has a timber SFRS consisting of shear walls with wood-based panels or of braced or moment-resisting frames as defined in Table 4.1.8.9., the lateral earthquake force, V, as determined in accordance with Sentence 4.1.8.11.(2) shall be multiplied by 1.2 but need not exceed the value determined by using Sentence 4.1.8.11.(2). (See Note A-4.1.8.10.(4).) | obc2019_divb | Div B | 4.1.8.11.(12) | 4.1.8.11. Equivalent Static Force Procedure for Structures | Where the fundamental lateral period, Ta, is determined in accordance with Clause (3)(d) and the building is constructed with more than 4 storeys of continuous wood construction and has a timber SFRS consisting of shear walls with wood-based panels, braced frames or moment-resisting frames as defined in Table 4.1.8.9., the lateral earthquake force, V, as determined in accordance with Sentence (2) shall be multiplied by 1.2 but need not exceed the value determined by using Clause (2)(c). (See Appendix Note A-4.1.8.10.(4)) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.11.(2) | Equivalent Static Force Procedure for Structures Satisfying | Except as provided in Sentence 4.1.8.11.(12), the minimum lateral earthquake force, V, shall be calculated using the following formula: V=STa MvIEW/ RdRoexcept for walls, coupled walls and wall-frame systems, V shall not be less than S4.0M vIEW/ RdRo for moment-resisting frames, braced frames, and other systems, V shall not be less than S2.0M vIEW/ RdRo for buildings located on a site other than Class F and having an SFRS with an Rd equal to or greater than 1.5, V need not be greater than the larger of 23S0.2IEW/RdRoandS0.5IEW/ RdRo | obc2019_divb | Div B | 4.1.8.11.(2) | 4.1.8.11. Equivalent Static Force Procedure for Structures | Except as provided in Sentence (12), the minimum lateral earthquake force, V, shall be calculated using the following formula:V = S (Ta) MvIEW/ (RdRo) except, (a) for walls, coupled walls and wall-frame systems, V shall not be less than, S (4.0) Mv IEW/ (RdRo) (b) for moment-resisting frames, braced frames and other systems, V shall not be less than, S (2.0) Mv IEW/ (RdRo) (c) for buildings located on a site other than Class F and having an SFRS with an Rd equal to or greater than 1.5, V need not be greater than the larger of, 2/3 S (0.2) IEW / (RdRo) and S (0.5) IEW/ (RdRo) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.11.(3) | Equivalent Static Force Procedure for Structures Satisfying | Except as provided in Sentence 4.1.8.11.(4), the fundamental lateral period, Ta, in the direction under consideration in Sentence 4.1.8.11.(2), shall be determined as: for moment-resisting frames that resist 100% of the required lateral forces and where the frame is not enclosed by or adjoined by more rigid elements that would tend to prevent the frame from resisting lateral forces, and where hn is in metres: 0.085 (hn)3/4 for steel moment frames, 0.075 (hn)3/4 for concrete moment frames, or 0.1 N for other moment frames, 0.025hn for braced frames where hn is in metres, 0.05 (hn)3/4 for shear wall and other structures where hn is in metres, or other established methods of mechanics using a structural model that complies with the requirements of Sentence 4.1.8.3.(8), except that for moment-resisting frames, Ta shall not be taken greater than 1.5 times that determined in Sentence 4.1.8.11.(3), for braced frames, Ta shall not be taken greater than 2.0 times that determined in Sentence 4.1.8.11.(3), for shear wall structures, Ta shall not be taken greater than 2.0 times that determined in Sentence 4.1.8.11.(3), for other structures, Ta shall not be taken greater than that determined in Sentence 4.1.8.11.(3), and for the purpose of calculating the deflections, the period without the upper limit specified in Subclauses 4.1.8.11.(3) to 4.1.8.11.(3) may be used, except that, for walls, coupled walls and wall-frame systems, Ta shall not exceed 4.0 s, and for moment-resisting frames, braced frames, and other systems, Ta shall not exceed 2.0 s. | obc2019_divb | Div B | 4.1.8.11.(3) | 4.1.8.11. Equivalent Static Force Procedure for Structures | Except as provided in Sentence (4), the fundamental lateral period, Ta, in the direction under consideration in Sentence (2) shall be determined as, (a) for moment-resisting frames that resist 100% of the required lateral forces and where the frame is not enclosed by or adjoined by more rigid elements that would tend to prevent the frame from resisting lateral forces, and where hn is in metres, (i) 0.085 (hn)3/4 for steel moment frames, (ii) 0.075 (hn)3/4 for concrete moment frames, or (iii) 0.1 N for other moment frames, (b) 0.025 hn for braced frames where hn is in metres, (c) 0.05 (hn)3/4 for shear wall and other structures where hn is in metres, or (d) other established methods of mechanics using a structural model that complies with the requirements of SentenceÃ‚ 4.1.8.3.(8), except that, (i) for moment-resisting frames, Ta shall not be taken greater than 1.5 times that determined in Clause (a), (ii) for braced frames, Ta shall not be taken greater than 2.0 times that determined in Clause (b), (iii) for shear wall structures, Ta shall not be greater than 2.0 times that determined in Clause (c), (iv) for other structures, Ta shall not be taken greater than that determined in Clause (c), and (v) for the purpose of calculating the deflections, the period without the upper limit specified in Subclauses (d)(i) to (iv) may be used, except that, for walls, coupled walls and wall-frame systems, Ta shall not exceed 4.0 s, and for moment-resisting frames, braced frames, and other systems, Ta shall not exceed 2.0 s. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.11.(4) | Equivalent Static Force Procedure for Structures Satisfying | For single-storey buildings with steel deck or wood roof diaphragms, the fundamental lateral period, Ta, in the direction under consideration is permitted to be taken as a) 0.05 (hn)3/4 + 0.004 L for shear walls, b) 0.035 hn + 0.004 L for steel moment frames and steel braced frames, or c) the value obtained from methods of mechanics using a structural model that complies with the requirements of Sentence 4.1.8.3.(8), except that Ta shall not be greater than 1.5 times the value determined in Clause (a) or (b), as applicable, where L is the shortest length of the diaphragm, in m, between adjacent vertical elements of the SFRS in the direction perpendicular to the direction under consideration. | obc2019_divb | Div B | 4.1.8.11.(4) | 4.1.8.11. Equivalent Static Force Procedure for Structures | For single-storey buildings with steel deck or wood roof diaphragms, the fundamental lateral period, Ta, in the direction under consideration is permitted to be taken as, (a) 0.05 (hn)3/4 + 0.004 L for shear walls, (b) 0.035 hn + 0.004 L for steel moment frames and steel braced frames, or (c) the value obtained from methods of mechanics using a structural model that complies with the requirements of Sentence 4.1.8.3.(8), except that Ta shall not be greater than 1.5 times the value determined in Clause (a) or (b), as applicable, where L is the shortest length of the diaphragm, in m, between adjacent vertical elements of the SFRS in the direction perpendicular to the direction under consideration. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.11.(5) | Equivalent Static Force Procedure for Structures Satisfying | The weight, W, of the building shall be calculated using the following formula: W=i=1nWi | obc2019_divb | Div B | 4.1.8.11.(5) | 4.1.8.11. Equivalent Static Force Procedure for Structures | The weight, W, of the building shall be calculated using the formula, | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.11.(6) | Equivalent Static Force Procedure for Structures Satisfying | The higher mode factor, Mv, and its associated base overturning moment reduction factor, J, shall conform to Table 4.1.8.11. | obc2019_divb | Div B | 4.1.8.11.(6) | 4.1.8.11. Equivalent Static Force Procedure for Structures | The higher mode factor, Mv, and its associated base overturning moment reduction factor, J, shall conform to Tables 4.1.8.11.A. to 4.1.8.11.E. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.11.(7) | Equivalent Static Force Procedure for Structures Satisfying | The total lateral seismic force, V, shall be distributed such that a portion, Ft, shall be assumed to be concentrated at the top of the building, where Ft is equal to 0.07 TaV but need not exceed 0.25 V and may be considered as zero where the fundamental lateral period, Ta, does not exceed 0.7 s; the remainder, V - Ft , shall be distributed along the height of the building, including the top level, in accordance with the following formula: Fx=V-Ft Wxhx/i=1n Wihi | obc2019_divb | Div B | 4.1.8.11.(7) | 4.1.8.11. Equivalent Static Force Procedure for Structures | The total lateral seismic force, V, shall be distributed such that a portion, Ft, shall be assumed to be concentrated at the top of the building, where Ft, is equal to 0.07 TaV but need not exceed 0.25 V and may be considered as zero, where the fundamental lateral period, Ta, does not exceed 0.7 s; the remainder, V - Ft, shall be distributed along the height of the building, including the top level, in accordance with the formula,Fx = (V Ã¢â‚¬" Ft) Wxhx / | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.11.(8) | Equivalent Static Force Procedure for Structures Satisfying | The structure shall be designed to resist overturning effects caused by the earthquake forces determined in Sentence 4.1.8.11.(7) and the overturning moment at level x, Mx, shall be determined using the following equation: Mx=Jxi=xn Fihi-hxwhereJx = 1.0 for hx ? 0.6hn, and Jx = J + (1 - J)(hx / 0.6hn) for hx &lt; 0.6hn whereJ= base overturning moment reduction factor conforming to Table 4.1.8.11. | obc2019_divb | Div B | 4.1.8.11.(8) | 4.1.8.11. Equivalent Static Force Procedure for Structures | The structure shall be designed to resist overturning effects caused by the earthquake forces determined in Sentence ‚ (7) and the overturning moment at level x, Mx, shall be determined using the formula,(hi Ã¢â‚¬" hx) where, Jx = 1.0 for hx Ã¢â€°Â¥ 0.6hn, and Jx = J + (1- J)(hx / 0.6hn) for hx, &lt; 0.6hn where, J = base overturning moment reduction factor conforming to Table 4.1.8.11. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.11.(9) | Equivalent Static Force Procedure for Structures Satisfying | Torsional effects that are concurrent with the effects of the forces mentioned in Sentence (7) and are caused by the simultaneous actions of the following torsional moments shall be considered in the design of the structure according to Sentence (11): a) torsional moments introduced by eccentricity between the centres of mass and resistance and their dynamic amplification, and b) torsional moments due to accidental eccentricities. | obc2019_divb | Div B | 4.1.8.11.(9) | 4.1.8.11. Equivalent Static Force Procedure for Structures | Torsional effects that are concurrent with the effects of the forces mentioned in Sentence (7) and are caused by the simultaneous actions of the following torsional moments shall be considered in the design of the structure according to Sentence (11): (a) torsional moments introduced by eccentricity between the centres of mass and resistance and their dynamic amplification, and (b) torsional moments due to accidental eccentricities. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.12.(1) | Dynamic Analysis Procedure | Except as provided in Articles 4.1.8.19. and 4.1.8.21., the Dynamic Analysis Procedure shall be in accordance with one of the following methods: Linear Dynamic Analysis by either the Modal Response Spectrum Method or the Numerical Integration Linear Time History Method using a structural model that complies with the requirements of Sentence 4.1.8.3.(8) (see Note A-4.1.8.12.(1)(a)), or Non-linear Dynamic Analysis, in which case a special study shall be performed (see Note A-4.1.8.12.(1)(b)). | obc2019_divb | Div B | 4.1.8.12.(1) | 4.1.8.12. Dynamic Analysis Procedure | Except as provided in Articles 4.1.8.19. and 4.1.8.21., the Dynamic Analysis Procedure shall be in accordance with one of the following methods: (a) Linear Dynamic Analysis by either the Modal Response Spectrum Method or the Numerical Integration Linear Time History Method using a structural model that complies with the requirements of Sentence 4.1.8.3.(8), or (See Appendix A) (b) Non-Linear Dynamic Analysis, in which case a special study shall be performed. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.12.(10) | Dynamic Analysis Procedure | Except as required by Sentence 4.1.8.12.(11), the values of elastic storey shears, storey forces, member forces, and deflections obtained from the Linear Dynamic Analysis, including the effect of accidental torsion determined in Sentence 4.1.8.12.(4), shall be multiplied by Vd/Ve to determine their design values, where Vd is the base shear. | obc2019_divb | Div B | 4.1.8.12.(10) | 4.1.8.12. Dynamic Analysis Procedure | Except as required by Sentence (11), the values of elastic storey shears, storey forces, member forces, and deflections obtained from the Linear Dynamic Analysis, including the effect of accidental torsion determined in SentenceÃ‚ (4), shall be multiplied by Vd/Ve to determine their design values, where Vd is the base shear. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.12.(11) | Dynamic Analysis Procedure | For the purpose of calculating deflections, it is permitted to use a value for V based on the value for Ta determined in Clause 4.1.8.11.(3)(d) to obtain Vd in Sentences (8) and (9). | obc2019_divb | Div B | 4.1.8.12.(11) | 4.1.8.12. Dynamic Analysis Procedure | For the purpose of calculating deflections, it is permitted to use a value for V based on the value for Ta determined in Clause 4.1.8.11.(3)(d) to obtain Vd in Sentences (8) and (9). | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.12.(12) | Dynamic Analysis Procedure | For buildings constructed with more than 4 storeys of continuous wood construction, having a timber SFRS consisting of shear walls with wood-based panels or braced or moment-resisting frames as defined in Table 4.1.8.9., and whose fundamental lateral period, Ta, is determined in accordance with Sentence 4.1.8.11.(3), the design base shear, Vd, shall be taken as the larger value of Vd determined in accordance with Sentence 4.1.8.12.(7) and 100% of V. (See Note A-4.1.8.10.(4).) | obc2019_divb | Div B | 4.1.8.12.(12) | 4.1.8.12. Dynamic Analysis Procedure | For buildings constructed with more than 4 storeys of continuous wood construction, having a timber SFRS consisting of shear walls with wood-based panels, braced frames or moment-resisting frames as defined in Table 4.1.8.9., and whose fundamental lateral period, Ta, is determined in accordance with Clause 4.1.8.11.(3)(d), the design base shear, Vd, shall be taken as the larger value of Vd determined in accordance with Sentence (7) and 100% of V. (See A-4.1.8.10.(4) in Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.12.(2) | Dynamic Analysis Procedure | The spectral acceleration values used in the Modal Response Spectrum Method shall be the design spectral acceleration values, S(T), defined in Sentence 4.1.8.4.(9). | obc2019_divb | Div B | 4.1.8.12.(2) | 4.1.8.12. Dynamic Analysis Procedure | The spectral acceleration values used in the Modal Response Spectrum Method shall be the design spectral acceleration values, S(T), defined in Sentence 4.1.8.4.(7). | Common Sentence | Yes | Loads
2015 | ON | NBC | Div B | 4.1.8.12.(3) | Dynamic Analysis Procedure | The ground motion histories used in the Numerical Integration Linear Time History Method shall be compatible with a response spectrum constructed from the design spectral acceleration values, S(T), defined in Sentence 4.1.8.4.(9). (See Note A-4.1.8.12.(3).) | obc2019_divb | Div B | 4.1.8.12.(3) | 4.1.8.12. Dynamic Analysis Procedure | The ground motion histories used in the Numerical Integration Linear Time History Method shall be compatible with a response spectrum constructed from the design spectral acceleration values, S(T), defined in Sentence 4.1.8.4.(7). (See Appendix A.) | Common Sentence | Yes | Loads
2015 | ON | NBC | Div B | 4.1.8.12.(4) | Dynamic Analysis Procedure | The effects of accidental torsional moments acting concurrently with the lateral earthquake forces that cause them shall be accounted for by the following methods: the static effects of torsional moments due to (Â± 0.10 Dnx)Fx at each level x, where Fx is either determined from the elastic dynamic analysis or determined from Sentence 4.1.8.11.(7) multiplied by RdRo/IE, shall be combined with the effects determined by dynamic analysis (see Note A-4.1.8.12.(4)(a)), or if B, as defined in Sentence 4.1.8.11.(10), is less than 1.7, it is permitted to use a three-dimensional dynamic analysis with the centres of mass shifted by a distance of â€“0.05 Dnx and + 0.05 Dnx. | obc2019_divb | Div B | 4.1.8.12.(4) | 4.1.8.12. Dynamic Analysis Procedure | The effects of accidental torsional moments acting concurrently with the lateral earthquake forces that cause them shall be accounted for by the following methods: (a) the static effects of torsional moments due to (Ã‚Â± 0.10 Dnx)Fx at each level x, where Fx is either determined from the elastic dynamic analysis or determined from Sentence 4.1.8.11.(7) multiplied by RdRo/IE, shall be combined with the effects determined by dynamic analysis, or (See Appendix A.) (b) if B, as defined in Sentence 4.1.8.11.(10), is less than 1.7, it is permitted to use a three-dimensional dynamic analysis with the centres of mass shifted by a distance of Ã¢â‚¬"0.05 Dnx and +0.05 Dnx. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.12.(5) | Dynamic Analysis Procedure | Except as provided in Sentence (6), the design elastic base shear, Ved, is equal to the elastic base shear, Ve, obtained from a Linear Dynamic Analysis. | obc2019_divb | Div B | 4.1.8.12.(5) | 4.1.8.12. Dynamic Analysis Procedure | Except as provided in Sentence (6), the design elastic base shear, Ved, is equal to the elastic base shear, Ve, obtained from a Linear Dynamic Analysis. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.12.(6) | Dynamic Analysis Procedure | For structures located on sites other than Class F that have an SFRS with Rd equal to or greater than 1.5, the elastic base shear obtained from a Linear Dynamic Analysis may be multiplied by the larger of the following factors to obtain the design elastic base shear, Ved: 2S0.23 STa ?1.0andS0.5/STa?1.0 | obc2019_divb | Div B | 4.1.8.12.(6) | 4.1.8.12. Dynamic Analysis Procedure | For structures located on sites other than Class F that have an SFRS with Rd equal to or greater than 1.5, the elastic base shear obtained from a Linear Dynamic Analysis may be multiplied by the larger of the following factors to obtain the design elastic base shear, Ved:and S(0.5) / S(Ta) Ã¢â€°Â¤ 1.0 | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.12.(7) | Dynamic Analysis Procedure | The design elastic base shear, Ved, shall be multiplied by the importance factor, IE, as determined in Article 4.1.8.5., and shall be divided by RdRo, as determined in Article 4.1.8.9., to obtain the design base shear, Vd. | obc2019_divb | Div B | 4.1.8.12.(7) | 4.1.8.12. Dynamic Analysis Procedure | The design elastic base shear, Ved, shall be multiplied by the importance factor, IE, as determined in Article 4.1.8.5., and shall be divided by RdRo, as determined in Article 4.1.8.9., to obtain the design base shear, Vd. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.12.(8) | Dynamic Analysis Procedure | Except as required by Sentence (9) or (12), if the base shear, Vd, obtained in Sentence (7) is less than 80% of the lateral earthquake design force, V, of Article 4.1.8.11., Vd shall be taken as 0.8 V. | obc2019_divb | Div B | 4.1.8.12.(8) | 4.1.8.12. Dynamic Analysis Procedure | Except as required by Sentence (9) or (12), if the base shear, Vd, obtained in Sentence (7) is less than 80% of the lateral earthquake design force, V, of Article 4.1.8.11., Vd shall be taken as 0.8 V. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.12.(9) | Dynamic Analysis Procedure | For irregular structures requiring dynamic analysis in accordance with Article 4.1.8.7., Vd shall be taken as the larger of the Vd determined in Sentence (7) and 100% of V. | obc2019_divb | Div B | 4.1.8.12.(9) | 4.1.8.12. Dynamic Analysis Procedure | For irregular structures requiring dynamic analysis in accordance with Article 4.1.8.7., Vd shall be taken as the larger of the Vd determined in Sentence (7) and 100% of V. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.13.(1) | Deflections and Drift Limits | Except as provided in Sentences (5) and (6), lateral deflections of a structure shall be calculated in accordance with the loads and requirements defined in this Subsection. | obc2019_divb | Div B | 4.1.8.13.(1) | 4.1.8.13. Deflections and Drift Limits | Except as provided in Sentences (5) and (6), lateral deflections of a structure shall be calculated in accordance with the loads and requirements defined in this Subsection. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.13.(2) | Deflections and Drift Limits | Lateral deflections obtained from a linear elastic analysis using the methods given in Articles 4.1.8.11. and 4.1.8.12. and incorporating the effects of torsion, including accidental torsional moments, shall be multiplied by RdRo/IE and increased as required in Sentences 4.1.8.10.(6) and Sentence 4.1.8.16.(1) to give realistic values of anticipated deflections. | obc2019_divb | Div B | 4.1.8.13.(2) | 4.1.8.13. Deflections and Drift Limits | Lateral deflections obtained from a linear elastic analysis using the methods given in Articles 4.1.8.11. and 4.1.8.12. and incorporating the effects of torsion, including accidental torsional moments, shall be multiplied by RdRo/IE and increased as required by Sentences 4.1.8.10.(6) and 4.1.8.16.(1) to give realistic values of anticipated deflections. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.13.(3) | Deflections and Drift Limits | Based on the lateral deflections calculated in Sentences (2), (5) and (6), the largest interstorey deflection at any level shall be limited to 0.01 hs for post-disaster buildings, 0.02 hs for High Importance Category buildings, and 0.025 hs for all other buildings. | obc2019_divb | Div B | 4.1.8.13.(3) | 4.1.8.13. Deflections and Drift Limits | Based on the lateral deflections calculated in Sentences (2), (5) and (6), the largest interstorey deflection at any level shall be limited to 0.01 hs for post-disaster buildings, 0.02 hs for High Importance Category buildings, and 0.025 hs for all other buildings. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.13.(4) | Deflections and Drift Limits | The deflections calculated in Sentence (2) shall be used to account for sway effects as required by Sentence 4.1.3.2.(12). (See Note A-4.1.8.13.(4).) | obc2019_divb | Div B | 4.1.8.13.(4) | 4.1.8.13. Deflections and Drift Limits | The deflections calculated in Sentence (2) shall be used to account for sway effects as required by Sentence 4.1.3.2.(12). (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.13.(5) | Deflections and Drift Limits | The lateral deflections of a seismically isolated structure shall be calculated in accordance with Article 4.1.8.20. | obc2019_divb | Div B | 4.1.8.13.(5) | 4.1.8.13. Deflections and Drift Limits | The lateral deflections of a seismically isolated structure shall be calculated in accordance with Article 4.1.8.20. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.13.(6) | Deflections and Drift Limits | The lateral deflections of a structure with supplemental energy dissipation shall be calculated in accordance with Article 4.1.8.22. | obc2019_divb | Div B | 4.1.8.13.(6) | 4.1.8.13. Deflections and Drift Limits | The lateral deflections of a structure with supplemental energy dissipation shall be calculated in accordance with Article 4.1.8.22. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.14.(1) | Structural Separation | Adjacent structures shall be separated by a distance equal to at least the square root of the sum of the squares of their individual deflections calculated in Sentence 4.1.8.13.(2), or connected to each other. | obc2019_divb | Div B | 4.1.8.14.(1) | 4.1.8.14. Structural Separation | Adjacent structures shall be, (a) separated by a distance equal to at least the square root of the sum of the squares of their individual deflections calculated in Sentence 4.1.8.13.(2), or (b) connected to each other. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.14.(2) | Structural Separation | The method of connection required in Sentence (1) shall take into account the mass, stiffness, strength, ductility and anticipated motion of the connected buildings and the character of the connection. | obc2019_divb | Div B | 4.1.8.14.(2) | 4.1.8.14. Structural Separation | The method of connection required in Sentence (1) shall take into account the mass, stiffness, strength, ductility and anticipated motion of the connected buildings and the character of the connection. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.14.(3) | Structural Separation | Rigidly connected buildings shall be assumed to have the lowest RdRo value of the buildings connected. | obc2019_divb | Div B | 4.1.8.14.(3) | 4.1.8.14. Structural Separation | Rigidly connected buildings shall be assumed to have the lowest RdRo value of the buildings connected. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.14.(4) | Structural Separation | Buildings with non-rigid or energy-dissipating connections require special studies. | obc2019_divb | Div B | 4.1.8.14.(4) | 4.1.8.14. Structural Separation | Buildings with non-rigid or energy-dissipating connections require special studies. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.15.(1) | Design Provisions | Except as provided in Sentences 4.1.8.15.(2) and 4.1.8.15.(3), diaphragms, collectors, chords, struts and connections shall be designed so as not to yield, and the design shall account for the shape of the diaphragm, including openings, and for the forces generated in the diaphragm due to the following cases, whichever one governs (see Note A-4.1.8.15.(1)): forces due to loads determined in Article 4.1.8.11. or 4.1.8.12. applied to the diaphragm are increased to reflect the lateral load capacity of the SFRS, plus forces in the diaphragm due to the transfer of forces between elements of the SFRS associated with the lateral load capacity of such elements and accounting for discontinuities and changes in stiffness in these elements, or a minimum force corresponding to the design-based shear divided by N for the diaphragm at level x. | obc2019_divb | Div B | 4.1.8.15.(1) | 4.1.8.15. Design Provisions | Except as provided in Sentences (2) and (3), diaphragms, collectors, chords, struts and connections shall be designed so as not to yield, and the design shall account for the shape of the diaphragm, including openings, and for the forces generated in the diaphragm due to the following cases, whichever one governs: (See Appendix A.) (a) forces due to loads determined in Article 4.1.8.11. or 4.1.8.12. applied to the diaphragm are increased to reflect the lateral load capacity of the SFRS, plus forces in the diaphragm due to the transfer of forces between elements of the SFRS associated with the lateral load capacity of such elements and accounting for discontinuities and changes in stiffness in these elements, or (b) a minimum force corresponding to the design-based shear divided by N for the diaphragm at level x. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.15.(10) | Design Provisions | Foundation displacements and rotations shall be considered as required by Sentence 4.1.8.16.(1). | obc2019_divb | Div B | 4.1.8.15.(10) | 4.1.8.15. Design Provisions | Foundation displacements and rotations shall be considered as required by Sentence 4.1.8.16.(1). | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.15.(2) | Design Provisions | Steel deck roof diaphragms in buildings of less than 4 storeys or wood diaphragms that are designed and detailed according to the applicable referenced design standards to exhibit ductile behaviour shall meet the requirements of Sentence 4.1.8.15.(1), except that they may yield and the forces shall be for wood diaphragms acting in combination with vertical wood shear walls, equal to the lateral earthquake design force, for wood diaphragms acting in combination with other SFRS, not less than the force corresponding to RdRo = 2.0, and for steel deck roof diaphragms, not less than the force corresponding to RdRo = 2.0. | obc2019_divb | Div B | 4.1.8.15.(2) | 4.1.8.15. Design Provisions | Steel deck roof diaphragms in buildings of less than 4 storeys or wood diaphragms that are designed and detailed according to the applicable referenced design standards to exhibit ductile behaviour shall meet the requirements of Sentence (1), except that they may yield and the forces shall be, (a) for wood diaphragms acting in combination with vertical wood shear walls, equal to the lateral earthquake design force, (b) for wood diaphragms acting in combination with other SFRS, not less than the force corresponding to RdRo = 2.0, and (c) for steel deck roof diaphragms, not less than the force corresponding to RdRo = 2.0. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.15.(3) | Design Provisions | Where diaphragms are designed in accordance with Sentence (2), the struts shall be designed in accordance with Clause 4.1.8.15.(1)(a) and the collectors, chords and connections between the diaphragms and the vertical elements of the SFRS shall be designed for forces corresponding to the capacity of the diaphragms in accordance with the applicable CSA standards. (SeeNote A-4.1.8.15.(3).) | obc2019_divb | Div B | 4.1.8.15.(3) | 4.1.8.15. Design Provisions | Where diaphragms are designed in accordance with Sentence (2), the struts shall be designed in accordance with Clause (1)(a) and the collectors, chords and connections between the diaphragms and the vertical elements of the SFRS shall be designed for forces corresponding to the capacity of the diaphragms in accordance with the applicable CSA standards. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.15.(4) | Design Provisions | For single-storey buildings with steel deck or wood roof diaphragms designed with a value of Rd greater than 1.5 and where the calculated maximum relative deflection, ?D, of the diaphragm under lateral loads exceeds 50% of the average storey drift, ?B, of the adjoining vertical elements of the SFRS, dynamic magnification of the inelastic response due to the in-plane diaphragm deformations shall be accounted for in the design as follows: the vertical elements of the SFRS shall be designed and detailed to any one of the following: to accommodate the anticipated magnified lateral deformations taken as RoRd (?B +?D) - Ro?D, to resist the forces magnified by Rd(1 + ?D/?B)/(Rd + ?D/?B), or by a special study, and the roof diaphragm and chords shall be designed for in-plane shears and moments determined while taking into consideration the inelastic higher mode response of the structure. | obc2019_divb | Div B | 4.1.8.15.(4) | 4.1.8.15. Design Provisions | For single-storey buildings with steel deck or wood roof diaphragms designed with a value of Rd greater than 1.5 and where the calculated maximum relative deflection, ÃŽ"D, of the diaphragm under lateral loads exceeds 50% of the average storey drift, ÃŽ"B, of the adjoining vertical elements of the SFRS, dynamic magnification of the inelastic response due to the in-plane diaphragm deformations shall be accounted for in the design as follows: (a) the vertical elements of the SFRS shall be designed and detailed to any one of the following: (i) to accommodate the anticipated magnified lateral deformations taken as RoRd (ÃŽ"B+ ÃŽ"D) - RoÃŽ"D, (ii) to resist the forces magnified by Rd(1 + ÃŽ"D/ÃŽ"B)/( Rd + ÃŽ"D/ÃŽ"B), or (iii) by a special study, and (b) the roof diaphragm and chords shall be designed for in-plane shears and moments determined while taking into consideration the inelastic higher mode response of the structure. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.15.(5) | Design Provisions | In cases where IEFaSa(0.2) is equal to or greater than 0.35, the elements supporting any discontinuous wall, column or braced frame shall be designed for the lateral load capacity of the components of the SFRS they support. (See Note A-4.1.8.15.(5).) | obc2019_divb | Div B | 4.1.8.15.(5) | 4.1.8.15. Design Provisions | In cases where IEFaSa(0.2) is equal to or greater than 0.35, the elements supporting any discontinuous wall, column or braced frame shall be designed for the lateral load capacity of the components of the SFRS they support. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.15.(6) | Design Provisions | Where structures have vertical variations of RdRo satisfying Sentence 4.1.8.9.(4), the elements of the SFRS below the level where the change in RdRo occurs shall be designed for the forces associated with the lateral load capacity of the SFRS above that level. (See Note A-4.1.8.15.(6).) | obc2019_divb | Div B | 4.1.8.15.(6) | 4.1.8.15. Design Provisions | Where structures have vertical variations of RdRo satisfying Sentence 4.1.8.9.(4), the elements of the SFRS below the level where the change in RdRo occurs shall be designed for the forces associated with the lateral load capacity of the SFRS above that level. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.15.(7) | Design Provisions | Where earthquake effects can produce forces in a column or wall due to lateral loading along both orthogonal axes, account shall be taken of the effects of potential concurrent yielding of other elements framing into the column or wall from all directions at the level under consideration and as appropriate at other levels. (See Note A-4.1.8.15.(7).) | obc2019_divb | Div B | 4.1.8.15.(7) | 4.1.8.15. Design Provisions | Where earthquake effects can produce forces in a column or wall due to lateral loading along both orthogonal axes, account shall be taken of the effects of potential concurrent yielding of other elements framing into the column or wall from all directions at the level under consideration and as appropriate at other levels. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.15.(8) | Design Provisions | The design forces associated with the lateral capacity of the SFRS need not exceed the forces determined in accordance with Sentence 4.1.8.7.(1) with RdRo taken as 1.0, unless otherwise provided by the applicable referenced design standards for elements, in which case the design forces associated with the lateral capacity of the SFRS need not exceed the forces determined in accordance with Sentence 4.1.8.7.(1) with RdRo taken as less than or equal to 1.3. (See Note A-4.1.8.15.(8).) | obc2019_divb | Div B | 4.1.8.15.(8) | 4.1.8.15. Design Provisions | The design forces associated with the lateral capacity of the SFRS need not exceed the forces determined in accordance with Sentence 4.1.8.7.(1) with RdRo taken as 1.0, unless otherwise provided by the applicable referenced design standards for elements, in which case the design forces associated with the lateral capacity of the SFRS need not exceed the forces determined in accordance with Sentence 4.1.8.7.(1) with RdRo taken as less than or equal to 1.3. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.15.(9) | Design Provisions | Foundations need not be designed to resist the lateral load overturning capacity of the SFRS, provided the design and the Rd and Ro for the type of SFRS used conform to Table 4.1.8.9. and that the foundation is designed in accordance with Sentence 4.1.8.16.(4). | obc2019_divb | Div B | 4.1.8.15.(9) | 4.1.8.15. Design Provisions | Foundations need not be designed to resist the lateral load overturning capacity of the SFRS, provided the design and the Rd and Ro for the type of SFRS used conform to Table 4.1.8.9. and the foundation is designed in accordance with Sentence 4.1.8.16.(4). | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.16.(1) | Foundation Provisions | The increased displacements of the structure resulting from foundation movement shall be shown to be within acceptable limits for both the SFRS and the structural framing elements not considered to be part of the SFRS. (See Note A-4.1.8.16.(1).) | obc2019_divb | Div B | 4.1.8.16.(1) | 4.1.8.16. Foundation Provisions | The increased displacements of the structure resulting from foundation movement shall be shown to be within acceptable limits for both the SFRS and the structural framing elements not considered to be part of the SFRS. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.16.(10) | Foundation Provisions | The potential for liquefaction of the soil and its consequences, such as significant ground displacement and loss of soil strength and stiffness, shall be evaluated based on the ground motion parameters referenced in Subsection 1.1.3., as modified by Article 4.1.8.4., and shall be taken into account in the design of the structure and its foundations. (See Note A-4.1.8.16.(10).) | obc2019_divb | Div B | 4.1.8.16.(10) | 4.1.8.16. Foundation Provisions | The potential for liquefaction of the soil and its consequences, such as significant ground displacement and loss of soil strength and stiffness, shall be evaluated based on the ground motion parameters referenced in Subsection 1.1.2., as modified by Article 4.1.8.4., and shall be taken into account in the design of the structure and its foundations. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.16.(2) | Foundation Provisions | Except as provided in Sentences (3) and (4), foundations shall be designed to have factored shear and overturning resistances greater than the lateral load capacity of the SFRS. (See Note A-4.1.8.16.(2).) | obc2019_divb | Div B | 4.1.8.16.(2) | 4.1.8.16. Foundation Provisions | Except as provided in Sentences (3) and (4), foundations shall be designed to have factored shear and overturning resistances greater than the lateral load capacity of the SFRS. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.16.(3) | Foundation Provisions | The shear and overturning resistances of the foundation determined using a bearing stress equal to 1.5 times the factored bearing strength of the soil or rock and all other resistances equal to 1.3 times the factored resistances need not exceed the design forces determined in Sentence 4.1.8.7.(1) using RdRo = 1.0 except that the factor of 1.3 shall not apply to the portion of the resistance to uplift or overturning resulting from gravity loads. | obc2019_divb | Div B | 4.1.8.16.(3) | 4.1.8.16. Foundation Provisions | The shear and overturning resistances of the foundation determined using a bearing stress equal to 1.5 times the factored bearing strength of the soil or rock and all other resistances equal to 1.3 times the factored resistances need not exceed the design forces determined in Sentence 4.1.8.7.(1) using RdRo = 1.0 except that the factor of 1.3 shall not apply to the portion of the resistance to uplift or overturning resulting from gravity loads. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.16.(4) | Foundation Provisions | A foundation is permitted to have a factored overturning resistance less than the lateral load overturning capacity of the supported SFRS, provided the following requirements are met: neither the foundation nor the supported SFRS are constrained against rotation, and the design overturning moment of the foundation is not less than 75% of the overturning capacity of the supported SFRS, and not less than that determined in Sentence 4.1.8.7.(1) using RdRo = 2.0. | obc2019_divb | Div B | 4.1.8.16.(4) | 4.1.8.16. Foundation Provisions | A foundation is permitted to have a factored overturning resistance less than the lateral load overturning capacity of the supported SFRS, provided the following requirements are met: (a) neither the foundation nor the supported SFRS are constrained against rotation, and (b) the design overturning moment of the foundation is, (i) not less than 75% of the overturning capacity of the supported SFRS, and (ii) not less than that determined in Sentence 4.1.8.7.(1) using RdRo = 2.0. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.16.(5) | Foundation Provisions | The design of foundations shall be such that they are capable of transferring earthquake loads and effects between the building and the ground without exceeding the capacities of the soil and rock | obc2019_divb | Div B | 4.1.8.16.(5) | 4.1.8.16. Foundation Provisions | The design of foundations shall be such that they are capable of transferring earthquake loads and effects between the building and the ground without exceeding the capacities of the soil and rock | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.16.(6) | Foundation Provisions | In cases where IEFaSa(0.2) is equal to or greater than 0.35, the following requirements shall be satisfied: piles or pile caps, drilled piers, and caissons shall be interconnected by continuous ties in not less than two directions (see Note A-4.1.8.16.(6)(a)), piles, drilled piers, and caissons shall be embedded a minimum of 100 mm into the pile cap or structure, and piles, drilled piers, and caissons, other than wood piles, shall be connected to the pile cap or structure for a minimum tension force equal to 0.15 times the factored compression load on the pile. | obc2019_divb | Div B | 4.1.8.16.(6) | 4.1.8.16. Foundation Provisions | In cases where IEFaSa(0.2) is equal to or greater than 0.35, the following requirements shall be satisfied: (a) piles or pile caps, drilled piers, and caissons shall be interconnected by continuous ties in no fewer than two directions, (See Appendix A.) (b) piles, drilled piers, and caissons shall be embedded a minimum of 100 mm into the pile cap or structure, and (c) piles, drilled piers, and caissons, other than wood piles, shall be connected to the pile cap or structure for a minimum tension force equal to 0.15 times the factored compression load on the pile. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.16.(7) | Foundation Provisions | At sites where IEFaSa(0.2) is equal to or greater than 0.35, basement walls shall be designed to resist earthquake lateral pressures from backfill or natural ground. (See Note A-4.1.8.16.(7).) | obc2019_divb | Div B | 4.1.8.16.(7) | 4.1.8.16. Foundation Provisions | At sites where IEFaSa(0.2) is equal to or greater than 0.35, basement walls shall be designed to resist earthquake lateral pressures from backfill or natural ground. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.16.(8) | Foundation Provisions | At sites where IEFaSa(0.2) is greater than 0.75, the following requirements shall be satisfied: piles, drilled piers, or caissons shall be designed and detailed to accommodate cyclic inelastic behaviour when the design moment in the element due to earthquake effects is greater than 75% of its moment capacity (see Note A-4.1.8.16.(8)(a)), and spread footings founded on soil defined as Site Class E or F shall be interconnected by continuous ties in not less than two directions. | obc2019_divb | Div B | 4.1.8.16.(8) | 4.1.8.16. Foundation Provisions | At sites where IEFaSa(0.2) is greater than 0.75, the following requirements shall be satisfied: (a) piles, drilled piers, or caissons shall be designed and detailed to accommodate cyclic inelastic behaviour when the design moment in the element due to earthquake effects is greater than 75% of its moment capacity, and (See Appendix A.) (b) spread footings founded on soil defined as Site Class E or F shall be interconnected by continuous ties in no fewer than two directions. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.16.(9) | Foundation Provisions | Each segment of a tie between elements that is required by Clause (6)(a) or (8)(b) shall be designed to carry by tension or compression a horizontal force at least equal to the greatest factored pile cap or column vertical load in the elements it connects, multiplied by a factor of 0.10 IEFaSa(0.2), unless it can be demonstrated that equivalent restraints can be provided by other means. (See Note A-4.1.8.16.(9).) | obc2019_divb | Div B | 4.1.8.16.(9) | 4.1.8.16. Foundation Provisions | Each segment of a tie between elements that is required by Clause (6)(a) or (8)(b) shall be designed to carry by tension or compression a horizontal force at least equal to the greatest factored pile cap or column vertical load in the elements it connects, multiplied by a factor of 0.10 IEFaSa(0.2), unless it can be demonstrated that equivalent restraints can be provided by other means. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.17.(1) | Site Stability | The potential for slope instability and its consequences, such as slope displacement, shall be evaluated based on site-specific material properties and ground motion parameters referenced in Subsection 1.1.3., as modified by Article 4.1.8.4., and shall be taken into account in the design of the structure and its foundations. (See Note A-4.1.8.17.(1).) | obc2019_divb | Div B | 4.1.8.17.(1) | 4.1.8.17. Site Stability | The potential for slope instability and its consequences, such as slope displacement, shall be evaluated based on site-specific material properties and ground motion parameters referenced in Subsection 1.1.2., as modified by Article 4.1.8.4., and shall be taken into account in the design of the structure and its foundations. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.18.(1) | Elements of Structures, Non-structural Components and Equipment | Exceptas providedin Sentences (2), (7) and (16), elementsand components of buildings described in Table 4.1.8.18. and their connections to the structure shall be designed to accommodate the building deflections calculated in accordance with Article 4.1.8.13. and the element orcomponent deflections calculated in accordance with Sentence (9), and shall be designed for a lateral force,Vp,distributed according to the distribution of mass: Vp= 0.3FaSa(0.2) IESpWp where, Fa = as defined in Sentence 4.1.8.4.(7), Sa(0.2) = spectral response acceleration value at 0.2 s, as defined in Sentence 4.1.8.4.(1), IE = importance factor for the building, as defined in Article 4.1.8.5., Sp = CpArAx/Rp (the maximum value of Sp shall be taken as 4.0 and the minimum value of Sp shall be taken as 0.7), where, Cp = element or component factor from Table 4.1.8.18., Ar = element or component force amplification factor from Table 4.1.8.18., Ax = height factor (1 + 2 hx / hn), Rp = element or component response modification factor from Table 4.1.8.18., and Wp = weight of the component or element. | obc2019_divb | Div B | 4.1.8.18.(1) | 4.1.8.18. Elements of Structures, Non-Structural Components | Except as provided in Sentences (2), (7) and (16), elements and components of buildings described in Table 4.1.8.18. and their connections to the structure shall be designed to accommodate the building deflections calculated in accordance with Article 4.1.8.13. and the element or component deflections calculated in accordance with Sentence (9), and shall be designed for a lateral force, VP, applied through the centre of mass of the element or component that is equal to:Vp= 0.3FaSa(0.2) IESpWp where, Fa = as defined in Sentence 4.1.8.4.(7), Sa(0.2) = spectral response acceleration value at 0.2 s, as defined in Sentence 4.1.8.4.(1), IE = importance factor for the building, as defined in Article 4.1.8.5., Sp = CpArAx/Rp (the maximum value of Sp shall be taken as 4.0 and the minimum value of Sp shall be taken as 0.7), where, Cp = element or component factor from Table 4.1.8.18., Ar = element or component force amplification factor from Table 4.1.8.18., Ax = height factor (1 + 2 hx / hn), Rp = element or component response modification factor from Table 4.1.8.18., and Wp = weight of the component or element. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.18.(10) | Elements of Structures, Non-structural Components and Equipment | The elements or components shall be designed so as not to transfer to the structure any forces unaccounted for in the design, and rigid elements such as walls or panels shall satisfy the requirements of Sentence 4.1.8.3.(6). | obc2019_divb | Div B | 4.1.8.18.(10) | 4.1.8.18. Elements of Structures, Non-Structural Components | The elements or components shall be designed so as not to transfer to the structure any forces unaccounted for in the design, and rigid elements such as walls or panels shall satisfy the requirements of Sentence 4.1.8.3.(6). | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.18.(11) | Elements of Structures, Non-structural Components and Equipment | Seismic restraint for suspended equipment, pipes, ducts, electrical cable trays, etc. shall be designed to meet the force and displacement requirements of this Article and be constructed in a manner that will not subject hanger rods to bending. | obc2019_divb | Div B | 4.1.8.18.(11) | 4.1.8.18. Elements of Structures, Non-Structural Components | Seismic restraint for suspended equipment, pipes, ducts, electrical cable trays, etc. shall be designed to meet the force and displacement requirements of this Article and be constructed in a manner that will not subject hanger rods to bending. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.18.(12) | Elements of Structures, Non-structural Components and Equipment | Isolated suspended equipment and components, such as pendent lights, may be designed as a pendulum system provided that adequate chains or cables capable of supporting 2.0 times the weight of the suspended component are provided and the deflection requirements of Sentence (10) are satisfied. | obc2019_divb | Div B | 4.1.8.18.(12) | 4.1.8.18. Elements of Structures, Non-Structural Components | Isolated suspended equipment and components, such as pendant lights, may be designed as a pendulum system provided that adequate chains or cables capable of supporting 2.0 times the weight of the suspended component are provided and the deflection requirements of Sentence (11) are satisfied. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.18.(13) | Elements of Structures, Non-structural Components and Equipment | Free-standing steel pallet storage racks are permitted to be designed to resist earthquake effects using rational analysis, provided the design achieves the minimum performance level required by Subsection 4.1.8.(See Note A-4.1.8.18.(13).) | obc2019_divb | Div B | 4.1.8.18.(13) | 4.1.8.18. Elements of Structures, Non-Structural Components | Free-standing steel pallet storage racks are permitted to be designed to resist earthquake effects using rational analysis, provided the design achieves the minimum performance level required by this Subsection. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.18.(14) | Elements of Structures, Non-structural Components and Equipment | Except as provided in Sentence 4.1.8.18.(15), the relative displacement of glass in glazing systems, (a) Dfallout, shall be equal to the greater of Dfallout?1.25I EDP, whereDfallout ..........= relative displacement at which glass fallout occurs, and Dp ..........= relative earthquake displacement that the component must be designed to accommodate, calculated in accordance with Article 4.1.8.13. and applied over the height of the glass component, or (b) 13 mm. | obc2019_divb | Div B | 4.1.8.18.(14) | 4.1.8.18. Elements of Structures, Non-Structural Components | Except as provided in Sentence (15), the relative displacement of glass in glazing systems, Dfallout , shall be equal to the greater of, (a) 13 mm, or (b) Dfallout Ã¢â€°Â¥ 1.25IEDp , where, Dfallout = relative displacement at which glass fallout occurs, and Dp = relative earthquake displacement that the component must be designed to accommodate, calculated in accordance with Article 4.1.8.13. and applied over the height of the glass component. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.18.(15) | Elements of Structures, Non-structural Components and Equipment | Glass need not comply with Sentence 4.1.8.18.(14), provided at least one of the following conditions is met: (a) IEFaSa(0.2) &lt; 0.35, (b) the glass has sufficient clearance from its frame such that Dclear ? 1.25 Dp calculated as follows: Dclear=2C11+hpC2/bpC 1where Dclear = relative horizontal displacement measured over the height of the glass panel, which causes initial glass-to-frame contact, C1 = average of the clearances on both sides between the vertical glass edges and the frame, hp = height of the rectangular glass panel, C2 = averages of the top and bottom clearances between the horizontal glass edges and the frame, and bp = width of the rectangular glass panel, (c) the glass is fully tempered, monolithic, installed in a non-post-disaster building, and no part of the glass is located more than 3 m above a walking surface, or (d) the glass is annealed or heat-strengthened laminated glass in a single thickness with an interlayer no less than 0.76 mm and captured mechanically in a wall system glazing pocket with the perimeter secured to the frame by a wet, glazed, gunable, curing, elastomeric sealant perimeter bead of 13 mm minimum glass contact width. | obc2019_divb | Div B | 4.1.8.18.(15) | 4.1.8.18. Elements of Structures, Non-Structural Components | Glass need not comply with Sentence (14), provided at least one of the following conditions is met: (a) IEFaSa(0.2) &lt; 0.35, (b) the glass has sufficient clearance from its frame such that Dclear Ã¢â€°Â¥ 1.25 Dp calculated as follows: Dclear= 2C1(1 + hpC2/(bpC1)) where, Dclear = relative horizontal displacement measured over the height of the glass panel, which causes initial glass-to-frame contact, C1 = average of the clearances on both sides between the vertical glass edges and the frame, hp = height of the rectangular glass panel, C2 = average of the top and bottom clearances between the horizontal glass edges and the frame, and bp = width of the rectangular glass panel, (c) the glass is fully tempered, monolithic, installed in a building that is not a post-disaster building, and no part of the glass is located more than 3 m above a walking surface, or (d) the glass is annealed or heat-strengthened laminated glass in a single thickness with an interlayer no less than 0.76 mm and captured mechanically in a wall system glazing pocket with the perimeter secured to the frame by a wet, glazed, gunable, curing, elastomeric sealant perimeter bead of 13 mm minimum glass contact width. (See Appendix Note A-4.1.8.18.(14)) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.18.(16) | Elements of Structures, Non-structural Components and Equipment | For a structure with supplemental energy dissipation, the following criteria shall apply: (a) the value of Sa(0.2) used in Sentence (1) shall be determined from the mean 5% damped floor spectral acceleration values at 0.2 s by averaging the individual 5% damped floor spectra at the base of the structure determined using Non-Linear Dynamic Analysis, and (b) the value of Fa used in Sentence (1) shall be 1. | obc2019_divb | Div B | 4.1.8.18.(16) | 4.1.8.18. Elements of Structures, Non-Structural Components | For a structure with supplemental energy dissipation, the following criteria shall apply: (a) the value of Sa(0.2) used in Sentence (1) shall be determined from the mean 5% damped floor spectral acceleration values at 0.2 s by averaging the individual 5% damped floor spectra at the base of the structure determined using Non-Linear Dynamic Analysis, and (b) the value of Fa used in Sentence (1) shall be 1. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.18.(2) | Elements of Structures, Non-structural Components and Equipment | For buildings other than post-disaster buildings, seismically isolated buildings and buildings with supplemental energy dissipation systems, where IEFaSa(0.2) is less than 0.35, the requirements of Sentence (1) need not apply to Categories 6 through 22 of Table 4.1.8.18. | obc2019_divb | Div B | 4.1.8.18.(2) | 4.1.8.18. Elements of Structures, Non-Structural Components | For buildings other than post-disaster buildings, seismically isolated buildings and buildings with supplemental energy dissipation systems, where IEFaSa(0.2) is less than 0.35, the requirements of Sentence (1) need not apply to Categories 6 through 22 of Table 4.1.8.18. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.18.(3) | Elements of Structures, Non-structural Components and Equipment | For the purpose of applying Sentence (1) and Categories 11 and 12 of Table 4.1.8.18., elements or components shall be assumed to be flexible or flexibly connected unless it can be shown that the fundamental period of the element or component and its connection is less than or equal to 0.06 s, in which case the element or component is classified as being rigid or rigidly connected. | obc2019_divb | Div B | 4.1.8.18.(3) | 4.1.8.18. Elements of Structures, Non-Structural Components | For the purpose of applying Sentence (1) and Categories 11 and 12 of Table 4.1.8.18., elements or components shall be assumed to be flexible or flexibly connected unless it can be shown that the fundamental period of the element or component and its connection is less than or equal to 0.06 s, in which case the element or component is classified as being rigid or rigidly connected. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.18.(4) | Elements of Structures, Non-structural Components and Equipment | The weight of access floors shall include the dead load of the access floor and the weight of permanent equipment, which shall not be taken as less than 25% of the floor live load. | obc2019_divb | Div B | 4.1.8.18.(4) | 4.1.8.18. Elements of Structures, Non-Structural Components | The weight of access floors shall include the dead load of the access floor and the weight of permanent equipment, which shall not be taken as less than 25% of the floor live load. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.18.(5) | Elements of Structures, Non-structural Components and Equipment | When the mass of a tank plus its contents or the mass of a flexible or flexibly connected piece of machinery, fixture or equipment is greater than 10% of the mass of the supporting floor, the lateral forces shall be determined by rational analysis. | obc2019_divb | Div B | 4.1.8.18.(5) | 4.1.8.18. Elements of Structures, Non-Structural Components | When the mass of a tank plus its contents or the mass of a flexible or flexibly connected piece of machinery, fixture or equipment is greater than 10% of the mass of the supporting floor, the lateral forces shall be determined by rational analysis. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.18.(6) | Elements of Structures, Non-structural Components and Equipment | Forces shall be applied in the horizontal direction that results in the most critical loading for design, except for Category 6 of Table 4.1.8.18., where the forces shall be applied up and down vertically. | obc2019_divb | Div B | 4.1.8.18.(6) | 4.1.8.18. Elements of Structures, Non-Structural Components | Forces shall be applied in the horizontal direction that results in the most critical loading for design, except for Category 6 of Table 4.1.8.18., where the forces shall be applied up and down vertically. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.18.(7) | Elements of Structures, Non-structural Components and Equipment | Connections to the structure of elements and components listed in Table 4.1.8.18. shall be designed to support the component or element for gravity loads, shall conform to the requirements of Sentence 4.1.8.18.(1), and shall also satisfy these additional requirements: friction due to gravity loads shall not be considered to provide resistance to seismic forces, Rp for non-ductile connections, such as adhesives or power-actuated fasteners, shall be taken as 1.0, Rp for anchorage using shallow expansion, chemical, epoxy or cast-in-place anchors shall be 1.5, where shallow anchors are those with a ratio of embedment length to diameter of less than 8, power-actuated fasteners and drop-in anchors shall not be used for tension loads, connections for non-structural elements or components of Category 1, 2 or 3 of Table 4.1.8.18. attached to the side of a building and above the first level above grade shall satisfy the following requirements: for connections where the body of the connection is ductile, the body shall be designed for values of Cp, Ar and Rp given in Table 4.1.8.18., and all of the other parts of the connection, such as anchors, welds, bolts and inserts, shall be capable of developing 2.0 times the nominal yield resistance of the body of the connection, and connections where the body of the connection is not ductile shall be designed for values of Cp = 2.0, Rp = 1.0 and Ar given in Table 4.1.8.18., and a ductile connection is one where the body of the connection is capable of dissipating energy through cyclic inelastic behaviour. | obc2019_divb | Div B | 4.1.8.18.(7) | 4.1.8.18. Elements of Structures, Non-Structural Components | Connections to the structure of elements and components listed in Table 4.1.8.18. shall be designed to support the component or element for gravity loads, shall conform to the requirements of Sentence (1), and shall also satisfy these additional requirements: (a) friction due to gravity loads shall not be considered to provide resistance to seismic forces, (b) Rp for non-ductile connections, such as adhesives or power actuated fasteners, shall be taken as 1.0, (c) Rp for anchorage using shallow expansion, chemical, epoxy or cast-in place anchors shall be 1.5, where shallow anchors are those with a ratio of embedment length to diameter of less than 8, (d) power-actuated fasteners and drop-in anchors shall not be used for tension loads, (e) connections for non-structural elements or components of Category 1, 2 or 3 of Table 4.1.8.18. attached to the side of a building and above the first level above grade shall satisfy the following requirements: (i) for connections where the body of the connection is ductile, the body shall be designed for values of CP, Ar and Rp given in Table 4.1.8.18., and all of the other parts of the connection, such as anchors, welds, bolts and inserts, shall be capable of developing 2.0 times the nominal yield resistance of the body of the connection, and (ii) connections where the body of the connection is not ductile shall be designed for values of Cp = 2.0, Rp = 1.0 and Ar given in Table 4.1.8.18., and (f) a ductile connection is one where the body of the connection is capable of dissipating energy through cyclic inelastic behaviour. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.18.(8) | Elements of Structures, Non-structural Components and Equipment | Floors and roofs acting as diaphragms shall satisfy the requirements for diaphragms stated in Article 4.1.8.15. | obc2019_divb | Div B | 4.1.8.18.(8) | 4.1.8.18. Elements of Structures, Non-Structural Components | Floors and roofs acting as diaphragms shall satisfy the requirements for diaphragms stated in Article 4.1.8.15. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.18.(9) | Elements of Structures, Non-structural Components and Equipment | Lateral deflections of elements or components shall be based on the loads defined in Sentence (1) and lateral deflections obtained from an elastic analysis shall be multiplied by Rp/IE to give realistic values of the anticipated deflections. | obc2019_divb | Div B | 4.1.8.18.(9) | 4.1.8.18. Elements of Structures, Non-Structural Components | Lateral deflections of elements or components shall be based on the loads defined in Sentence (1) and lateral deflections obtained from an elastic analysis shall be multiplied by Rp/IE to give realistic values of the anticipated deflections. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.19.(1) | Seismic Isolation | For the purposes of this Article and Article 4.1.8.20., the following terms shall have the meaning stated herein: a) "seismic isolation" is an alternative seismic design concept that consists of installing an isolation system with low horizontal stiffness, thereby substantially increasing the fundamental period of the structure, b) "isolation system" is a collection of structural elements at the level of the isolation interface that includes all individual isolator units, all structural elements that transfer force between elements of the isolation system, all connections to other structural elements, and may also include a wind-restraint system, energy-dissipation devices, and a displacement restraint system, c) "seismically isolated structure" includes the upper portion of the structure above the isolation system, the isolation system, and the portion of the structure below the isolation system, d) "isolator unit" is a structural element of the isolation system that permits large lateral deformations under lateral earthquake design forces and is characterized by vertical-load-carrying capability combined with increased horizontal flexibility and high vertical stiffness, energy dissipation (hysteretic or viscous), self-centering capability, and lateral restraint (sufficient elastic stiffness) under non-seismic service lateral loads, e) "isolation interface" is the boundary between the isolated upper portion of the structure above the isolation system and the lower portion of the structure below the isolation system, and (f) "wind-restraint system" is the collection of structural elements of the isolation system that provides restraint of the seismically isolated structure for wind loads and is permitted to be either an integral part of the isolator units or a separate device. | obc2019_divb | Div B | 4.1.8.19.(1) | 4.1.8.19. Seismic Isolation | For the purposes of this Article and Article 4.1.8.20., the following terms shall have the meaning stated herein: (a) "seismic isolation" is an alternative seismic design concept that consists of installing an isolation system with low horizontal stiffness, thereby substantially increasing the fundamental period of the structure, (b) "isolation system" is a collection of structural elements at the level of the isolation interface that includes all individual isolator units, all structural elements that transfer force between elements of the isolation system, all connections to other structural elements, and may also include a wind-restraint system, energy-dissipation devices, and a displacement restraint system, (c) "seismically isolated structure" includes the upper portion of the structure above the isolation system, the isolation system, and the portion of the structure below the isolation system, (d) "isolator unit" is a structural element of the isolation system that permits large lateral deformations under lateral earthquake design forces and is characterized by vertical-load-carrying capability combined with increased horizontal flexibility and high vertical stiffness, energy dissipation (hysteretic or viscous), self-centering capability, and lateral restraint (sufficient elastic stiffness) under non-seismic service lateral loads, (e) "isolation interface" is the boundary between the isolated upper portion of the structure above the isolation system and the lower portion of the structure below the isolation system, and (f) "wind-restraint system" is the collection of structural elements of the isolation system that provides restraint of the seismically isolated structure for wind loads and is permitted to be either an integral part of the isolator units or a separate device. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.19.(2) | Seismic Isolation | Every seismically isolated structure and every portion thereof shall be analyzed and designed in accordance with, (a) the loads and requirements prescribed in this Article and Article 4.1.8.20., (b) other applicable requirements of this Subsection, and (c) appropriate engineering principles and current engineering practice. (See Note A-4.1.8.19.(2)) | obc2019_divb | Div B | 4.1.8.19.(2) | 4.1.8.19. Seismic Isolation | Every seismically isolated structure and every portion thereof shall be analyzed and designed in accordance with, (a) the loads and requirements prescribed in this Article and Article 4.1.8.20., (b) other applicable requirements of this Subsection, and (c) appropriate engineering principles and current engineering practice. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.19.(3) | Seismic Isolation | For the analysis and modeling of the seismically isolated structure, the following criteria shall apply: a three-dimensional Non-linear Dynamic Analysis of the structure shall be performed in accordance with Article 4.1.8.12. (see Note A-4.1.8.19.(3)(a)), unless verified from rational analysis, the inherent equivalent viscous dampingâ€”excluding the hysteretic damping provided by the isolation system or supplemental energy dissipation devicesâ€”used in the analysis shall not be taken as more than 2.5% of the critical damping at the significant modes of vibration, all individual isolator units shall be modeled with sufficient detail to account for their non-linear force-deformation characteristics, including effects of the relevant loads, and with consideration of variations in material properties over the design life of the structure, and except for elements of the isolation system, other components of the seismically isolated structure shall be modeled using elastic material properties in accordance with Sentence 4.1.8.3.(8). | obc2019_divb | Div B | 4.1.8.19.(3) | 4.1.8.19. Seismic Isolation | For the analysis and modeling of the seismically isolated structure, the following criteria shall apply: (a) three dimensional Non-Linear Dynamic Analysis of the structure shall be performed in accordance with Article 4.1.8.12, (See Appendix A.) (b) unless verified from rational analysis, the inherent equivalent viscous damping Ã¢â‚¬" excluding the hysteretic damping provided by the isolation system or supplemental energy dissipation devices Ã¢â‚¬" used in the analysis shall not be taken as more than 2.5% of the critical damping at the significant modes of vibration, (c) all individual isolator units shall be modeled with sufficient detail to account for their non-linear force-deformation characteristics, including effects of the relevant loads, and with consideration of variations in material properties over the design life of the structure, and (d) except for elements of the isolation system, other components of the seismically isolated structure shall be modeled using elastic material properties in accordance with Sentence 4.1.8.3.(8). | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.19.(4) | Seismic Isolation | The ground motion histories used in Sentence 4.1.8.19.(3) shall be appropriately selected and scaled following good engineering practice, compatible with a response spectrum derived from the design spectral acceleration values, S(T), defined in Sentence 4.1.8.4.(9) for ground conditions of Site Classes A, B and C, and a 5% damped response spectrum based on a site-specific evaluation for ground conditions of Site Classes D, E and F, and amplitude-scaled in an appropriate manner over the period range of 0.2 T1 to 1.5 T1 , where T1 is the period of the isolated structure determined using the post-yield stiffness of the isolation system in the horizontal direction under consideration, or the period specified in Sentence 4.1.8.20.(1) if the post-yield stiffness of the isolation system is not well defined. | obc2019_divb | Div B | 4.1.8.19.(4) | 4.1.8.19. Seismic Isolation | The ground motion histories used in Sentence (3) shall be, (a) appropriately selected and scaled following good engineering practice, (b) compatible with, (i) a response spectrum derived from the design spectral acceleration values, S(T), defined in Sentence 4.1.8.4.(9) for ground conditions of Site Classes A, B and C, and (ii) a 5% damped response spectrum based on a site-specific evaluation for ground conditions of Site Classes D, E and F, and (c) amplitude-scaled in an appropriate manner over the period range of 0.2 T1 to 1.5 T1, where T1 is the period of the isolated structure determined using the post-yield stiffness of the isolation system in the horizontal direction under consideration, or the period specified in Sentence 4.1.8.20.(1) if the post-yield stiffness of the isolation system is not well defined. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.2.(1) | Notation | Notation for Equation | obc2019_divb | Div B | 4.1.8.2.(1) | 4.1.8.2. Notation | Notation for Equation | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.2.(10) | Analysis | Deflections obtained from a linear analysis shall include the effects of torsion and be multiplied by Rs/IE to get realistic values of expected deflections. | obc2019_divb | Div B | 4.1.8.2.(10) | 4.1.8.1. Analysis | Deflections obtained from a linear analysis shall include the effects of torsion and be multiplied by Rs/IE to get realistic values of expected deflections. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.2.(14) | Analysis | The value of Vsp shall be doubled for unreinforced masonry elements. | obc2019_divb | Div B | 4.1.8.2.(14) | 4.1.8.1. Analysis | The value of Vsp shall be doubled for unreinforced masonry elements. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.2.(6) | Analysis | Earthquake forces shall be assumed to act horizontally and independently about any two orthogonal axes. | obc2019_divb | Div B | 4.1.8.2.(6) | 4.1.8.2.(4) | Earthquake forces shall be assumed to act horizontally and independently about any two orthogonal axes. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.20.(10) | Seismic Isolation Design Provisions | The isolation system, including a separate wind-restraint system if used, shall limit lateral displacement due to wind loads across the isolation interface to a value equal to that required for the least storey height in accordance with Sentence 4.1.3.5.(3) | obc2019_divb | Div B | 4.1.8.20.(10) | 4.1.8.20. Seismic Isolation Design Provisions | The isolation system, including a separate wind-restraint system if used, shall limit lateral displacement due to wind loads across the isolation interface to a value equal to that required for the least storey height in accordance with Sentence 4.1.3.5.(3) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.20.(3) | Seismic Isolation Design Provisions | The values of storey shears, storey forces, member forces, and deflections used in the design of all structural framing elements and components of the isolation system shall be obtained from analysis conforming to Sentence 4.1.8.19.(3) using one of the following values, whichever produces the most critical effect: mean plus IE times the standard deviation of results of all Non-linear Dynamic Analyses, or ?IE times the mean of the results of all Non-linear Dynamic Analyses. | obc2019_divb | Div B | 4.1.8.20.(3) | 4.1.8.20. Seismic Isolation Design Provisions | The values of storey shears, storey forces, member forces, and deflections used in the design of all structural framing elements and components of the isolation system shall be obtained from analysis conforming to Sentence 4.1.8.19.(3) using one of the following values, whichever produces the most critical effect: (a) mean plus IE times the standard deviation of the results of all Non-Linear Dynamic Analyses, or (b) times the mean of the results of all Non-Linear Dynamic Analyses. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.20.(4) | Seismic Isolation Design Provisions | The force-deformation and damping characteristics of the isolation system used in the analysis and design of seismically isolated structures shall be validated by testing at least two full-size specimens of each predominant type and size of isolator unit of the isolation system, which shall include the individual isolator units, separate supplemental damping devices, if used, and separate sacrificial wind-restraint systems, if used. | obc2019_divb | Div B | 4.1.8.20.(4) | 4.1.8.20. Seismic Isolation Design Provisions | The force-deformation and damping characteristics of the isolation system used in the analysis and design of the seismically isolated structures shall be validated by testing at least two full-size specimens of each predominant type and size of isolator unit of the isolation system, which shall include, (a) the individual isolator units, (b) separate supplemental damping devices, if used, and (c) separate sacrificial wind-restraint systems, if used. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.20.(5) | Seismic Isolation Design Provisions | A diaphragm or horizontal structural elements shall provide continuity immediately above the isolation interface to transmit forces due to non-uniform ground motions from one part of the structure to another. | obc2019_divb | Div B | 4.1.8.20.(6) | 4.1.8.20. Seismic Isolation Design Provisions | A diaphragm or horizontal structural elements shall provide continuity immediately above the isolation interface to transmit forces due to non-uniform ground motions from one part of the structure to another. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.20.(5) | Seismic Isolation Design Provisions | The force-deformation characteristics and damping value of a representative sample of the isolator units installed in the building shall be validated by tests prior to their installation. | obc2019_divb | Div B | 4.1.8.20.(5) | 4.1.8.20. Seismic Isolation Design Provisions | The force-deformation characteristics and damping value of a representative sample of the isolator units installed in the building shall be validated by tests prior to their installation. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.20.(7) | Seismic Isolation Design Provisions | All structural framing elements shall be designed for the forces described in Sentence 4.1.8.20.(3) with RdRo= 1.0, except for structures with IE &lt; 1.5, all SFRS shall be detailed in accordance with the requirements for Rd ? 1.5 and the applicable referenced design standards, and for structures with IE = 1.5, all SFRS shall be detailed in accordance with the requirements for Rd ? 2.0 and the applicable referenced design standards. | obc2019_divb | Div B | 4.1.8.20.(7) | 4.1.8.20. Seismic Isolation Design Provisions | All structural framing elements shall be designed for the forces described in Sentence (3) with RdRo= 1.0, except, (a) for structures with IE &lt; 1.5, all the SFRS shall be detailed in accordance with the requirements for Rd Ã¢â€°Â¥ 1.5 and the applicable referenced design standards, and (b) for structures with IE = 1.5, all the SFRS shall be detailed in accordance with the requirements for Rd Ã¢â€°Â¥ 2.0 and the applicable referenced design standards. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.20.(8) | Seismic Isolation Design Provisions | The height restrictions noted in Table 4.1.8.9. need not apply to seismically isolated structures. | obc2019_divb | Div B | 4.1.8.20.(8) | 4.1.8.20. Seismic Isolation Design Provisions | The height restrictions noted in Table 4.1.8.9. need not apply to seismically isolated structures. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.20.(9) | Seismic Isolation Design Provisions | All isolator units shall be, a) designed for the forces described in Sentence (3), and b) able to accommodate the TDD determined at the specific location of each isolator unit. | obc2019_divb | Div B | 4.1.8.20.(9) | 4.1.8.20. Seismic Isolation Design Provisions | All isolator units shall be, (a) designed for the forces described in Sentence (3), and (b) able to accommodate the TDD determined at the specific location of each isolator unit. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.21.(1) | Supplemental Energy Dissipation | For the purposes of this Article and Article 4.1.8.22., the following terms shall have the meaning stated herein: a) "supplemental energy dissipation device" is a dedicated structural element of the supplemental energy dissipation system that dissipates energy due to relative motion of each of its ends or by alternative means, and includes all pins, bolts, gusset plates, brace extensions and other components required to connect it to the other elements of the structure; a device may be classified as either displacement-dependent or velocity-dependent, or a combination thereof, and may be configured to act in either a linear or non-linear manner, and b) "supplemental energy dissipation system" is a collection of energy dissipation devices installed in a structure that supplement the energy dissipation of the SFRS. | obc2019_divb | Div B | 4.1.8.21.(1) | 4.1.8.21. Supplemental Energy Dissipation | For the purposes of this Article and Article 4.1.8.22., the following terms shall have the meaning stated herein: (a) "supplemental energy dissipation device" is a dedicated structural element of the supplemental energy dissipation system that dissipates energy due to relative motion of each of its ends or by alternative means, and includes all pins, bolts, gusset plates, brace extensions and other components required to connect it to the other elements of the structure; a device may be classified as either displacement-dependent or velocity-dependent, or a combination thereof, and may be configured to act in either a linear or non-linear manner, and (b) "supplemental energy dissipation system" is a collection of energy dissipation devices installed in a structure that supplement the energy dissipation of the SFRS. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.21.(1) | Seismic Isolation Design Provisions | The period of the isolated structure, determined using the post-yield stiffness of the isolation system in the horizontal direction under consideration, shall be greater than three times the period of the structure above the isolation interface calculated as a fixed base. | obc2019_divb | Div B | 4.1.8.21.(1) | 4.1.8.20. Seismic Isolation Design Provisions | The period of the isolated structure, determined using the post-yield stiffness of the isolation system in the horizontal direction under consideration, shall be greater than three times the period of the structure above the isolation interface calculated as a fixed base. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.21.(2) | Supplemental Energy Dissipation | Every structure with a supplemental energy dissipation system and every portion thereof shall be designed and constructed in accordance with, a) the loads and requirements prescribed in this Article and Article 4.1.8.22., b) other applicable requirements of this Subsection, and c) appropriate engineering principles and current engineering practice.(See Note A-4.1.8.21.(2).) | obc2019_divb | Div B | 4.1.8.21.(2) | 4.1.8.21. Supplemental Energy Dissipation | Every structure with a supplemental energy dissipation system and every portion thereof shall be designed and constructed in accordance with, (a) the loads and requirements prescribed in this Article and Article 4.1.8.22., (b) other applicable requirements of this Subsection, and (c) appropriate engineering principles and current engineering practice. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.21.(2) | Seismic Isolation Design Provisions | The isolation system shall be configured to produce a restoring force such that the lateral force at the TDD at the centre of mass of the isolated structure above the isolation interface is at least 0.025Wb greater than the lateral force at 50% of the TDD at the same location, in each horizontal direction, where Wb is the portion of W above the isolation interface. | obc2019_divb | Div B | 4.1.8.21.(2) | 4.1.8.20. Seismic Isolation Design Provisions | The isolation system shall be configured to produce a restoring force such that the lateral force at the TDD at the centre of mass of the isolated structure above the isolation interface is at least 0.025Wb greater than the lateral force at 50% of the TDD at the same location, in each horizontal direction, where Wb is the portion of W above the isolation interface. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.21.(3) | Supplemental Energy Dissipation | Where supplemental energy dissipation devices are used across the isolation interface of a seismically isolated structure, displacements, velocities, and accelerations shall be determined in accordance with Article 4.1.8.20. | obc2019_divb | Div B | 4.1.8.21.(3) | 4.1.8.21. Supplemental Energy Dissipation | Where supplemental energy dissipation devices are used across the isolation interface of a seismically isolated structure, displacements, velocities, and accelerations shall be determined in accordance with Article 4.1.8.20. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.21.(4) | Supplemental Energy Dissipation | For the analysis and modeling of structures with supplemental energy dissipation devices, the following criteria shall apply: a three-dimensional Non-linear Dynamic Analysis of the structure shall be performed in accordance with Article 4.1.8.12. (see Note A-4.1.8.21.(4)(a)), for SFRS with Rd > 1.0, the non-linear hysteretic behaviour of the SFRS shall be explicitlyâ€”with sufficient detailâ€”accounted for in the modeling and analysis of the structure, unless verified from rational analysis, the inherent equivalent viscous dampingâ€”excluding the damping provided by the supplemental energy dissipation devicesâ€”used in the analysis shall not be taken as more than 2.5% of the critical damping at the significant modes of vibration, all supplemental energy dissipation devices shall be modeled with sufficient detail to account for their non-linear force deformation characteristics, including effects of the relevant loads, and with consideration of variations in their properties over the design life of the structure, and except for the SFRS and elements of the supplemental energy dissipation system, other components of the structure shall be modeled using elastic material properties in accordance with Sentence 4.1.8.3.(8). | obc2019_divb | Div B | 4.1.8.21.(4) | 4.1.8.21. Supplemental Energy Dissipation | For the analysis and modeling of structures with supplemental energy dissipation devices, the following criteria shall apply: (a) a three-dimensional Non-Linear Dynamic Analysis of the structure shall be performed in accordance with Article 4.1.8.12., (See Appendix A.) (b) for SFRS with Rd > 1.0, the non-linear hysteretic behaviour of the SFRS shall be explicitly Ã¢â‚¬" with sufficient detail Ã¢â‚¬" accounted for in the modeling and analysis of the structure, (c) unless verified from rational analysis, the inherent equivalent viscous damping Ã¢â‚¬" excluding the damping provided by the supplemental energy dissipation devices Ã¢â‚¬" used in the analysis shall not be taken as more than 2.5% of the critical damping at the significant modes of vibration, (d) all supplemental energy dissipation devices shall be modeled with sufficient detail to account for their non-linear force deformation characteristics, including effects of the relevant loads, and with consideration of variations in their properties over the design life of the structure, and (e) except for the SFRS and elements of the supplemental energy dissipation system, other components of the structure shall be modeled using elastic material properties in accordance with Sentence 4.1.8.3.(8). | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.21.(5) | Supplemental Energy Dissipation | The ground motion histories used in Sentence 4.1.8.21.(4) shall be appropriately selected and scaled following good engineering practice, compatible with a 5% damped response spectrum derived from the design spectral acceleration values, S(T), defined in Sentence 4.1.8.4.(9), and amplitude-scaled in an appropriate manner over the period range of 0.2 T1 to 1.5 T1 , where T1 is the fundamental lateral period of the structure with the supplemental energy dissipation system. | obc2019_divb | Div B | 4.1.8.21.(5) | 4.1.8.21. Supplemental Energy Dissipation | The ground motion histories used in Sentence (4) shall be, (a) appropriately selected and scaled following good engineering practice, (b) compatible with a 5% damped response spectrum derived from the design spectral acceleration values, S(T), defined in Sentence 4.1.8.4.(9), and (c) amplitude-scaled in an appropriate manner over the period range of 0.2 T1 to 1.5 T1, where T1 is the fundamental lateral period of the structure with the supplemental energy dissipation system. (See Appendix Note A-.4.1.8.19.(4)) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.22.(1) | Supplemental Energy Dissipation Design Considerations | The values of storey shears, storey forces, member forces, and deflections for the design of all structural framing elements and all supplemental energy dissipation devices shall be obtained from analysis conforming to Sentence 4.1.8.21.(4) using one of the following values, whichever produces the most critical effect: mean plus IE times the standard deviation of the results of all Non-linear Dynamic Analyses, or ?IE times the mean of the results of all Non-linear Dynamic Analyses. | obc2019_divb | Div B | 4.1.8.22.(1) | 4.1.8.22. Supplemental Energy Dissipation Design Considerations | The values of storey shears, storey forces, member forces, and deflections for the design of all structural framing elements and all supplemental energy dissipation devices shall be obtained from analysis conforming to Sentence 4.1.8.21.(4) using one of the following values, whichever produces the most critical effect: (a) mean plus IE times the standard deviation of the results of all Non-Linear Dynamic Analyses, or (b) times the mean of the results of all Non-Linear Dynamic Analyses. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.22.(2) | Supplemental Energy Dissipation Design Considerations | The largest interstorey deflection at any level of the structure as determined in accordance with Sentence (1) shall conform to the limits stated in Sentence 4.1.8.13.(3). | obc2019_divb | Div B | 4.1.8.22.(2) | 4.1.8.22. Supplemental Energy Dissipation Design Considerations | The largest interstorey deflection at any level of the structure as determined in accordance with Sentence (1) shall conform to the limits stated in Sentence 4.1.8.13.(3). | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.22.(3) | Supplemental Energy Dissipation Design Considerations | The force-deformation and force-velocity characteristics of the supplemental energy dissipation devices used in the analysis and design of structures with supplemental energy dissipation systems shall be validated by testing at least two full-size specimens of each type of supplementary energy dissipation device. | obc2019_divb | Div B | 4.1.8.22.(3) | 4.1.8.22. Supplemental Energy Dissipation Design Considerations | The force-deformation and force-velocity characteristics of the supplemental energy dissipation devices used in the analysis and design of structures with supplemental energy dissipation systems shall be validated by testing at least two full-size specimens of each type of supplemental energy dissipation device. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.22.(4) | Supplemental Energy Dissipation Design Considerations | The force-deformation and force-velocity characteristics and damping values of a representative sample of the supplemental energy dissipation devices installed in the building shall be validated by tests prior to their installation. | obc2019_divb | Div B | 4.1.8.22.(4) | 4.1.8.22. Supplemental Energy Dissipation Design Considerations | The force-deformation and force-velocity characteristics and damping values of a representative sample of the supplemental energy dissipation devices installed in the building shall be validated by tests prior to their installation. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.22.(5) | Supplemental Energy Dissipation Design Considerations | Elements of the supplemental energy dissipation system, except the supplemental energy dissipation devices themselves, shall be designed to remain elastic for the design loads. | obc2019_divb | Div B | 4.1.8.22.(5) | 4.1.8.22. Supplemental Energy Dissipation Design Considerations | Elements of the supplemental energy dissipation system, except the supplemental energy dissipation devices themselves, shall be designed to remain elastic for the design loads. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.22.(6) | Supplemental Energy Dissipation Design Considerations | All structural framing elements shall be designed for an SFRS with Rd =1.0, using the forces referred to in Sentence 4.1.8.22.(1) with RdRo = 1.0, except that the SFRS shall be detailed in accordance with the requirements for Rd ? 1.5 and the applicable referenced design standards, or for an SFRS with Rd > 1.0, using the forces referred to in Sentence 4.1.8.22.(1) with RdRo = 1.0, except that the SFRS shall be detailed in accordance with the requirements for the selected Rd and the applicable referenced design standards. | obc2019_divb | Div B | 4.1.8.22.(6) | 4.1.8.22. Supplemental Energy Dissipation Design Considerations | All structural framing elements shall be designed, (a) for an SFRS with Rd =1.0, using the forces referred to in Sentence (1) with RdRo = 1.0, except that the SFRS shall be detailed in accordance with the requirements for Rd Ã¢â€°Â¥ 1.5 and the applicable referenced design standards, or (b) for an SFRS with Rd > 1.0, using the forces referred to in Sentence (1) with RdRo = 1.0, except that the SFRS shall be detailed in accordance with the requirements for the selected Rd and the applicable referenced design standards. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.22.(7) | Supplemental Energy Dissipation Design Considerations | Supplemental energy dissipation devices and other components of the supplemental energy dissipation system shall be designed in accordance with Sentence 4.1.8.22.(1) with consideration of the following: low-cycle, large-displacement degradation due to seismic loads, high-cycle, small-displacement degradation due to wind, thermal, or other cyclic loads, forces or displacements due to gravity loads, adhesion of device parts due to corrosion or abrasion, biodegradation, moisture, or chemical exposure, exposure to environmental conditions, including, but not limited to, temperature, humidity, moisture, radiation (e.g., ultraviolet light), and reactive or corrosive substances (e.g., salt water), devices subject to failure due to low-cycle fatigue must resist wind forces without slip, movement, or inelastic cycling, the range of thermal conditions, device wear, manufacturing tolerances, and other effects that cause device properties to vary during the design life of the device, and connection points of devices must provide sufficient articulation to accommodate simultaneous longitudinal, lateral, and vertical displacements of the supplemental energy dissipation system. | obc2019_divb | Div B | 4.1.8.22.(7) | 4.1.8.22. Supplemental Energy Dissipation Design Considerations | Supplemental energy dissipation devices and other components of the supplemental energy dissipation system shall be designed in accordance with Sentence (1) with consideration of the following: (a) low-cycle, large-displacement degradation due to seismic loads, (b) high-cycle, small-displacement degradation due to wind, thermal, or other cyclic loads, (c) forces or displacements due to gravity loads, (d) adhesion of device parts due to corrosion or abrasion, biodegradation, moisture, or chemical exposure, (e) exposure to environmental conditions, including, but not limited to, temperature, humidity, moisture, radiation (e.g., ultraviolet light), and reactive or corrosive substances (e.g., salt water), (f) devices subject to failure due to low-cycle fatigue must resist wind forces without slip, movement, or inelastic cycling, (g) the range of thermal conditions, device wear, manufacturing tolerances, and other effects that cause device properties to vary during the design life of the device, and (h) connection points of devices must provide sufficient articulation to accommodate simultaneous longitudinal, lateral, and vertical displacements of the supplemental energy dissipation system. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.3.(1) | General Requirements | The building shall be designed to meet the requirements of this Subsection and of the design standards referenced in Section 4.3. | obc2019_divb | Div B | 4.1.8.3.(1) | 4.1.8.3. General Requirements | The building shall be designed to meet the requirements of this Subsection and of the design standards referenced in Section 4.3. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.3.(2) | General Requirements | _Structures shall be designed with a clearly defined load path, or paths, that will transfer the inertial forces generated in an earthquake to the supporting ground. | obc2019_divb | Div B | 4.1.8.3.(2) | 4.1.8.3. General Requirements | Structures shall be designed with a clearly defined load path, or paths, that will transfer the inertial forces generated in an earthquake to the supporting ground. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.3.(3) | General Requirements | The structure shall have a clearly defined Seismic Force Resisting System(s) (SFRS), as defined in Article 4.1.8.2. | obc2019_divb | Div B | 4.1.8.3.(3) | 4.1.8.3. General Requirements | The structure shall have a clearly defined Seismic Force Resisting System(s) (SFRS), as defined in Article 4.1.8.2. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.3.(4) | General Requirements | The SFRS shall be designed to resist 100% of the earthquake loads and their effects. (See Note A-4.1.8.3.(4).) | obc2019_divb | Div B | 4.1.8.3.(4) | 4.1.8.3. General Requirements | The SFRS shall be designed to resist 100% of the earthquake loads and their effects. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.3.(5) | General Requirements | All structural framing elements not considered to be part of the SFRS must be investigated and shown to behave elastically or to have sufficient non-linear capacity to support their gravity loads while undergoing earthquake-induced deformations calculated from the deflections determined in Article 4.1.8.13. | obc2019_divb | Div B | 4.1.8.3.(5) | 4.1.8.3. General Requirements | All structural framing elements not considered to be part of the SFRS must be investigated and shown to behave elastically or to have sufficient non-linear capacity to support their gravity loads while undergoing earthquake-induced deformations calculated from the deflections determined in Article 4.1.8.13. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.3.(6) | General Requirements | Stiff elements that are not considered part of the SFRS, such as concrete, masonry, brick or pre-cast walls or panels, shall be a) separated from all structural elements of the building such that no interaction takes place as the building undergoes deflections due to earthquake effects as calculated in this Subsection, or b) made part of the SFRS and satisfy the requirements of this Subsection. (See See Note A-4.1.8.3.(6).) | obc2019_divb | Div B | 4.1.8.3.(6) | 4.1.8.3. General Requirements | Stiff elements that are not considered part of the SFRS, such as concrete, masonry, brick or pre-cast walls or panels, shall be, (a) separated from all structural elements of the building such that no interaction takes place as the building undergoes deflections due to earthquake effects as calculated in this Subsection, or (b) made part of the SFRS and satisfy the requirements of this Subsection. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.3.(7) | General Requirements | Stiffness imparted to the structure from elements not part of the SFRS, other than those described in Sentence 4.1.8.3.(6), shall not be used to resist earthquake deflections but shall be accounted for in calculating the period of the structure for determining forces if the added stiffness decreases the fundamental lateral period by more than 15%, in determining the irregularity of the structure, except the additional stiffness shall not be used to make an irregular SFRS regular or to reduce the effects of torsion (see Note A-4.1.8.3.(7)(b)), and in designing the SFRS if inclusion of the elements not part of the SFRS in the analysis has an adverse effect on the SFRS (see Note A-4.1.8.3.(7)(b)). | obc2019_divb | Div B | 4.1.8.3.(7) | 4.1.8.3. General Requirements | Stiffness imparted to the structure from elements not part of the SFRS, other than those described in Sentence (6), shall not be used to resist earthquake deflections but shall be accounted for, (a) in calculating the period of the structure for determining forces if the added stiffness decreases the fundamental lateral period by more than 15%, (b) in determining the irregularity of the structure, except the additional stiffness shall not be used to make an irregular SFRS regular or to reduce the effects of torsion, and (See Appendix A.) (c) in designing the SFRS if inclusion of the elements not part of the SFRS in the analysis has an adverse effect on the SFRS. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.3.(8) | General Requirements | Structural modeling shall be representative of the magnitude and spatial distribution of the mass of the building and of the stiffness of all elements of the SFRS, including stiff elements that are not separated in accordance with Sentence 4.1.8.3.(6), and shall account for the effect of cracked sections in reinforced concrete and reinforced masonry elements, the effect of the finite size of members and joints, sway effects arising from the interaction of gravity loads with the displaced configuration of the structure, and other effects that influence the lateral stiffness of the building. | obc2019_divb | Div B | 4.1.8.3.(8) | 4.1.8.3. General Requirements | Structural modelling shall be representative of the magnitude and spatial distribution of the mass of the building and of the stiffness of all elements of the SFRS, including stiff elements that are not separated in accordance with SentenceÃ‚ 4.1.8.3.(6), and shall account for, (a) the effect of cracked sections in reinforced concrete and reinforced masonry elements, (b) the effect of the finite size of members and joints, (c) sway effects arising from the interaction of gravity loads with the displaced configuration of the structure, and (d) other effects that influence the lateral stiffness of the building. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.4.(1) | Site Properties | The peak ground acceleration (PGA), peak ground velocity (PGV) and the 5% damped spectral response acceleration values, Sa(T), for the reference ground conditions (Site Class C in Table 4.1.8.4.-A.) for periods T of 0.2 s, 0.5 s, 1.0 s, 2.0 s, 5.0 s and 10.0 s, shall be determined in accordance with Subsection 1.1.3. and are based on a 2% probability of exceedance in 50 years. | obc2019_divb | Div B | 4.1.8.4.(1) | 4.1.8.4. Site Properties | The peak ground acceleration (PGA), peak ground velocity (PGV) and the 5% damped spectral response acceleration values, Sa(T), for the reference ground conditions (Site Class C in Table 4.1.8.4.A.) for periods T of 0.2 s, 0.5Ã‚ s, 1.0 s, 2.0 s, 5.0 s and 10.0 s, shall be determined in accordance with Subsection 1.1.2. and are based on a 2% probability of exceedance in 50 years. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.4.(2) | Site Properties | Site classifications for ground shall conform to Table 4.1.8.4.-A and shall be determined using V? s30, or where V? s30 is not known, using Sentence 4.1.8.4.(3). | obc2019_divb | Div B | 4.1.8.4.(2) | 4.1.8.4. Site Properties | Site classifications for ground shall conform to Table 4.1.8.4.A. and shall be determined using , or where is not known, using Sentence (3). | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.4.(3) | Site Properties | If average shear wave velocity, V? s30, is not known, Site Class shall be determined from energy-corrected Average Standard Penetration Resistance, N? 60, or from soil average undrained shear strength, su, as noted in Table 4.1.8.4.-A, N? 60 and su being calculated based on rational analysis. (See Note A-4.1.8.4.(3).) | obc2019_divb | Div B | 4.1.8.4.(3) | 4.1.8.4. Site Properties | If average shear wave velocity,, is not known, Site Class shall be determined from energy-corrected Average Standard Penetration Resistance, , or from soil average undrained shear strength, su, as noted in Table 4.1.8.4.A., and su being calculated based on rational analysis. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.4.(4) | Site Properties | For the purpose of determining the values of F(T) to be used in the calculation of design spectral acceleration, S(T), in Sentence 4.1.8.4.(9), and the values of F(PGA) and F(PGV), the value of PGAref to be used with Tables 4.1.8.4.-B to 4.1.8.4.-I shall be taken as 0.8 PGA, where the ratio Sa(0.2)/PGA & lt; 2.0, and PGA, otherwise. | obc2019_divb | Div B | 4.1.8.4.(4) | 4.1.8.4. Site Properties | For the purpose of determining the values of F(T) to be used in the calculation of design spectral acceleration, S(T), in Sentence (9), and the values of F(PGA) and F(PGV), the value of PGAref to be used with Tables 4.1.8.4.B. to 4.1.8.4.I. shall be taken as, (a) 0.8 PGA, where the ratio Sa(0.2)/PGA & lt; 2.0, and (b) 1 PGA, in all other cases. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.4.(5) | Site Properties | The values of the site coefficient for design spectral acceleration at period T, F(T),and of similar coefficients F(PGA) and F(PGV) shall conform toTables 4.1.8.4.-B to 4.1.8.4.I using linear interpolation for intermediate values of PGAref. | obc2019_divb | Div B | 4.1.8.4.(5) | 4.1.8.4 Site Properties | The values of the site coefficient for design spectral acceleration at period T, F(T), and of similar coefficients F(PGA) and F(PGV) shall conform to Tables 4.1.8.4.B. to 4.1.8.4.I. using linear interpolation for intermediate values of PGAref. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.4.(6) | Site Properties | Site-specific evaluation is required to determine F(T), F(PGA) and F(PGV) for Site Class F. (See Note A-4.1.8.4.(3).) | obc2019_divb | Div B | 4.1.8.4.(6) | 4.1.8.4. Site Properties | Site-specific evaluation is required to determine F(T), F(PGA) and F(PGV) for Site Class F. (See Appendix Note A-4.1.8.4.(3)) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.4.(7) | Site Properties | For all applications in Subsection 4.1.8., Fa = F(0.2) and Fv = F(1.0). | obc2019_divb | Div B | 4.1.8.4.(7) | 4.1.8.4. Site Properties | For all applications in Subsection 4.1.8., Fa = F(0.2) and Fv = F(1.0). | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.4.(8) | Site Properties | For structures with a fundamental period of vibration equal to or less than 0.5 s that are built on liquefiable soils, Site Class and the corresponding values of F(T) may be determined as described in Tables 4.1.8.4.-A , 4.1.8.4.-B, and 4.1.8.4.-C by assuming that the soils are not liquefiable. (See Note A-4.1.8.4.(3).) | obc2019_divb | Div B | 4.1.8.4.(8) | 4.1.8.4. Site Properties | For structures with a fundamental period of vibration equal to or less than 0.5 s that are built on liquefiable soils, Site Class and the corresponding values of F(T) may be determined as described in Tables 4.1.8.4.A., 4.1.8.4.B., and 4.1.8.4.C. by assuming that the soils are not liquefiable. (See Appendix Note A-4.1.8.4.(3)) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.4.(9) | Site Properties | The design spectral acceleration values of S(T) shall be determined as follows, using linear interpolation for intermediate values of T: S(T) = F(0.2)Sa(0.2) or F(0.5)Sa(0.5), whichever is larger, for T ? 0.2 s = F(0.5)Sa(0.5) for T = 0.5 s = F(1.0)Sa(1.0) for T = 1.0 s = F(2.0)Sa(2.0) for T = 2.0 s = F(5.0)Sa(5.0) for T = 5.0 s = F(10.0)Sa(10.0) for T ? 10.0 s | obc2019_divb | Div B | 4.1.8.4.(9) | 4.1.8.4 Site Properties | The design spectral acceleration values of S(T) shall be determined as follows, using linear interpolation for intermediate values of T: S(T) = F(0.2)Sa(0.2) or F(0.5)Sa(0.5), whichever is larger, for T ? 0.2 s = F(0.5)Sa(0.5) for T = 0.5 s = F(1.0)Sa(1.0) for T = 1.0 s = F(2.0)Sa(2.0) for T = 2.0 s = F(5.0)Sa(5.0) for T = 5.0 s = F(10.0)Sa(10.0) for T ? 10.0 s | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.5.(1) | Importance Factor | The earthquake importance factor, IE, shall be determined according to Table 4.1.8.5. | obc2019_divb | Div B | 4.1.8.5.(1) | 4.1.8.5. Importance Factor | The earthquake importance factor, IE, shall be determined according to Table 4.1.8.5. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.6.(1) | Structural Configuration | Structures having any of the features listed in Table 4.1.8.6. shall be designated irregular. | obc2019_divb | Div B | 4.1.8.6.(1) | 4.1.8.6. Structural Configuration | Structures having any of the features listed in Table 4.1.8.6. shall be designated irregular. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.6.(2) | Structural Configuration | Structures not classified as irregular according to Sentence 4.1.8.6.(1) may be considered regular. | obc2019_divb | Div B | 4.1.8.6.(2) | 4.1.8.6. Structural Configuration | Structures not classified as irregular according to Sentence 4.1.8.6.(1) may be considered regular. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.6.(3) | Structural Configuration | Except as required by Article 4.1.8.10., in cases where IEFaSa(0.2) is equal to or greater than 0.35, structures designated as irregular must satisfy the provisions referenced in Table 4.1.8.6. | obc2019_divb | Div B | 4.1.8.6.(3) | 4.1.8.6. Structural Configuration | Except as required by Article 4.1.8.10., in cases where IEFaSa(0.2) is equal to or greater than 0.35, structures designated as irregular must satisfy the provisions referenced in Table 4.1.8.6. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.7.(1) | Methods of Analysis | Analysis for design earthquake actions shall be carried out in accordance with the Dynamic Analysis Procedure described in Article 4.1.8.12., except that the Equivalent Static Force Procedure described in Article 4.1.8.11. may be used for structures that meet any of the following criteria: a) in cases where IEFaSa(0.2) is less than 0.35, b) regular structures that are less than 60 m in height and have a fundamental lateral period, Ta, less than 2 s in each of two orthogonal directions as defined in Article 4.1.8.8., or c) structures with structural irregularity, of Type 1, 2, 3, 4, 5, 6 or 8 as defined in Table 4.1.8.6., that are less than 20 m in height and have a fundamental lateral period, Ta, less than 0.5 s in each of two orthogonal directions as defined in Article 4.1.8.8. | obc2019_divb | Div B | 4.1.8.7.(1) | 4.1.8.7. Methods of Analysis | Analysis for design earthquake actions shall be carried out in accordance with the Dynamic Analysis Procedure described in Article 4.1.8.12., except that the Equivalent Static Force Procedure described in Article 4.1.8.11. may be used for structures that meet any of the following criteria: (See Appendix A.) (a) in cases where IEFaSa(0.2) is less than 0.35, (b) regular structures that are less than 60 m in height and have a fundamental lateral period, Ta, less than 2 s in each of two orthogonal directions as defined in Article 4.1.8.8., or (c) structures with structural irregularity, of Type 1, 2, 3, 4, 5, 6 or 8 as defined in Table 4.1.8.6., that are less than 20 m in height and have a fundamental lateral period, Ta, less than 0.5 s in each of two orthogonal directions as defined in Article 4.1.8.8. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.8.(1) | Direction of Loading | Earthquake forces shall be assumed to act in any horizontal direction, except that the following shall be considered to provide adequate design force levels in the structure: a) where components of the SFRS are oriented along a set of orthogonal axes, independent analyses about each of the principal axes of the structure shall be performed, b) where the components of the SFRS are not oriented along a set of orthogonal axes and IEFaSa(0.2) is less than 0.35, independent analyses about any two orthogonal axes is permitted, or c) where the components of the SFRS are not oriented along a set of orthogonal axes and IEFaSa(0.2) is equal to or greater than 0.35, analysis of the structure independently in any two orthogonal directions for 100% of the prescribed earthquake loads applied in one direction plus 30% of the prescribed earthquake loads in the perpendicular direction, with the combination requiring the greater element strength being used in the design. | obc2019_divb | Div B | 4.1.8.8.(1) | 4.1.8.8. Direction of Loading | Earthquake forces shall be assumed to act in any horizontal direction, except that the following shall be considered to provide adequate design force levels in the structure: (a) where components of the SFRS are oriented along a set of orthogonal axes, independent analyses about each of the principal axes of the structure shall be performed, (b) where the components of the SFRS are not oriented along a set of orthogonal axes and IEFaSa(0.2) is less than 0.35, independent analyses about any two orthogonal axes is permitted, or (c) where the components of the SFRS are not oriented along a set of orthogonal axes and IEFaSa(0.2) is equal to or greater than 0.35, analysis of the structure independently in any two orthogonal directions for 100% of the prescribed earthquake loads applied in one direction plus 30% of the prescribed earthquake loads in the perpendicular direction, with the combination requiring the greater element strength being used in the design. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.9.(1) | SFRS Force Reduction Factors, System Overstrength Factors, | Except as provided in Sentence 4.1.8.20.(7), the values of Rd and Ro and the corresponding system restrictions shall conform to Table 4.1.8.9. and the requirements of this Subsection. | obc2019_divb | Div B | 4.1.8.9.(1) | 4.1.8.9. SFRS Force Reduction Factors, System Overstrength | Except as provided in Sentence 4.1.8.20.(7), the values of Rd and Ro and the corresponding system restrictions shall conform to Table 4.1.8.9. and the requirements of this Subsection. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.9.(2) | SFRS Force Reduction Factors, System Overstrength Factors, | When a particular value of Rd is required by this Article, the corresponding Ro shall be used. | obc2019_divb | Div B | 4.1.8.9.(2) | 4.1.8.9. SFRS Force Reduction Factors, System Overstrength | When a particular va1ue of Rd is required by this Article, the corresponding Ro shall be used. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.9.(3) | SFRS Force Reduction Factors, System Overstrength Factors, | For combinations of different types of SFRS acting in the same direction in the same storey, RdRo shall be taken as the lowest value of RdRo corresponding to these systems. | obc2019_divb | Div B | 4.1.8.9.(3) | 4.1.8.9. SFRS Force Reduction Factors, System Overstrength | For combinations of different types of SFRS acting in the same direction in the same storey, RdRo shall be taken as the lowest value of RdRo corresponding to these systems. | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.9.(4) | SFRS Force Reduction Factors, System Overstrength Factors, | For vertical variations of RdRo, excluding rooftop structures not exceeding two storeys in height whose weight is less than the greater of 10% of W and 30% of Wi of the level below, the value of RdRo used in the design of any storey shall be less than or equal to the lowest value of RdRo used in the given direction for the storeys above, and the requirements of Sentence 4.1.8.15.(6) must be satisfied. (See Note A-4.1.8.9.(4).) | obc2019_divb | Div B | 4.1.8.9.(4) | 4.1.8.9. SFRS Force Reduction Factors, System Overstrength | For vertical variations of RdRo, excluding rooftop structures not exceeding two storeys in height whose weight is less than the greater of 10% of W and 30% of Wi of the level below, the value of RdRo used in the design of any storey shall be less than or equal to the lowest value of RdRo used in the given direction for the storeys above, and the requirements of Sentence 4.1.8.15.(5) must be satisfied. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.1.8.9.(5) | SFRS Force Reduction Factors, System Overstrength Factors, | If it can be demonstrated through testing, research and analysis that the seismic performance of a structural system is at least equivalent to one of the types of SFRS mentioned in Table 4.1.8.9., then such a structural system will qualify for values of Rd and Ro corresponding to the equivalent type in that Table. (See Note A-4.1.8.9.(5).) | obc2019_divb | Div B | 4.1.8.9.(5) | 4.1.8.9. SFRS Force Reduction Factors, System Overstrength | If it can be demonstrated through testing, research and analysis that the seismic performance of a structural system is at least equivalent to one of the types of SFRS mentioned in Table 4.1.8.9., then such a structural system will qualify for values of Rd and Ro corresponding to the equivalent type in that Table. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.1.1.(1) | Application | This Section applies to excavations and foundation systems for buildings. | obc2019_divb | Div B | 4.2.1.1.(1) | 4.2.1.1. Application | This Section applies to excavations and foundation systems for buildings. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.2.1.(1) | Subsurface Investigation | A subsurface investigation, including groundwater conditions, shall be carried out by or under the direction of a professional engineer having knowledge and experience in planning and executing such investigations to a degree appropriate for the building and its use, the ground and the surrounding site conditions. (See Note A-4.2.2.1.(1) .) | obc2019_divb | Div B | 4.2.2.1.(1) | 4.2.2.1. Subsurface Investigation | A subsurface investigation, including groundwater conditions, shall be carried out, by or under the direction of a person having knowledge and experience in planning and executing such investigations to a degree appropriate for the building and its use, the ground and the surrounding site conditions. (See Appendix A.) | Common Sentence
2015 | ON | NBC | Div B | 4.2.2.1.(1) | Subsurface Investigation | A subsurface investigation, including groundwater conditions, shall be carried out, by or under the direction of a professional engineer having knowledge and experience in planning and executing such investigations to a degree appropriate for the building and its use, the ground and the surrounding site conditions. (See Note A-4.2.2.1.(1).) | obc2019_divb | Div B | 4.2.2.1.(1) | 4.2.2.1. Subsurface Investigation | A subsurface investigation, including groundwater conditions, shall be carried out, by or under the direction of a person having knowledge and experience in planning and executing such investigations to a degree appropriate for the building and its use, the ground and the surrounding site conditions. | Common Sentence
2015 | ON | NBC | Div B | 4.2.2.3.(1) | Field Review | A field review shall be carried out by the designer or by another suitably qualified person to ascertain that the subsurface conditions are consistent with the design and that construction is carried out in accordance with the design and good engineering practice. (See Note A-4.2.2.3.(1).) | obc2019_divb | Div B | 4.2.2.2.(1) | 4.2.2.2. Field Review | A field review shall be carried out by the designer or by another suitably qualified person to ascertain that the subsurface conditions are consistent with the design and that construction is carried out in accordance with the design and good engineering practice. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.2.3.(2) | Field Review | The review required by Sentence (1) shall be carried out (a) on a continuous basis (i) during the construction of all deep foundation units with all pertinent information recorded for each foundation unit, (ii) during the installation and removal of retaining structures and related backfilling operations, and (iii) during the placement of engineered fills that are to be used to support the foundation units, and (b) as required, unless otherwise directed by the authority having jurisdiction, (i) in the construction of all shallow foundation units, and (ii) in excavating, dewatering and other related works. | obc2019_divb | Div B | 4.2.2.2.(2) | 4.2.2.2. Field Review | The review required in Sentence (1) shall be carried out, (a) on a continuous basis, (i) during the construction of all deep foundation units with all pertinent information recorded for each foundation unit, (ii) during the installation and removal of retaining structures and related backfilling operations, and (iii) during the placement of engineered fills that are to be used to support the foundation units, and (b) as required, unless otherwise directed by the chief building official, (i) in the construction of all shallow foundation units, and (ii) in excavating, dewatering and other related works. | Common Sentence
2015 | ON | NBC | Div B | 4.2.2.4.(1) | Altered Subsurface Condition | If during construction, the soil, rock or groundwater is found not to be of the type or in the condition used in design and as indicated on the drawings, the design shall be reassessed by the designer. | obc2019_divb | Div B | 4.2.2.3.(1) | 4.2.2.3. Altered Subsurface Condition | If during construction, the soil, rock or groundwater is found not to be of the type or in the condition used in design, and as indicated on the drawings, the design shall be reassessed by the designer. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.2.4.(2) | Altered Subsurface Condition | If, during construction, climatic or any other conditions change the properties of the soil, rock or groundwater, the design shall be reassessed by the designer. | obc2019_divb | Div B | 4.2.2.3.(2) | 4.2.2.3. Altered Subsurface Condition | If during construction, climatic or any other conditions have changed the properties of the soil, rock or groundwater, the design shall be reassessed by the designer. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.3.1.(1) | Wood | Wood used in foundations or in support of soil or rock shall conform with the appropriate requirements of Subsection 4.3.1. | obc2019_divb | Div B | 4.2.3.1.(1) | 4.2.3.1. Wood | Wood used in foundations or in support of soil or rock shall conform to the appropriate requirements of Subsection 4.3.1. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.3.10.(1) | Corrosion of Steel | Where conditions are corrosive to steel, adequate protection of exposed steel shall be provided. (See Article 1.2.1.1. of Division A for use of other materials.) | obc2019_divb | Div B | 4.2.3.10.(1) | 4.2.3.10. Corrosion of Steel | Where conditions are corrosive to steel, adequate protection of exposed steel shall be provided. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.3.2.(1) | Preservation Treatment of Wood | Wood exposed to soil or air above the lowest anticipated groundwater table shall be treated with preservative in conformance with CAN/CSA-O80 Series, "Wood Preservation", and the requirements of the appropriate commodity standard as follows: (a) CAN/CSA-O80.2, "Processing and Treatment" (b) CAN/CSA-O80.3, "Preservative Formulations", or (c) CSA O80.15, "Preservative Treatment of Wood for Building Foundation Systems, Basements, and Crawl Spaces by Pressure Processes". | obc2019_divb | Div B | 4.2.3.2.(1) | 4.2.3.2. Preservation Treatment of Wood | Wood exposed to soil or air above the lowest anticipated groundwater table shall be treated with preservative in conformance with CAN/CSA-O80 Series, "Wood Preservation", and the requirements of the appropriate commodity standard as follows: (a) CAN/CSA-O80.2, "Processing and Treatment", (b) CAN/CSA-O80.3, "Preservative Formulations", or (c) CSA O80.15, “Preservative Treatment of Wood for Building Foundation Systems, Basements, and Crawl Spaces by Pressure Processes”. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.3.3.(1) | Plain and Reinforced Masonry | Plain or reinforced masonry used in foundations or in support of soil or rock shall conform to the requirements of Subsection 4.3.2. | obc2019_divb | Div B | 4.2.3.3.(1) | 4.2.3.3. Plain and Reinforced Masonry | Plain or reinforced masonry used in foundations or in support of soil or rock shall conform to the requirements of Subsection 4.3.2. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.3.4.(1) | Prevention of Deterioration of Masonry | Where plain or reinforced masonry in foundations or in structures supporting soil or rock may be subject to conditions conducive to deterioration, protection shall be provided to prevent such deterioration. | obc2019_divb | Div B | 4.2.3.4.(1) | 4.2.3.4. Prevention of Deterioration of Masonry | Where plain or reinforced masonry in foundations or in structures supporting soil or rock may be subject to conditions conducive to deterioration, protection shall be provided to prevent such deterioration. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.3.5.(1) | Concrete | Plain, reinforced or prestressed concrete used in foundations or in support of soil or rock shall conform to the requirements of Subsection 4.3.3. | obc2019_divb | Div B | 4.2.3.5.(1) | 4.2.3.5. Concrete | Plain, reinforced or prestressed concrete used in foundations or in support of soil or rock shall conform to the requirements of Subsection 4.3.3. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.3.6.(1) | Protection Against Chemical Attack | Where concrete in foundations may be subject to chemical attack, it shall be treated in conformance with the requirements in CSA A23.1, "Concrete Materials and Methods of Concrete Construction". | obc2019_divb | Div B | 4.2.3.6.(1) | 4.2.3.6. Protection Against Chemical Attack | Where concrete in foundations may be subject to chemical attack, it shall be treated in conformance with the requirements in CSA A23.1, "Concrete Materials and Methods of Concrete Construction". | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.3.7.(1) | Steel | Steel used in foundations or in support of soil or rock shall conform with the appropriate requirements of Subsection 4.3.3. or 4.3.4., unless otherwise specified in this Section. | obc2019_divb | Div B | 4.2.3.7.(1) | 4.2.3.7. Steel | Steel used in foundations or in support of soil or rock shall conform with the appropriate requirements of Subsections 4.3.3. or 4.3.4., unless otherwise specified in this Section. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.3.8.(1) | Steel Piles | Where steel piles are used in deep foundations and act as permanent load-carrying members, the steel shall conform with one of the following standards: (a) ASTM A252, "Welded and Seamless Steel Pipe Piles,"( b) ASTM A283 / A283M, "Low and Intermediate Tensile Strength Carbon Steel Plates," (c) ASTM A1008 / A1008M , "Steel, Sheet, Cold-Rolled, Carbon, Structural, High-Strength Low-Alloy, and High-Strength Low-Alloy with Improved Formability, Solution Hardened, and Bake Hardenable," (d) ASTM A1011 / A1011M, "Steel, Sheet and Strip, Hot-Rolled, Carbon, Structural, High-Strength Low-Alloy, High-Strength Low-Alloy with Improved Formability, and Ultra-High Strength", or (e) CSA G40.21, "Structural Quality Steel". | obc2019_divb | Div B | 4.2.3.8.(1) | 4.2.3.8. Steel Piles | Where steel piles are used in deep foundations and act as permanent load-carrying members, the steel shall conform with one of the following standards: (a) ASTM A252, "Welded and Seamless Steel Pipe Piles", (b) ASTM A283 / A283M, "Low and Intermediate Tensile Strength Carbon Steel Plates", (c) ASTM A1008 / A1008M , "Steel, Sheet, Cold-Rolled, Carbon, Structural, High-Strength Low-Alloy, and High-Strength Low-Alloy with Improved Formability, Solution Hardened, and Bake Hardenable", (d) ASTM A1011 / A1011M, "Steel, Sheet and Strip, Hot-Rolled, Carbon, Structural, High-Strength Low-Alloy, High-Strength Low-Alloy with Improved Formability, and Ultra-High Strength", or (e) CSA G40.21, "Structural Quality Steel". | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.3.9.(1) | High Strength Steel Tendons | Where high strength steel is used for tendons in anchor systems used for the permanent support of a foundation or in the erection of temporary support of soil or rock adjacent to an excavation, it shall conform with the requirements of CSA A23.1, "Concrete Materials and Methods of Concrete Construction". | obc2019_divb | Div B | 4.2.3.9.(1) | 4.2.3.9. High Strength Steel Tendons | Where high strength steel is used for tendons in anchor systems used for the permanent support of a foundation or in the erection of temporary support of soil or rock adjacent to an excavation, it shall conform with the requirements of CSA A23.1, "Concrete Materials and Methods of Concrete Construction". | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.4.1.(1) | Design Basis | The design of foundations, excavations and soil- and rock-retaining structures shall be based on a subsurface investigation carried out in conformance with the requirements of this Section, and on any of the following, as appropriate: (a) application of generally accepted geotechnical and civil engineering principles by a professional engineer especially qualified in this field of work, as provided in this Section and other Sections of Part 4, (b) established local practice, where such practice includes successful experience both with soils and rocks of similar type and condition and with a foundation or excavation of similar type, construction method, size and depth, or (c) in situ testing of foundation units, such as the load testing of piles, anchors or footings, carried out by a person competent in this field of work. (See Note A-4.2.4.1.(1).) | obc2019_divb | Div B | 4.2.4.1.(1) | 4.2.4.1. Design Basis | The design of foundations, excavations and soil- and rock-retaining structures shall be based on a subsurface investigation carried out by a person competent in this field of work, and on any of the following: (a) application of generally accepted geotechnical and civil engineering principles by a person especially qualified in this field of work as provided in this Section and other Sections of this Part, (b) established local practice where such practice includes successful experience both with soils and rocks of similar type and condition and with a foundation or excavation of similar type, construction method, size and depth, or (c) in situ testing of foundation units such as the load testing of piles, anchors or footings carried out by a person competent in this field of work. | Common Sentence
2015 | ON | NBC | Div B | 4.2.4.1.(2) | Design Basis | The foundations of a building shall be capable of resisting all the loads stipulated in Section 4.1., in accordance with limit states design in Subsection 4.1.3. | obc2019_divb | Div B | 4.2.4.1.(2) | 4.2.4.1. Design Basis | The foundations of a building shall be capable of resisting all the loads stipulated in Section 4.1., in accordance with limit states design in Subsection 4.1.3. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.4.1.(3) | Design Basis | For the purpose of the application of the load combinations given in Table 4.1.3.2.-A, the geotechnical components of loads and the factored geotechnical resistances at ULS shall be determined by a suitably qualified and experienced professional engineer. (See Note A-4.2.4.1.(3).) | obc2019_divb | Div B | 4.2.4.1.(3) | 4.2.4.1. Design Basis | For the purpose of the application of the load combinations given in Table 4.1.3.2.A., the geotechnical components of loads and the factored geotechnical resistances at ULS shall be determined by a suitably qualified and experienced person. (See Appendix A.) | Common Sentence
2015 | ON | NBC | Div B | 4.2.4.1.(4) | Design Basis | Geotechnical components of service loads and geotechnical reactions for SLS shall be determined by a suitably qualified and experienced professional engineer. | obc2019_divb | Div B | 4.2.4.1.(4) | 4.2.4.1. Design Basis | Geotechnical components of service loads and geotechnical reactions for SLS shall be determined by a suitably qualified and experienced person. | Common Sentence
2015 | ON | NBC | Div B | 4.2.4.1.(5) | Design Basis | The foundation of a building shall be designed to satisfy SLS requirements within the limits that the building is designed to accommodate, including total settlement and differential settlement, heave, lateral movement, tilt or rotation. (See Note A-4.2.4.1.(5).) | obc2019_divb | Div B | 4.2.4.1.(5) | 4.2.4.1. Design Basis | The foundation of a building shall be designed to satisfy SLS requirements within the limits that the building is designed to accommodate, including total settlement and differential settlement, heave, lateral movement, tilt or rotation. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.4.1.(6) | Design Basis | Communication, interaction and coordination between the designer and the professional engineer responsible for the geotechnical aspects of the project shall take place to a degree commensurate with the complexity and requirements of the project. | obc2019_divb | Div B | 4.2.4.1.(6) | 4.2.4.1. Design Basis | Communication, interaction and coordination between the designer and the person responsible for the geotechnical aspects of the project shall take place to a degree commensurate with the complexity and requirements of the project. | Common Sentence
2015 | ON | NBC | Div B | 4.2.4.10.(1) | Permafrost | Where conditions of permafrost are encountered or proven to exist, the design of the foundation shall be based upon analysis of these conditions by a person especially qualified in that field of work. | obc2019_divb | Div B | 4.2.4.10.(1) | 4.2.4.10. Permafrost | Where conditions of permafrost are encountered or proven to exist, the design of the foundation shall be based upon analysis of these conditions by a person especially qualified in that field of work. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.4.11.(1) | Swelling and Shrinking Soils | Where swelling or shrinking soils, in which movements resulting from moisture content changes may be sufficient to cause damage to a structure, are encountered or known to exist, such a condition shall be fully investigated and provided for in the design. | obc2019_divb | Div B | 4.2.4.11.(1) | 4.2.4.11. Swelling and Shrinking Soils | Where swelling or shrinking soils, in which movements resulting from moisture content changes may be sufficient to cause damage to a structure, are encountered or known to exist, such a condition shall be fully investigated and provided for in the design. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.4.12.(1) | Expanding and Deteriorating Rock | Where rock that expands or deteriorates when subjected to unfavourable environmental conditions or to stress release is known to exist, this condition shall be fully investigated and provided for in the design. | obc2019_divb | Div B | 4.2.4.12.(1) | 4.2.4.12. Expanding and Deteriorating Rock | Where rock that expands or deteriorates when subjected to unfavourable environmental conditions or to stress release is known to exist, this condition shall be fully investigated and provided for in the design. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.4.13.(1) | Construction on Fill | Buildings may be placed on fill if it can be shown by subsurface investigation that (a) the fill is or can be made capable of safely supporting the building, (b) detrimental movement of the building or services leading to the building will not occur, and (c) explosive gases can be controlled or do not exist. | obc2019_divb | Div B | 4.2.4.13.(1) | 4.2.4.13. Construction on Fill | Buildings may be placed on fill if it can be shown by subsurface investigation that, (a) the fill is or can be made capable of safely supporting the building, (b) detrimental movement of the building or services leading to the building will not occur, and (c) explosive gases can be controlled or do not exist. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.4.14.(1) | Structural Design | The structural design of the foundation of a building, the procedures and construction practices shall conform with the appropriate Sections of this Code unless otherwise specified in this Section. | obc2019_divb | Div B | 4.2.4.14.(1) | 4.2.4.14. Structural Design | The structural design of the foundation of a building, the procedures and construction practices shall conform with the appropriate Sections of this Code unless otherwise specified in this Section. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.4.2.(1) | Subsurface Investigation | A subsurface investigation shall be carried out to the depth and extent to which the building or excavation will significantly change the stress in the soil or rock, or to such a depth and extent as to provide all the necessary information for the design and construction of the excavation or the foundations. | obc2019_divb | Div B | 4.2.4.2.(1) | 4.2.4.2. Subsurface Investigation | A subsurface investigation shall be carried out to the depth and extent to which the building or excavation will significantly change the stress in the soil or rock, or to such a depth and extent as to provide all the necessary information for the design and construction of the excavation or the foundations. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.4.3.(1) | Identification | The identification and classification of soil, rock and groundwater and descriptions of their engineering and physical properties shall be in accordance with a widely accepted system. | obc2019_divb | Div B | 4.2.4.3.(1) | 4.2.4.3. Identification | The identification and classification of soil, rock and groundwater and descriptions of their engineering and physical properties shall be in accordance with a widely accepted system. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.4.4.(1) | Depth of Foundations | Except as permitted in Sentence 4.2.4.4.(2), the bearing surface of a foundation shall be below the level of potential damage, including damage resulting from frost action, and the foundation shall be designed to prevent damage resulting from adfreezing and frost jacking. (See Note A-4.2.4.4.(1) .) | obc2019_divb | Div B | 4.2.4.4.(1) | 4.2.4.4. Depth of Foundations | Except as permitted in Sentence (2), the bearing surface of a foundation shall be below the level of potential damage, including damage resulting from frost action, and the foundation shall be designed to prevent damage resulting from adfreezing and frost jacking. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.4.4.(2) | Depth of Foundations | The bearing surface of a foundation need not be below the level of potential damage from frost where the foundation a) is designed against frost action, or b) overlies material not susceptible to frost action. | obc2019_divb | Div B | 4.2.4.4.(2) | 4.2.4.4. Depth of Foundations | The bearing surface of a foundation need not be below the level of potential damage from frost where the foundation, (a) is designed against frost action, or (b) overlies material not susceptible to frost action. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.4.5.(1) | Sloping Ground | Where a foundation is to rest on, in or near sloping ground, this particular condition shall be provided for in the design. | obc2019_divb | Div B | 4.2.4.5.(1) | 4.2.4.5. Sloping Ground | Where a foundation is to rest on, in or near sloping ground, this particular condition shall be provided for in the design. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.4.6.(1) | Eccentric and Inclined Loads | Where there is eccentricity or inclination of loading in foundation units, this effect shall be fully investigated and provided for in the design. | obc2019_divb | Div B | 4.2.4.6.(1) | 4.2.4.6. Eccentric and Inclined Loads | Where there is eccentricity or inclination of loading in foundation units, this effect shall be fully investigated and provided for in the design. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.4.7.(1) | Dynamic Loading | Where dynamic loading conditions apply, the effects shall be assessed by a special investigation of these conditions and provided for in the design. | obc2019_divb | Div B | 4.2.4.7.(1) | 4.2.4.7. Dynamic Loading | Where dynamic loading conditions apply, the effects shall be assessed by a special investigation of these conditions and provided for in the design. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.4.8.(1) | Hydrostatic Uplift | Where a foundation or any part of a building is subject to hydrostatic uplift, the effects shall be provided for in the design. | obc2019_divb | Div B | 4.2.4.8.(1) | 4.2.4.8. Hydrostatic Uplift | Where a foundation or any part of a building is subject to hydrostatic uplift the effects shall be provided for in the design. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.4.9.(1) | Groundwater Level Change | Where proposed construction will result in a temporary or permanent change in the groundwater level, the effects of this change on adjacent buildings shall be fully investigated and provided for in the design. | obc2019_divb | Div B | 4.2.4.9.(1) | 4.2.4.9. Groundwater Level Change | Where proposed construction will result in a temporary or permanent change in the groundwater level, the effects of this change on adjacent buildings shall be fully investigated and provided for in the design. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.5.1.(1) | Design of Excavations | The design of excavations and of supports for the sides of excavations shall conform with Subsection 4.2.4. and with this Subsection. (See Note A-4.2.5.1.(1) .) | obc2019_divb | Div B | 4.2.5.1.(1) | 4.2.5.1. Design of Excavations | The design of excavations and of supports for the sides of excavations shall conform to the requirements of Subsection 4.2.4. and this Subsection. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.5.2.(1) | Excavation Construction | Every excavation shall be undertaken in such a manner as to (a) prevent movement that would cause damage to adjacent buildings at all phases of construction, and (b) comply with the appropriate requirements of Part 8. | obc2019_divb | Div B | 4.2.5.2.(1) | 4.2.5.2. Excavation Construction | Every excavation shall be undertaken in such a manner as to prevent movement that would cause damage to adjacent buildings at all phases of construction. | Common Sentence | Yes | Excavation
2015 | ON | NBC | Div B | 4.2.5.2.(2) | Excavation Construction | Material shall not be placed nor shall equipment be operated or placed in or adjacent to an excavation in a manner that may endanger the integrity of the excavation or its supports. | obc2019_divb | Div B | 4.2.5.2.(2) | 4.2.5.2. Excavation Construction | Material shall not be placed nor shall equipment be operated or placed in or adjacent to an excavation in a manner that may endanger the integrity of the excavation or its supports. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.5.3.(1) | Supported Excavations | The sides of an excavation in soil or rock shall be supported by a retaining structure conforming with the requirements of Articles 4.2.5.1. and 4.2.5.2., except as permitted in Article 4.2.5.4. | obc2019_divb | Div B | 4.2.5.3.(1) | 4.2.5.3. Supported Excavations | The sides of an excavation in soil or rock shall be supported by a retaining structure conforming with the requirements of Articles 4.2.5.1. and 4.2.5.2., except as permitted in Article 4.2.5.4. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.5.4.(1) | Unsupported Excavations | The sides of an excavation in soil or rock may be unsupported where a design is prepared in conformance with the requirements of Articles 4.2.5.1. and Article 4.2.5.2. | obc2019_divb | Div B | 4.2.5.4.(1) | 4.2.5.4. Unsupported Excavations | The sides of an excavation in soil or rock may be unsupported where a design is prepared by a person especially qualified in this field of work in conformance with the requirements of Articles 4.2.5.1. and 4.2.5.2. | Common Sentence | Yes | Excavation
2015 | ON | NBC | Div B | 4.2.5.5.(1) | Control of Water Around Excavations | Surface water, all groundwater, perched groundwater and in particular artesian groundwater shall be kept under control at all phases of excavation and construction. | obc2019_divb | Div B | 4.2.5.5.(1) | 4.2.5.5. Control of Water Around Excavations | Surface water, all groundwater, perched groundwater and in particular artesian groundwater shall be kept under control at all phases of excavation and construction. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.5.6.(1) | Loss of Ground | At all phases of excavation and construction, loss of ground due to water or any other cause shall be prevented | obc2019_divb | Div B | 4.2.5.6.(1) | 4.2.5.6. Loss of Ground | At all phases of excavation and construction, loss of ground due to water or any other cause shall be prevented | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.5.7.(1) | Protection and Maintenance at Excavations | All sides of an excavation, supported and unsupported, shall be continuously maintained and protected from possible deterioration by construction activity or by the action of frost, rain and wind. | obc2019_divb | Div B | 4.2.5.7.(1) | 4.2.5.7. Protection and Maintenance at Excavations | All sides of an excavation, supported and unsupported, shall be continuously maintained and protected from possible deterioration by construction activity or by the action of frost, rain and wind. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.5.8.(1) | Backfilling | Where an excavation is backfilled, the backfill shall be placed so as to (a) provide lateral support to the soil adjacent to the excavation, and (b) prevent detrimental movements. | obc2019_divb | Div B | 4.2.5.8.(1) | 4.2.5.8. Backfilling | Where an excavation is backfilled, the backfill shall be placed so as to, (a) provide lateral support to the soil adjacent to the excavation, and (b) prevent detrimental movements. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.5.8.(2) | Backfilling | The material used as backfill or fill supporting a footing, foundation or a floor on grade shall be of a type that is not subject to detrimental volume change with changes in moisture content and temperature. | obc2019_divb | Div B | 4.2.5.8.(2) | 4.2.5.8. Backfilling | The material used as backfill or fill supporting a footing, foundation or a floor on grade shall be of a type that is not subject to detrimental volume change with changes in moisture content and temperature. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.6.1.(1) | Design of Shallow Foundations | The design of shallow foundations shall be in conformance with Subsection 4.2.4. and the requirements of this Subsection. (See Note A-4.2.6.1.(1) .) | obc2019_divb | Div B | 4.2.6.1.(1) | 4.2.6.1. Design of Shallow Foundations | The design of shallow foundations shall be in conformance with the requirements of Subsection 4.2.4. and this Subsection. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.6.2.(1) | Support of Shallow Foundations | Where a shallow foundation is to be placed on soil or rock, the soil or rock shall be cleaned of loose and unsound material and shall be adequate to support the design load taking into account temperature, precipitation, construction activities and other factors that may lead to changes of the properties of soil or rock. | obc2019_divb | Div B | 4.2.6.2.(1) | 4.2.6.2. Support of Shallow Foundations | Where a shallow foundation is to be placed on soil or rock, the soil or rock shall be cleaned of loose and unsound material and shall be adequate to support the design load taking into account temperature, precipitation, construction activities and other factors that may lead to changes of the properties of soil or rock. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.6.3.(1) | Incorrect Placement of Shallow Foundations | Where a shallow foundation unit has not been placed or located as indicated on the drawings, (a) the error shall be corrected, or (b) the design of the foundation unit shall be recalculated for the altered conditions by the designer and action taken as required in Article 2.2.4.7. of Division C. | obc2019_divb | Div B | 4.2.6.3.(1) | 4.2.6.3. Incorrect Placement of Shallow Foundations | Where a shallow foundation unit has not been placed or located as indicated on the drawings, (a) the error shall be corrected, or (b) the design of the foundation unit shall be recalculated for the altered conditions by the designer. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.6.4.(1) | Damaged Shallow Foundations | If a shallow foundation unit is damaged, (a) it shall be repaired, or (b) the design of the foundation unit shall be recalculated for the damaged condition by the designer and action taken as required in Article 2.2.4.7. of Division C. | obc2019_divb | Div B | 4.2.6.4.(1) | 4.2.6.4. Damaged Shallow Foundations | Where a shallow foundation unit is damaged, (a) it shall be repaired, or (b) the design of the foundation unit shall be recalculated for the damaged condition by the designer. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.7.1.(1) | General | A deep foundation shall provide support for a building by transferring loads by end-bearing to a competent stratum at considerable depth below the structure, or by mobilizing resistance by adhesion or friction, or both, in the soil or rock in which it is placed. (See Note A-4.2.7.1.(1).) | obc2019_divb | Div B | 4.2.7.1.(1) | 4.2.7.1. General | A deep foundation unit shall provide support for a building by transferring loads by end-bearing to a competent stratum at considerable depth below the structure, or by mobilizing resistance by adhesion or friction, or both, in the soil or rock in which it is placed. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.7.2.(1) | Design of Deep Foundations | Deep foundation units shall be designed in conformance with Subsection 4.2.4. and this Subsection. (See Note A-4.2.7.2.(1) .) | obc2019_divb | Div B | 4.2.7.2.(1) | 4.2.7.2. Design for Deep Foundations | Deep foundation units shall be designed in conformance with Subsection 4.2.4. and this Subsection. (See Appendix‚ A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.7.2.(2) | Design of Deep Foundations | Where deep foundation units are load tested, as required in Clause 4.2.4.1.(1)(c), the determination of the number and type of load test and the interpretation of the results shall be carried out by by a professional engineer especially qualified in this field of work. (See Note A-4.2.7.2.(2).) | obc2019_divb | Div B | 4.2.7.2.(2) | 4.2.7.2. Design for Deep Foundations | Where deep foundation units are load tested, as required in Clause 4.2.4.1.(1)(c), the determination of the number and type of load test and the interpretation of the results shall be carried out by a person especially qualified in this field of work. (See Appendix A.) | Common Sentence
2015 | ON | NBC | Div B | 4.2.7.2.(3) | Design of Deep Foundations | The design of deep foundations shall be determined on the basis of geotechnical considerations taking into account (a) the method of installation, (b) the degree of inspection, (c) the spacing of foundation units and group effects, (d) other requirements of this Subsection, and (e) the appropriate structural requirements of Section 4.1. and Subsections 4.3.1., 4.3.3. and 4.3.4. | obc2019_divb | Div B | 4.2.7.2.(3) | 4.2.7.2. Design for Deep Foundations | The design of deep foundations shall be determined on the basis of geotechnical considerations taking into account, (a) the method of installation, (b) the degree of inspection, (c) the spacing of foundation units and group effects, (d) other requirements of this Subsection, and (e) the appropriate structural requirements of Section 4.1. and Subsections 4.3.1., 4.3.3. and 4.3.4. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.7.2.(4) | Design of Deep Foundations | The portion of a deep foundation unit permanently in contact with soil or rock shall be structurally designed as a laterally supported compression member. | obc2019_divb | Div B | 4.2.7.2.(4) | 4.2.7.2. Design for Deep Foundations | The portion of a deep foundation unit permanently in contact with soil or rock shall be structurally designed as a laterally supported compression member. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.7.2.(5) | Design of Deep Foundations | The portion of a deep foundation unit that is not permanently in contact with soil or rock shall be structurally designed as a laterally unsupported compression member. | obc2019_divb | Div B | 4.2.7.2.(5) | 4.2.7.2. Design for Deep Foundations | The portion of a deep foundation unit that is not permanently in contact with soil or rock shall be structurally designed as a laterally unsupported compression member. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.7.2.(6) | Design of Deep Foundations | The structural design of prefabricated deep foundation units shall allow for all stresses resulting from driving, handling and testing. | obc2019_divb | Div B | 4.2.7.2.(6) | 4.2.7.2. Design for Deep Foundations | The structural design of prefabricated deep foundation units shall allow for all stresses resulting from driving, handling and testing. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.7.3.(1) | Tolerance in Alignment and Location | Permissible deviations from the design alignment and the location of the top of deep foundation units shall be determined by design analysis and shall be indicated on the drawings. | obc2019_divb | Div B | 4.2.7.3.(1) | 4.2.7.3. Tolerance in Alignment and Location | Permissible deviations from the design alignment and the location of the top of deep foundation units shall be determined by design analysis and shall be indicated on the drawings. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.7.4.(1) | Incorrect Alignment and Location | Where a deep foundation unit has not been placed within the permissible deviations referred to in Article 4.2.7.3., the condition of the foundation shall be assessed by the designer, any necessary changes made and action taken as required in Article 2.2.4.7. of Division C. | obc2019_divb | Div B | 4.2.7.4.(1) | 4.2.7.4. Incorrect Alignment and Location | Where a deep foundation unit has not been placed within the permissible deviations referred to in Article 4.2.7.3., the condition of the foundation shall be assessed by the designer. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.7.5.(1) | Installation of Deep Foundations | Deep foundation units shall be installed in such a manner as not to impair (a) the strength of the deep foundation units and the properties of the soil or rock on or in which they are placed beyond the calculated or anticipated limits, (b) the integrity of previously installed deep foundation units, or (c) the integrity of neighbouring buildings. | obc2019_divb | Div B | 4.2.7.5.(1) | 4.2.7.5. Installation of Deep Foundations | Deep foundation units shall be installed in such a manner as not to impair, (a) the strength of the deep foundation units and the properties of the soil or rock on or in which they are placed beyond the calculated or anticipated limits, (b) the integrity of previously installed deep foundation units, or (c) the integrity of neighbouring buildings. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.7.6.(1) | Damaged Deep Foundation Units | Where inspection shows that a deep foundation unit is damaged or not consistent with design or good engineering practice, (a) such a unit shall be reassessed by the designer, and (b) any necessary changes shall be made and (c) action taken as required in Article 2.2.4.7. of Division C. | obc2019_divb | Div B | 4.2.7.6.(1) | 4.2.7.6. Damaged Deep Foundation Units | Where inspection shows that a deep foundation unit is damaged or not consistent with design or good engineering practice, (a) such a unit shall be reassessed by the designer, and (b) any necessary changes shall be made and action taken as required. | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.8.1.(1) | General | Where special foundation systems are used, such systems shall conform to Subsection 4.2.4., Sentence 4.1.1.5.(2) and Article 1.2.1.1. of Division A. | obc2019_divb | Div B | 4.2.8.1.(1) | 4.2.8.1. General | Where special foundation systems are used, such systems shall conform to Subsection 4.2.4. and Sentence 4.1.1.4.(2). | Common Sentence | No
2015 | ON | NBC | Div B | 4.2.8.2(1) | Use of Existing Foundations | Existing foundations may be used to support new or altered buildings provided they comply with all pertinent requirements of this Section. | obc2019_divb | Div B | 4.2.8.2.(1) | 4.2.8.2. Use of Existing Foundations | Existing foundations may be used to support new or altered buildings provided they comply with all pertinent requirements of this Section. | Common Sentence | No
2015 | ON | NBC | Div B | 4.3.1.1.(1) | Design Basis for Wood | Buildings and their structural members made of wood shall conform to CSA O86, "Engineering Design in Wood". | obc2019_divb | Div B | 4.3.1.1.(1) | 4.3.1.1. Design Basis for Wood | Buildings and their structural members made of wood shall conform to CSA O86, "Engineering Design in Wood". | Common Sentence | No
2015 | ON | NBC | Div B | 4.3.1.2.(1) | Glued-Laminated Members | Glued-laminated members shall be fabricated in plants conforming to CSA O177, "Qualification Code for Manufacturers of Structural Glued-Laminated Timber". | obc2019_divb | Div B | 4.3.1.2.(1) | 4.3.1.2. Glue-Laminated Members | Glued-laminated members shall be fabricated in plants conforming to CSA O177, "Qualification Code for Manufacturers of Structural Glued-Laminated Timber". | Common Sentence | No
2015 | ON | NBC | Div B | 4.3.1.3.(1) | Termites | In areas known to be infested by termites, the requirements in Articles 9.3.2.9., 9.12.1.1. and 9.15.5.1. shall apply. | obc2019_divb | Div B | 4.3.1.3.(1) | 4.3.1.3. Termites | In areas known to be infested by termites, the requirements in Articles 9.3.2.9., 9.12.1.1. and 9.15.5.1. shall apply. | Common Sentence | No
2015 | ON | NBC | Div B | 4.3.2.1.(1) | Design Basis for Plain and Reinforced Masonry | Buildings and their structural members made of plain and reinforced masonry shall conform to CSA S304, "Design of Masonry Structures". | obc2019_divb | Div B | 4.3.2.1.(1) | 4.3.2.1. Design Basis for Plain and Reinforced Masonry | Buildings and their structural members made of plain and reinforced masonry shall conform to CSA S304, "Design of Masonry Structures". | Common Sentence | No
2015 | ON | NBC | Div B | 4.3.3.1.(1) | Design Basis for Plain, Reinforced and Pre-stressed Concrete | Buildings and their structural members made of plain, reinforced and pre-stressed concrete shall conform to CSA A23.3 Design of Concrete Structures (See Note A-4.3.3.1.(1).) | obc2019_divb | Div B | 4.3.3.1.(1) | 4.3.3.1. Design Basis for Plain, Reinforced and Prestressed | Buildings and their structural members made of plain, reinforced or prestressed concrete shall conform to CSA A23.3, "Design of Concrete Structures". (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.3.4.1.(1) | Design Basis for Structural Steel | Buildings and their structural members made of structural steel shall conform to CSA S16 Design of Steel Structures (See Note A-4.3.4.1.(1).) | obc2019_divb | Div B | 4.3.4.1.(1) | 4.3.4.1. Design Basis for Structural Steel | Buildings and their structural members made of structural steel shall conform to CSA S16, "Design of Steel Structures". (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.3.4.2.(1) | Design Basis for Cold-Formed Steel | Buildings and their structural members made of cold-formed steel shall conform to CSA S136, "North American Specification for the Design of Cold-Formed Steel Structural Members (using the Appendix B provisions applicable to Canada)." (See Note A-4.3.4.2.(1) .) | obc2019_divb | Div B | 4.3.4.2.(1) | 4.3.4.2. Design Basis for Cold-Formed Steel | Buildings and their structural members made of cold-formed steel shall conform to CSA S136, "North American Specification for the Design of Cold-Formed Steel Structural Members". (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.3.4.3.(1) | Steel Building Systems | Steel building systems shall be manufactured by companies certified in accordance with the requirements of CSA A660 "Certification of Manufacturers of Steel Building Systems". | obc2019_divb | Div B | 4.3.4.3.(1) | 4.3.4.3. Steel Building Systems | Steel building systems shall be manufactured by companies certified in accordance with the requirements of CSA A660, "Certification of Manufacturers of Steel Building Systems". | Common Sentence | No
2015 | ON | NBC | Div B | 4.3.5.1.(1) | Design Basis for Aluminum | Buildings and their structural members made of aluminum shall conform to CAN/CSA-S157 / S157.1, "Strength Design in Aluminum/Commentary on CSA S157-05, Strength Design in Aluminum", using the loads stipulated in Section 4.1., in accordance with limit states design in Subsection 4.1.3. | obc2019_divb | Div B | 4.3.5.1.(1) | 4.3.5.1. Design Basis for Aluminum | Buildings and their structural members made of aluminum shall conform to CAN/CSA-S157 / S157.1, "Strength Design in Aluminum/Commentary on CSA S157-05, Strength Design in Aluminum", using the loads stipulated in Section 4.1., in accordance with limit states design in Subsection 4.1.3. | Common Sentence | No
2015 | ON | NBC | Div B | 4.3.6.1.(1) | Design Basis for Glass | Glass used in buildings shall be designed in conformance with a) CAN/CGSB-12.20-M, "Structural Design of Glass for Buildings", using an adjustment factor on the wind load, W, of not less than 0.75, or b) ASTM E1300, "Determining Load Resistance of Glass in Buildings", using an adjustment factor on the wind load, W, of not less than 1.0. (See Note A-4.3.6.1.(1).) | obc2019_divb | Div B | 4.3.6.1.(1) | 4.3.6.1. Design Basis for Glass | Glass used in buildings shall be designed in conformance with, (a) CAN/CGSB-12.20-M, "Structural Design of Glass for Buildings", using an adjustment factor on the wind load, W, of not less than 0.75, or (b) ASTM E1300, "Determining Load Resistance of Glass in Buildings", using an adjustment factor on the wind load, W, of not less than 1.0. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 4.4.1.1.(1) | Design Basis for Air-Supported Structures | The structural design of air-supported structures shall conform to CSA S367, "Air-, Cable-, and Frame-Supported Membrane Structures" using the loads stipulated in Section 4.1., in accordance with limit states design in Subsection 4.1.3. | obc2019_divb | Div B | 4.4.1.1.(1) | 4.4.1.1. Design Basis for Air-Supported Structures | The structural design of air-supported structures shall conform to CSA S367, "Air-, Cable-, and Frame-Supported Membrane Structures" using the loads stipulated in Section 4.1., in accordance with limit states design in Subsection 4.1.3. | Common Sentence | No
2015 | ON | NBC | Div B | 4.4.2.1.(1) | Design Basis for Parking Structures and Repair Garages | Parking structures and repair garages shall be designed in conformance with CSA S413 "Parking Structures". (See Note A-4.4.2.1.(1).) | obc2019_divb | Div B | 4.4.2.1.(1) | 4.4.2.1. Design Basis for Parking Structures and Repair Garages | Storage garages and repair garages shall be designed in conformance with CSA S413, "Parking Structures". | Common Sentence | No
2015 | ON | NBC | Div B | 5.1.2.1.(1) | 5.1.2.1 Exposure to Exterior Space or the Ground and Separation of Dissimilar Environments | This Part applies, as described in part 1., to (a) building materials, components and assemblies exposed to exterior space or the ground, including those separating interior space from exterior space or separating interior space from the ground, (b) building materials, components and assemblies separating environmentally dissimilar interior spaces (see Note A-5.8.), and (c) site materials, components, assemblies and grading that may affect environmental loads on building materials, components and assemblies exposed to exterior space or the ground. (see Note A-5.1.2.1.(1).) | obc2019_divb | Div B | 5.1.2.1.(1) | 5.1.2.1. Exposure to Exterior Space or the Ground and Separation of Dissimilar Environments | This Part applies to, (a) building materials, components and assemblies exposed to exterior space or the ground, including those separating interior space from exterior space or separating interior space from the ground, (b) building materials, components and assemblies separating environmentally dissimilar interior spaces, and (See Appendix Note A-5.8.) (c) site materials, components, assemblies and grading that may affect environmental loads on building materials, components and assemblies exposed to exterior space or the ground. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 5.1.4.1(3) | 5.1.4.1. Structural and Environmental Loads | Compliance with Clause (1)(a) shall be demonstrated by design complying with Subsection 5.2.1.and construction conforming to that design. |  | Div B | 5.1.4.1(2) | 5.1.4.1. Structural and Environmental Loads | The design and construction required by Clause (1)(a) shall comply with Subsection 5.2.1. | Common Sentence | No
2015 | ON | NBC | Div B | 5.1.4.1.(1) | 5.1.4.1 Structural and Environmental Loads | Building materials, components and assemblies that separate dissimilar environments or are exposed to the exterior shall have sufficient capacity and integrity to resist or accommodate all environmental loads, and effects of those loads, that may reasonably be expected having regard to the intended use of the building, and the environment to which the materials, components and assemblies are subject, and all structural loads, and effects of those loads, that may reasonably be expected. | obc2019_divb | Div B | 5.1.4.1.(1) | 5.1.4.1. Structural and Environmental Loads | Building materials, components and assemblies that separate dissimilar environments or are exposed to the exterior shall be designed and constructed to provide sufficient capacity and integrity to resist or accommodate,(a) all environmental loads, and effects of those loads, that may reasonably be expected having regard to, (i) the intended use of the building, and (ii) the environment to which the materials, components and assemblies are subject, and (b) all structural loads, and effects of those loads, that may be reasonably expected. | Common Sentence | No
2015 | ON | NBC | Div B | 5.1.4.1.(4) | 5.1.4.1. Structural and Environmental Loads | Compliance with Clause 5.1.4.1.(1)(b) shall be demonstrated by design complying with Subsection 5.2.2, and construction conforming to that design, with regard to (a) materials, components and assemblies, and associated loads, that are identified in Part 4, (b) air pressure loads imposed on air barrier systems, (c) wind up-lift imposed on roofing, and (d) hydrostatic pressure imposed on the means of protection from moisture in the ground. | obc2019_divb | Div B | 5.1.4.1.(3) | 5.1.4.1. Structural and Environmental Loads | The design and construction required by Clause (1)(b) shall comply with Subsection 5.2.2., with regard to, (a) materials, components and assemblies, and associated loads, that are identified in Part 4, (b) air pressure loads imposed on air barrier systems, (c) wind up-lift imposed on roofing, and (d) hydrostatic pressure imposed on the means of protection from moisture in the ground. | Common Sentence | No
2015 | ON | NBC | Div B | 5.1.4.1.(5) | 5.1.4.1. Structural and Environmental Loads | For materials, components, assemblies and loads to which Sentence 5.1.4.1.(4) does not apply, compliance with Sentence 5.1.4.1.(1) shall be demonstrated by design complying with part 5. for individual applicable loads and construction conforming to that design, or in the case of common materials, components and assemblies, and their installation, by proven past performance over a period of several years for individual applicable loads. | obc2019_divb | Div B | 5.1.4.1.(4) | 5.1.4.1 Structural and Environmental Loads | For materials, components, assemblies and loads to which Sentence (3) does not apply, the design and construction required by Clause (1)(b) shall,(a) comply with Subsection 5.2.2. for individual applicable loads, or (b) in the case of common materials, components and assemblies, and their installation, be based on proven past performance over a period of several years for individual applicable loads. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 5.1.4.1.(6) | 5.1.4.1. Structural and Environmental Loads | Materials, components and assemblies separating dissimilar environments and assemblies exposed to the exterior, including their connections, that are subject to structural loads as defined in Article 5.2.2.1. shall (a) transfer such loads to the building structure without adverse effects on the performance of other materials, components or assemblies, (b) not deflect to a degree that adversely affects the performance of other materials, components or assemblies (see Note A-5.1.4.1.(6)(b)), and (c) be designed, and constructed according to that design, to accommodate (see Note A-5.1.4.1.(6)(b) and (c)) (i) the maximum relative structural movement that may reasonably be expected, and (ii) construction tolerances that may be reasonably expected. | obc2019_divb | Div B | 5.1.4.1.(5) | 5.1.4.1 Structural and Environmental Loads | Materials, components and assemblies separating dissimilar environments and assemblies exposed to the exterior, including their connections, that are subject to structural loads referred to in Article 5.2.2.1., shall,(a) transfer such loads to the building structure without adverse effects on the performance of other materials, components or assemblies, (b) not deflect to a degree that adversely affects the performance of other materials, components or assemblies, and (See Appendix A.) (c) be designed, and constructed according to that design, to accommodate, (i) the maximum relative structural movement that may reasonably be expected, and (ii) construction tolerances that may reasonably be expected. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 5.1.4.2.(1) | 5.1.4.2. Resistance to Deterioration | Except as provided in Sentence 5.1.4.2.(2), materials used in building components and assemblies that separate dissimilar environments, or in assemblies exposed to the exterior, shall be (a) compatible with adjoining materials, and (b) resistant to any mechanisms of deterioration that may reasonably be expected, given (i) the nature and function of the materials, and (ii) the exposure and climatic conditions in which they will be installed. | obc2019_divb | Div B | 5.1.4.2.(1) | 5.1.4.2. Resistance to Deterioration | Except as provided in Sentence (2), materials used in building components and assemblies that separate dissimilar environments, or in assemblies exposed to the exterior, shall be,(a) compatible with adjoining materials, and (b) resistant to any mechanisms of deterioration that may reasonably be expected given, (i) the nature and function of the materials, (ii) the exposure of the materials, and (iii) the climatic conditions in which the materials will be installed. | Common Sentence | No
2015 | ON | NBC | Div B | 5.1.4.2.(2) | 5.1.4.2. Resistance to Deterioration | Material compatibility and deterioration resistance are not required where it can be shown that incompatibility or uncontrolled deterioration will not adversely affect any of the health or safety of building users, the intended use of the building, or the operation of building services. | obc2019_divb | Div B | 5.1.4.2.(2) | 5.1.4.2. Resistance to Deterioration | Material compatibility and deterioration resistance are not required where it can be shown that incompatibility or uncontrolled deterioration will not adversely affect any of,(a) the health or safety of building users, (b) the intended use of the building, or (c) the operation of building services. | Common Sentence | No
2015 | ON | NBC | Div B | 5.1.5.1.(1) | 5.1.5.1. Requirements in Other Parts of the Code | Structural and fire safety requirements in other Parts of the NBC shall apply. | obc2019_divb | Div B | 5.1.5.1.(1) | 5.1.5.1 Requirements in Other Parts of the Code | Structural and fire safety requirements in other Parts of the Code shall apply. | Common Sentence | No
2015 | ON | NBC | Div B | 5.2.1.1.(1) | 5.2.1.1 Exterior Environmental Loads | Above ground climatic loads shall be determined according to Subsection 1.1.3. | obc2019_divb | Div B | 5.2.1.1.(1) | 5.2.1.1. Exterior Environmental Loads | Above ground climatic loads shall be determined according to MMAH Supplementary Standard SB-1, "Climatic and Seismic Data". | Common Sentence | Yes | Environmental Loads
2015 | ON | NBC | Div B | 5.2.1.1.(2) | 5.2.1.1 Exterior Environmental Loads | Except as provided in Sentence 5.2.1.1.(3), below ground exterior environmental loads not described in Subsection 1.1.3. shall be determined from existing geological and hydrological data or from site tests. | obc2019_divb | Div B | 5.2.1.1.(2) | 5.2.1.1. Exterior Environmental Loads | Except as provided in Sentence (3), below ground exterior environmental loads not described in MMAH Supplementary Standard SB-1, "Climatic and Seismic Data", shall be determined from existing geological and hydrological data or from site tests. | Common Sentence | Yes | Environmental Loads
2015 | ON | NBC | Div B | 5.2.1.1.(3) | 5.2.1.1 Exterior Environmental Loads | Where local design and construction practice has shown soil temperature analysis to be unnecessary, soil temperatures need not be determined. (See Note A-5.2.1.1.(3) .) | obc2019_divb | Div B | 5.2.1.1.(3) | 5.2.1.1. Exterior Environmental Loads | Where local design and construction practice has shown soil temperature analysis to be unnecessary, soil temperatures need not be determined. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 5.2.1.2.(1) | 5.2.1.2 Interior Environmental Loads | Interior environmental loads shall be determined in accordance with good practice as described in Sentence 6.2.1.1.(1) based on the intended use of the space. (See Note A-5.2.1.2.(1).) | obc2019_divb | Div B | 5.2.1.2.(1) | 5.2.1.2. Interior Environmental Loads | Interior environmental loads shall be determined in accordance with good engineering practice as described in Sentence 6.2.1.1.(1) based on the intended use of the space. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 5.2.1.3.(1) | 5.2.1.3. Environmental Load and Transfer Calculations | Calculations related to the transfer of heat, air and moisture and the transmission of sound shall conform to good practice such as that described in the ASHRAE Handbooks. | obc2019_divb | Div B | 5.2.1.3.(1) | 5.2.1.3. Environmental Load and Transfer Calculations | Calculations related to the transfer of heat, air and moisture and the transmission of sound shall conform to good engineering practice such as that described in the ASHRAE Fundamentals Handbook. | Common Sentence | No
2015 | ON | NBC | Div B | 5.2.1.3.(3) | 5.2.1.3. Environmental Load and Transfer Calculations | Wind load calculations shall conform to part 4. | obc2019_divb | Div B | 5.2.1.3.(3) | 5.2.1.3. Environmental Load and Transfer Calculations | Wind load calculations shall conform to Subsection 4.1.7. | Common Sentence | No
2015 | ON | NBC | Div B | 5.2.2.1.(1) | 5.2.2.1. Determination of Structural Loads and Effects | Where materials, components or assemblies that separate dissimilar environments or are exposed to the exterior, or their connections, are required to be designed to withstand structural loads, these loads shall be determined in accordance with Part 4. (See also Subsection 2.2.5 of Division C) | obc2019_divb | Div B | 5.2.2.1.(1) | 5.2.2.1. Determination of Structural Loads and Effects | Where materials, components or assemblies that separate dissimilar environments or are exposed to the exterior, or their connections, are required to be designed for structural loads, these loads shall be determined in accordance with Part 4. | Common Sentence | No
2015 | ON | NBC | Div B | 5.2.2.1.(2) | 5.2.2.1. Determination of Structural Loads and Effects | Except as provided in Article 4.1.8.18., the structural loads referred to in Sentence 5.2.2.1.(1) and their related effects shall include dead loads transferred from structural elements, wind, snow, rain, hydrostatic and earth pressures, earthquake effects for post-disaster buildings, depending on their intended function (see Note A-5.2.2.1.(2)(c)), live loads due to use and occupancy, and loads due to thermal or moisture-related expansion and contraction, deflection, deformation, creep, shrinkage, settlement, and differential movement. | obc2019_divb | Div B | 5.2.2.1.(2) | 5.2.2.1. Determination of Structural Loads and Effects | Except as provided in Article 4.1.8.18., the structural loads referred to in Sentence (1) and their related effects shall include,(a) dead loads transferred from structural elements, (b) wind, snow, rain, hydrostatic and earth pressures, (c) earthquake effects for post-disaster buildings, depending on their intended function, (See Appendix A.) (d) live loads due to use and occupancy, and (e) loads due to thermal or moisture-related expansion and contraction, deflection, deformation, creep, shrinkage, settlement, and differential movement. | Common Sentence | No
2015 | ON | NBC | Div B | 5.2.2.1.(3) | 5.2.2.1 Determination of Structural Loads and Effects | Where materials, components or assemblies that separate dissimilar environments or are exposed to the exterior, or their connections, can be expected to be subject to loads or other effects not described in this Subsection or in Part 4, such loads or effects shall be taken into account in the design based on the most current and applicable information available. | obc2019_divb | Div B | 5.2.2.1.(3) | 5.2.2.1. Determination of Structural Loads and Effects | Where materials, components or assemblies that separate dissimilar environments or are exposed to the exterior, or their connections, can be expected to be subject to loads or other effects not otherwise described in this Subsection or in Part 4, such loads or other effects shall be taken into account in the design based on the most current and applicable information available. | Common Sentence | No
2015 | ON | NBC | Div B | 5.2.2.2.(1) | 5.2.2.2. Determination of Wind Load | This Article applies to the determination of wind load to be used in the design of materials, components and assemblies, including their connections, that separate dissimilar environments or are exposed to the exterior, where these are subject to wind load, and required to be designed to resist wind load. | obc2019_divb | Div B | 5.2.2.2.(1) | 5.2.2.2. Determination of Wind Load | This Article applies to the determination of wind load to be used in the design of materials, components and assemblies, including their connections, that separate dissimilar environments or are exposed to the exterior, where these are,(a) subject to wind load, and (b) required to be designed to resist wind load. | Common Sentence | No
2015 | ON | NBC | Div B | 5.2.2.2.(2) | 5.2.2.2. Determination of Wind Load | Except as provided in Sentence 5.2.2.2.(3), the wind load referred to in Sentence 5.2.2.2.(1) shall be 100% of the specified wind load determined in accordance with Article 4.1.7.1. | obc2019_divb | Div B | 5.2.2.2.(2) | 5.2.2.2. Determination of Wind Load | Except as provided in Sentence (3), the wind load referred to in Sentence (1) shall be 100% of the specified wind load determined in accordance with Article 4.1.7.1. | Common Sentence | No
2015 | ON | NBC | Div B | 5.2.2.2.(3) | 5.2.2.2. Determination of Wind Load | Where it can be shown by test or analysis that a material, component, assembly or connection referred to in Sentence 5.2.2.2.(1) will be subject to less than 100% of the specified wind load, the wind load referred to in Sentence 5.2.2.2.(1) shall be not less than the load determined by test or analysis. | obc2019_divb | Div B | 5.2.2.2.(3) | 5.2.2.2. Determination of Wind Load | Where it can be shown by test or analysis that a material, component, assembly or connection described in Sentence (1) will be subject to less than 100% of the specified wind load, the wind load referred to in Sentence (1) shall be not less than the load determined by test or analysis. | Common Sentence | No
2015 | ON | NBC | Div B | 5.2.2.2.(4) | 5.2.2.2. Determination of Wind Load | Except as provided in Sentence 5.2.2.2.(5), the wind uplift resistance of membrane roofing assemblies shall be determined in accordance with the requirements of CSA CAN/CSA-A123.21-10 Dynamic Wind Uplift Resistance of Membrane-Roofing Systems (See Note A-5.2.2.2.(4).) | obc2019_divb | Div B | 5.2.2.2.(4) | 5.2.2.2. Determination of Wind Load | Except as provided in Sentence (5), the wind uplift resistance of membrane roofing assemblies shall be determined in accordance with the requirements of CSA A123.21, "Dynamic Wind Uplift Resistance of Membrane-Roofing Systems". (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 5.2.2.2.(5) | 5.2.2.2. Determination of Wind Load | Membrane roofing assemblies with proven past performance for the anticipated wind loads need not comply with Sentence 5.2.2.2.(4). (See Note A-5.1.4.1.(5).) | obc2019_divb | Div B | 5.2.2.2.(5) | 5.2.2.2. Determination of Wind Load | Membrane roofing assemblies with proven past performance for the anticipated wind loads need not comply with Sentence (4). | Common Sentence | No
2015 | ON | NBC | Div B | 5.2.2.3.(1) | 5.2.2.3. Design Procedures | Structural design shall be carried out in accordance with part 4. and other applicable requirements in Part 4. | obc2019_divb | Div B | 5.2.2.3.(1) | 5.2.2.3. Design Procedures | Structural design shall be carried out in accordance with Subsection 4.1.3. and other applicable requirements in PartÃ‚ 4. | Common Sentence | No
2015 | ON | NBC | Div B | 5.3.1.1.(1) | 5.3.1.1. Required Resistance to Heat Transfer | Except as provided in Sentence 5.3.1.1.(2), where a building component or assembly will be subjected to an intended temperature differential, the component or assembly shall include materials to resist heat transfer or a means to dissipate transferred heat in accordance with the remainder of this Subsection. | obc2019_divb | Div B | 5.3.1.1.(1) | 5.3.1.1. Required Resistance to Heat Transfer | Except as provided in Sentence (2), where a building component or assembly will be subjected to an intended temperature differential, the component or assembly shall include materials to resist heat transfer or means to dissipate transferred heat in accordance with this Subsection. | Common Sentence | No
2015 | ON | NBC | Div B | 5.3.1.1.(2) | 5.3.1.1. Required Resistance to Heat Transfer | The installation of materials to resist heat transfer in accordance with the remainder of this Subsection is not required where it can be shown that uncontrolled heat transfer will not adversely affect any of the health or safety of building users, the intended use of the building, or the operation of building services. | obc2019_divb | Div B | 5.3.1.1.(2) | 5.3.1.1. Required Resistance to Heat Transfer | The installation of materials to resist heat transfer in accordance with this Subsection is not required where it can be shown that uncontrolled heat transfer will not adversely affect any of,(a) the health or safety of building users, (b) the intended use of the building, or (c) the operation of building services. | Common Sentence | No
2015 | ON | NBC | Div B | 5.3.1.2.(1) | 5.3.1.2. Properties to Resist Heat Transfer or Dissipate Heat | Taking into account the conditions on either side of the environmental separator, materials and components installed to provide the required resistance to heat transfer or the means implemented to dissipate heat shall provide sufficient resistance or dissipation, (a) to minimize surface condensation on the warm side of the component or assembly, (b) in conjunction with other materials and components in the assembly, to minimize condensation within the component or assembly, (c) in conjunction with systems installed for space conditioning, to meet the interior design thermal conditions for the intended occupancy, and (d) to minimize ice damming on sloped roofs. | obc2019_divb | Div B | 5.3.1.2.(1) | 5.3.1.2. Properties to Resist Heat Transfer or Dissipate Heat | Materials and components installed to provide the required resistance to heat transfer or the means implemented to dissipate heat shall,(a) provide sufficient resistance or dissipation, (i) to minimize surface condensation on the warm side of the component or assembly, (ii) in conjunction with other materials and components in the assembly, to minimize condensation within the component or assembly, (iii) in conjunction with systems installed for space conditioning, to meet the interior design thermal conditions for the intended occupancy, and (iv) to minimize ice damming on sloped roofs, and (b) take into account the conditions on either side of the environmental separator. (See Appendix A.) | Common Sentence | Yes | Heat Transfer
2015 | ON | NBC | Div B | 5.3.1.3.(1) | 5.3.1.3. Location and Installation of Materials Providing Thermal |  |  | Div B | 5.3.1.3.(1) | 5.3.1.3. Location and Installation of Materials Providing Thermal |  | Common Sentence | No
2015 | ON | NBC | Div B | 5.3.1.3.(2) | 5.3.1.3. Location and Installation of Materials Providing Thermal Resistance | Materials providing required thermal resistance shall have sufficient inherent resistance to airflow or be positioned in the assembly so as to prevent convective airflow through and around the material. (See Note A-5.3.1.3.(2) .) | obc2019_divb | Div B | 5.3.1.3.(2) | 5.3.1.3. Location and Installation of Materials Providing Thermal | Materials providing required thermal resistance shall have sufficient inherent resistance to air flow or be positioned in the assembly so as to prevent convective air flow through and around the material. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 5.4.1.1.(1) | 5.4.1.1. Required Resistance to Air Leakage | Where a building component or assembly separates interior conditioned space from exterior space, interior space from the ground, or environmentally dissimilar interior spaces, the properties and position of the materials and components in those components or assemblies shall be such that they control air leakage or permit venting to the exterior so as (a) to provide acceptable conditions for the building occupants, (b) maintain appropriate conditions for the intended use of the building, (c) minimize the accumulation of condensation in and the penetration of precipitation into the building component or assembly, (d) control heat transfer to roofs where ice damming can occur, (e) minimize the ingress of airborne radon from the ground with an aim to controlling the indoor radon concentration to an acceptable level, and (f) not compromise the operation of building services. | obc2019_divb | Div B | 5.4.1.1.(1) | 5.4.1.1. Required Resistance to Air Leakage | Where a building component or assembly separates interior conditioned space from exterior space, interior space from the ground, or environmentally dissimilar interior spaces, the properties and position of the materials and components in those components or assemblies shall be such that they control air leakage or permit venting to the exterior so as to,(a) provide acceptable conditions for the building occupants, (b) maintain appropriate conditions for the intended use of the building, (c) minimize the accumulation of condensation in and penetration of precipitation into the building component or assembly, (d) control heat transfer to roofs where ice damming can occur, and (e) not compromise the operation of building services. | Common Sentence | Yes | Air Leakage
2015 | ON | NBC | Div B | 5.4.1.1.(2) | 5.4.1.1. Required Resistance to Air Leakage | Except as provided in Sentence 5.4.1.1.(3), an air barrier system shall be installed to provide the principal resistance to air leakage. | obc2019_divb | Div B | 5.4.1.1.(2) | 5.4.1.1. Required Resistance to Air Leakage | Except as provided in Sentence (3), an air barrier system shall be installed to provide the principal resistance to air leakage. | Common Sentence | No
2015 | ON | NBC | Div B | 5.4.1.1.(3) | 5.4.1.1. Required Resistance to Air Leakage | An air barrier system is not required where it can be shown that uncontrolled air leakage will not adversely affect any of the health or safety of building users, the intended use of the building, or the operation of building services. | obc2019_divb | Div B | 5.4.1.1.(3) | 5.4.1.1. Required Resistance to Air Leakage | An air barrier system is not required where it can be shown that uncontrolled air leakage will not adversely affect any of, (a) the health or safety of building users, (b) the intended use of the building, or (c) the operation of building services. | Common Sentence | No
2015 | ON | NBC | Div B | 5.4.1.2.(1) | 5.4.1.2. Air Barrier System Properties | Except as provided in Sentence 5.4.1.2.(2), air barrier materials intended to provide the principal resistance to air leakage shall (a) have an air leakage characteristic not greater than 0.02 L/(s·m2) measured at an air pressure difference of 75 Pa, when tested in accordance to ASTM E 2178-13 Air Permeance of Building Materials or (b) conform to ULC CAN/ULC-S741-08 Air Barrier Materials - Specification | obc2019_divb | Div B | 5.4.1.2.(1) | 5.4.1.2. Air Barrier System Properties | Except as provided in Sentence (2), materials intended to provide the principal resistance to air leakage shall, (a) have an air leakage characteristic not greater than 0.02 L/(s*m2) measured at an air pressure difference of 75 Pa when tested in accordance with ASTM E2178, "Air Permeance of Building Materials", or (b) conform to CAN/ULC-S741, "Air Barrier Materials Ã¢â‚¬" Specification". (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 5.4.1.2.(2) | 5.4.1.2. Air Barrier System Properties | The air leakage limit specified in Sentence 5.4.1.2.(1) is permitted to be increased where it can be shown that the higher rate of leakage will not adversely affect any of the health or safety of the building users, the intended use of the building, or the operation of building services. | obc2019_divb | Div B | 5.4.1.2.(2) | 5.4.1.2. Air Barrier System Properties | The air leakage limit specified in Sentence (1) is permitted to be increased where it can be shown that the higher rate of leakage will not adversely affect any of,(a) the health or safety of building users, (b) the intended use of the building, or (c) the operation of building services. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 5.4.1.2.(3) | 5.4.1.2. Air Barrier System Properties | The air barrier system shall be continuous across construction, control and expansion joints, across junctions between different building assemblies, and around penetrations through the building assembly. | obc2019_divb | Div B | 5.4.1.2.(3) | 5.4.1.2. Air Barrier System Properties | The air barrier system shall be continuous,(a) across construction, control and expansion joints, (b) across junctions between different building assemblies, and (c) around penetrations through the building assembly. | Common Sentence | No
2015 | ON | NBC | Div B | 5.4.1.2.(4) | 5.4.1.2. Air Barrier System Properties | The structural design of air barrier systems installed in assemblies subject to air pressure loads shall comply with Article 5.1.4.1. and part 5. | obc2019_divb | Div B | 5.4.1.2.(4) | 5.4.1.2. Air Barrier System Properties | The structural design of air barrier systems installed in assemblies subject to air pressure loads shall comply with Article 5.1.4.1. and Subsection 5.2.2. | Common Sentence | No
2015 | ON | NBC | Div B | 5.5.1.1.(1) | 5.5.1.1. Required Resistance to Vapour Diffusion | Where a building component or assembly is subjected to differentials in temperature and water vapour pressure, the properties and position of the materials and components in those components or assemblies shall be such that they control vapour diffusion or permit venting to the exterior so as to minimize the accumulation of condensation in the building component or assembly. | obc2019_divb | Div B | 5.5.1.1.(1) | 5.5.1.1. Required Resistance to Vapour Diffusion | Where a building component or assembly is subjected to differentials in temperature and water vapour pressure, the properties and position of the materials and components in those components or assemblies shall be such that they control vapour diffusion or permit venting to the exterior so as to minimize accumulation of condensation in the building component or assembly. | Common Sentence | No
2015 | ON | NBC | Div B | 5.5.1.1.(2) | 5.5.1.1. Required Resistance to Vapour Diffusion | Except as provided in Sentence 5.5.1.1.(3), a vapour barrier shall be installed to provide the principal resistance to water vapour diffusion. | obc2019_divb | Div B | 5.5.1.1.(2) | 5.5.1.1. Required Resistance to Vapour Diffusion | Except as provided in Sentence (3), a vapour barrier shall be installed to provide the principal resistance to water vapour diffusion. | Common Sentence | No
2015 | ON | NBC | Div B | 5.5.1.1.(3) | 5.5.1.1. Required Resistance to Vapour Diffusion | A vapour barrier is not required where it can be shown that uncontrolled vapour diffusion will not adversely affect any of the health or safety of building users, the intended use of the building, or the operation of building services. | obc2019_divb | Div B | 5.5.1.1.(3) | 5.5.1.1. Required Resistance to Vapour Diffusion | Except as provided in Sentence (3), a vapour barrier shall be installed to provide the principal resistance to water vapour diffusion. | Common Sentence | No
2015 | ON | NBC | Div B | 5.5.1.2.(1) | 5.5.1.2. Vapour Barrier Properties and Installation | The vapour barrier shall have sufficiently low permeance and shall be positioned in the building component or assembly so as to minimize moisture transfer by diffusion, to surfaces within the assembly that would be cold enough to cause condensation at the design temperature and humidity conditions, or reduce moisture transfer by diffusion, to surfaces within the assembly that would be cold enough to cause condensation at the design temperature and humidity conditions, to a rate that will not allow sufficient accumulation of moisture to cause deterioration or otherwise adversely affect any of the health or safety of building users, the intended use of the building, or the operation of building services. | obc2019_divb | Div B | 5.5.1.2.(1) | 5.5.1.2. Vapour Barrier Properties and Installation | The vapour barrier shall have sufficiently low permeance and shall be positioned in the building component or assembly so as to,(a) minimize moisture transfer by diffusion, to surfaces within the assembly that would be cold enough to cause condensation at the design temperature and humidity conditions, or (b) reduce moisture transfer by diffusion, to surfaces within the assembly that would be cold enough to cause condensation at the design temperature and humidity conditions, to a rate that will not allow sufficient accumulation of moisture to cause deterioration or otherwise adversely affect any of, (i) the health or safety of building users, (ii) the intended use of the building, or (iii) the operation of building services. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 5.5.1.2.(2) | 5.5.1.2. Vapour Barrier Properties and Installation | Coatings applied to gypsum board to provide required resistance to vapour diffusion shall conform to the requirements of Sentence 5.5.1.2.(1) when tested in accordance with CGSB CAN/CGSB-1.501-M89 Method for Permeance of Coated Wallboard | obc2019_divb | Div B | 5.5.1.2.(2) | 5.5.1.2. Vapour Barrier Properties and Installation | Coatings applied to gypsum wallboard to provide required resistance to vapour diffusion shall conform to the requirements of Sentence (1) when tested in accordance with CAN/CGSB-1.501-M, "Method for Permeance of Coated Wallboard". | Common Sentence | No
2015 | ON | NBC | Div B | 5.5.1.2.(3) | 5.5.1.2. Vapour Barrier Properties and Installation | Coatings applied to materials other than gypsum board to provide required resistance to vapour diffusion shall conform to the requirements of Sentence 5.5.1.2.(1) when tested in accordance with ASTM E 96/E 96M-13 Water Vapor Transmission of Materials by the desiccant method (dry cup). | obc2019_divb | Div B | 5.5.1.2.(3) | 5.5.1.2. Vapour Barrier Properties and Installation | Coatings applied to materials other than gypsum wallboard to provide required resistance to vapour diffusion shall conform to the requirements of Sentence (1) when tested in accordance with ASTM E96 / E96M, "Water Vapor Transmission of Materials" by the desiccant method (dry cup). | Common Sentence | No
2015 | ON | NBC | Div B | 5.6.1.1.(1) | 5.6.1.1. Required Protection from Precipitation | Except as provided in Sentence 5.6.1.1.(2), where a building component or assembly is exposed to precipitation, the component or assembly shall minimize ingress of precipitation into the component or assembly, and prevent ingress of precipitation into interior space. | obc2019_divb | Div B | 5.6.1.1.(1) | 5.6.1.1. Required Protection from Precipitation | Except as provided in Sentence (2), where a building component or assembly is exposed to precipitation, the component or assembly shall,(a) minimize ingress of precipitation into the component or assembly, and (b) prevent ingress of precipitation into interior space. | Common Sentence | No
2015 | ON | NBC | Div B | 5.6.1.1.(2) | 5.6.1.1. Required Protection from Precipitation | Protection from ingress of precipitation is not required where it can be shown that such ingress will not adversely affect any of the health or safety of building users, the intended use of the building, or the operation of building services. | obc2019_divb | Div B | 5.6.1.1.(2) | 5.6.1.1. Required Protection from Precipitation | Protection from ingress of precipitation is not required where it can be shown that such ingress will not adversely affect any of,(a) the health or safety of building users, (b) the intended use of the building, or (c) the operation of building services. | Common Sentence | No
2015 | ON | NBC | Div B | 5.6.1.2.(1) | 5.6.1.2. Installation of Protective Materials | Where protective materials are applied to assemblies to provide the required protection from precipitation, they shall be installed so as to shed precipitation or otherwise minimize its entry into the assembly and prevent its penetration through the assembly. (See Note A-5.6.1.2.(1).) | obc2019_divb | Div B | 5.6.1.2.(3) | 5.6.1.2. Installation of Protective Materials | Where protective materials are applied to assemblies to provide the required protection from precipitation, the materials shall be installed so as to shed precipitation or otherwise minimize its entry into the assembly and prevent its penetration through the assembly. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 5.6.1.2.(2) | 5.6.1.2. Installation of Protective Materials | Where protective materials applied to assemblies to provide the required protection from precipitation are part of a vegetated roofing system, they shall be resistant to root and rhizome penetration when tested in accordance with SPRI ANSI/GRHC/SPRI VR-1, " Investigating Resistance to Root Penetration on Vegetative Roofs." (See Note A-5.6.1.2.(2).) | obc2019_divb | Div B | 5.6.1.2.(4) | 5.6.1.2. Installation of Protective Materials | Where protective materials described in Sentence (3) are part of a vegetative roofing system, they shall be resistant to root and rhizome penetration when tested in accordance with ANSI/GRHC/SPRI VR-1, "Procedure for Investigating Resistance to Root Penetration on Vegetative Roofs". (See Appendix A.) | Common Sentence | Yes | Precipitation Management
2015 | ON | NBC | Div B | 5.6.2.1.(1) | 5.6.2.1. Sealing and Drainage | Except as provided in Sentence 5.6.2.1.(2), materials, components, assemblies, joints in materials, junctions between components and junctions between assemblies exposed to precipitation shall be sealed to prevent ingress of precipitation, or drained to direct precipitation to the exterior. | obc2019_divb | Div B | 5.6.2.1.(1) | 5.6.2.1. Sealing and Drainage | Except as provided in Sentence (2), materials, components, assemblies, joints in materials, junctions between components and junctions between assemblies exposed to precipitation shall be,(a) sealed to prevent ingress of precipitation, or (b) drained to direct precipitation to the exterior. | Common Sentence | No
2015 | ON | NBC | Div B | 5.6.2.1.(2) | 5.6.2.1. Sealing and Drainage | Sealing or drainage are not required where it can be shown that the omission of sealing and drainage will not adversely affect any of the health or safety of building users, the intended use of the building, or the operation of building services. | obc2019_divb | Div B | 5.6.2.1.(2) | 5.6.2.1. Sealing and Drainage | Sealing or drainage are not required where it can be shown that the omission of sealing and drainage will not adversely affect any of,(a) the health or safety of building users, (b) the intended use of the building, or (c) the operation of building services. | Common Sentence | No
2015 | ON | NBC | Div B | 5.6.2.2.(1) | 5.6.2.2. Accumulation and Disposal | Where precipitation can accumulate on sloped or horizontal assemblies, provision shall be made for drainage conforming with the relevant provincial or territorialregulations or municipalbylaws or, in the absence of such regulationsor bylaws, with Article 2.4.10.4. of Division B of the NPC. | obc2019_divb | Div B | 5.6.2.2.(2) | 5.6.2.2. Accumulation and Disposal | Where precipitation can accumulate on sloped or horizontal assemblies, provision shall be made for drainage conforming with Section 7.4. | Common Sentence | Yes | Precipitation Management
2015 | ON | NBC | Div B | 5.6.2.2.(1) | 5.6.2.2. Accumulation and Disposal | Where water, snow or ice can accumulate on a building, provision shall be made to minimize the likelihood of hazardous conditions arising from such accumulation. |  | Div B | 5.6.2.2.(1) | 5.6.2.2. Accumulation and Disposal | Where water, snow or ice can accumulate on a building, provision shall be made to minimize the likelihood of hazardous conditions arising from such accumulation. | Common Sentence | No
2015 | ON | NBC | Div B | 5.6.2.2.(3) | 5.6.2.2. Accumulation and Disposal | Where downspouts are provided and are not connected to a sewer, provisions shall be made to divert the water from the building, and prevent soil erosion. | obc2019_divb | Div B | 5.6.2.2.(3) | 5.6.2.2. Accumulation and Disposal | Where downspouts are provided and are not connected to a sewer, provisions shall be made to, (a) divert the water from the building, and (b) prevent soil erosion. | Common Sentence | No
2015 | ON | NBC | Div B | 5.7.1.1.(1) | 5.7.1.1. Application | This Subsection applies to the location of buildings, the grading of building sites, the directing of water away from building assemblies, and the provision of means for drainage. | obc2019_divb | Div B | 5.7.1.1.(1) | 5.7.1.1. Application | This Subsection applies to the location of buildings, the grading of building sites, the directing of surface water away from building assemblies and the provision of means for drainage. | Common Sentence | Yes | Precipitation Management
2015 | ON | NBC | Div B | 5.7.1.2.(1) | 5.7.1.2. Required Protection | The building shall be located, the building site shall be graded, or water shall be directed away from building assemblies so as to prevent or accommodate the accumulation of surface water against the building or adjacent buildings. | obc2019_divb | Div B | 5.7.1.2.(1) | 5.7.1.2. Required Protection | The building shall be located, the building site shall be graded or surface water shall be directed away from building assemblies so as to,(a) minimize the accumulation of surface water against the building in a manner that does not adversely affect adjacent buildings or properties, or (b) accommodate the accumulation of surface water on the property in a manner that does not adversely affect the building or adjacent buildings or properties. | Common Sentence | Yes | Precipitation Management
2015 | ON | NBC | Div B | 5.7.1.2.(2) | 5.7.1.2. Required Protection | Drainage shall be provided to direct water away from assemblies separating interior space from the ground, except where the assembly is designed in accordance with part 5. to withstand continuous hydrostatic pressure, or where it can be shown that the lack of drainage will not adversely affect the health or safety of building users, the intended use of the building, or the operation of building services. | obc2019_divb | Div B | 5.7.1.2.(2) | 5.7.1.2. Required Protection | Drainage shall be provided to direct surface water away from building assemblies separating interior space from the ground, except,(a) where the building assembly is designed in accordance with Subsection 5.7.2. to withstand continuous hydrostatic pressure, or (b) where it can be shown that the lack of drainage will not adversely affect any of, (i) the health or safety of building users, (ii) the intended use of the building, or (iii) the operation of building services. (See Appendix A.) | Common Sentence | Yes | Precipitation Management
2015 | ON | NBC | Div B | 5.7.2.2.(1) | 5.7.2.2. Design of Building Elements Under Hydrostatic Loads | Waterproofing materials, components, assemblies and systems described in Article 5.7.2.1. shall be designed in accordance with part 5. | obc2019_divb | Div B | 5.7.2.2.(1) | 5.7.2.2. Design of Building Elements under Hydrostatic Loads | Waterproofing materials, components, assemblies and systems described in Article 5.7.2.1. shall be designed in accordance with Subsection 5.1.4. | Common Sentence | No
2015 | ON | NBC | Div B | 5.7.2.2.(2) | 5.7.2.2. Design of Building Elements Under Hydrostatic Loads | Hydrostatic design loads shall be determined in accordance with Subsectino 5.2.2. | obc2019_divb | Div B | 5.7.2.2.(2) | 5.7.2.2. Design of Building Elements under Hydrostatic Loads | The hydrostatic design loads shall be determined in accordance with Subsection 5.2.2. | Common Sentence | No
2015 | ON | NBC | Div B | 5.7.3.2.(1) | 5.7.3.2. Required Protection | Except as provided in Sentence 5.7.3.2.(2) and Article 5.7.3.4., building assemblies described in Article 5.7.3.1. shall be protected by waterproofing in accordance with Article 5.7.3.3. so as to prevent the ingress of water into the building or the accumulation of water against the building. | obc2019_divb | Div B | 5.7.3.2.(1) | 5.7.3.2. Required Protection | Except as provided in Sentence (2) and Article 5.7.3.4., building assemblies described in Article 5.7.3.1. shall be protected by waterproofing in accordance with Article 5.7.3.3. so as to minimize the ingress of ground water into the building or the accumulation of ground water against the building. | Common Sentence | Yes | Precipitation Management
2015 | ON | NBC | Div B | 5.7.3.2.(2) | 5.7.3.2. Required Protection | Waterproofing is not required where it can be shown that (a) a building is designed to accommodate the ingress or accumulation of water, or (b) the ingress or accumulation of water will not negatively affect (i) the health or safety of building users, (ii) the intended use of the building, or (iii) the operation of building services. | obc2019_divb | Div B | 5.7.3.2.(2) | 5.7.3.2. Required Protection | Waterproofing is not required where it can be shown that,(a) a building is designed to accommodate the ingress or accumulation of ground water, or (b) the ingress or accumulation of ground water will not adversely affect any of, (i) the health or safety of building users, (ii) the intended use of the building, or (iii) the operation of building services. | Common Sentence | Yes | Precipitation Management
2015 | ON | NBC | Div B | 5.7.3.3.(1) | 5.7.3.3. Waterproofing | Waterproofing materials, components, assemblies, or systems installed to provide the required protection shall form a continuous and impervious barrier to the ingress of water and be capable of accommodating (a) imperfections, construction joints, control joints and expansion joints (see Note A-5.7.3.3.(1)(a)), (b) junctions between different building assemblies, and (c) elements penetrating building assemblies. | obc2019_divb | Div B | 5.7.3.3.(1) | 5.7.3.3. Waterproofing | Waterproofing materials, components, assemblies or systems installed to provide the required protection shall form a continuous and impervious barrier to the ingress of ground water and be capable of accommodating,(a) imperfections, construction joints, control joints and expansion joints, (See Appendix A.) (b) junctions between different building assemblies, and (c) elements penetrating building assemblies. | Common Sentence | Yes | Precipitation Management
2015 | ON | NBC | Div B | 5.7.3.4.(1) | 5.7.3.4. Where Dampproofing is Permitted | Vertical building assemblies that separate interior space from the ground are permitted to be dampproofed where (a) such assemblies are not subjected to hydrostatic pressure, (b) the substrate is cast-in-place concrete, and (c) a drainage layer is installed between the building assembly and the soil. | obc2019_divb | Div B | 5.7.3.4.(1) | 5.7.3.4. Where Dampproofing is Permitted | Vertical building assemblies that separate interior space from the ground are permitted to be dampproofed where,(a) the building assemblies are not subjected to hydrostatic pressure, (b) the substrate is cast-in-place concrete, and (c) a drainage layer is installed between the building assembly and the soil. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 5.8.1.1.(1) | 5.8.1.1. Required Protection | Except as provided in Sentence 5.8.1.1.(2), a dwelling unit shall be separated from every other space in a building in which noise may be generated by (a) a separating assembly and adjoining constructions, which, together, provide an apparent sound transmission class (ASTC) rating not less than 47, or (b) a separating assembly that provides a sound transmission class (STC) rating of not less than 50 and adjoining constructions that conform to Article 9.11.1.4. | obc2019_divb | Div B | 5.8.1.1.(1) | 5.8.1.1. Required Protection | Except as provided in Sentence (2), a dwelling unit shall be separated from every other space in a building in which noise may be generated by,(a) a separating assembly and adjoining construction, which, together, provide an apparent sound transmission class rating not less than 47, or (b) a separating assembly that provides a sound transmission class rating not less than 50 and adjoining construction that conforms to Article 9.11.1.4. | Common Sentence | No
2015 | ON | NBC | Div B | 5.8.1.2.(1) | 5.8.1.2. Determination of Sound Transmission Ratings | The STC ratings of separating assemblies shall be determined in accordance with ASTM E 413-10 Classification for Rating Sound Insulation using the results from measurements carried out in accordance with ASTM E 90-09 Laboratory Measurement of Airborne Sound Transmission Loss of Building Partitions and Elements | obc2019_divb | Div B | 5.8.1.2.(1) | 5.8.1.2. Determination of Sound Transmission Ratings | The STC ratings of separating assemblies shall be determined in accordance with ASTM E413, "Classification for Rating Sound Insulation", using the results from measurements carried out in accordance with ASTM E90, "Laboratory Measurement of Airborne Sound Transmission Loss of Building Partitions and Elements". | Common Sentence | No
2015 | ON | NBC | Div B | 5.8.1.2.(2) | 5.8.1.2. Determination of Sound Transmission Ratings | The ASTC ratings of separating assemblies and adjoining constructions shall be (a) determined in accordance with ASTM E 413-10 Classification for Rating Sound Insulation using the results from measurements carried out in accordance with ASTM E 336-11 Measurement of Airborne Sound Attenuation between Rooms in Buildings or calculated in accordance with (i) the detailed method described in Article 5.8.1.4., or (ii) the simplified method described in Article 5.8.1.5. | obc2019_divb | Div B | 5.8.1.2.(2) | 5.8.1.2. Determination of Sound Transmission Ratings | The ASTC ratings of separating assemblies and adjoining construction shall be,(a) determined in accordance ASTM E413, "Classification for Rating Sound Insulation", using the results from measurements carried out in accordance with ASTM E336, "Measurement of Airborne Sound Attenuation Between Rooms in Buildings", or (b) calculated in accordance with, (i) the detailed method described in Article 5.8.1.4., or (ii) the simplified method described in Article 5.8.1.5. | Common Sentence | No
2015 | ON | NBC | Div B | 5.8.1.3.(1) | 5.8.1.3. Compliance with Required Ratings | Compliance with the required STC ratings shall be demonstrated through (a) measurements carried out in accordance with Sentence 5.8.1.2.(1), or (b) the construction of separating assemblies conforming to those presented in Table 9.10.3.1.-A or 9.10.3.1.-B, as applicable. | obc2019_divb | Div B | 5.8.1.3.(1) | 5.8.1.3. Compliance with Required Ratings | Compliance with the required STC ratings shall be demonstrated through,(a) measurements carried out in accordance with Sentence 5.8.1.2.(1), or (b) the construction of separating assemblies conforming to Table 1 or 2 of MMAH Supplementary Standard SB-3, "Fire and Sound Resistance of Building Assemblies", as applicable. | Common Sentence | Yes | Sound Transmission
2015 | ON | NBC | Div B | 5.8.1.3.(1) | 5.8.1.4. Compliance with Required Ratings | Compliance with the required STC ratings shall be demonstrated through measurements carried out in accordance with Sentence 5.8.1.2.(1), or the construction of separating assemblies conforming to those presented in Table 9.10.3.1.-Aor 9.10.3.1.-B, as applicable. | obc2019_divb | Div B | 5.8.1.4.(1) | 5.8.1.4. Detailed Method for Calculating ASTC | This Article sets out the detailed method for calculating the ASTC ratings of separating assemblies and adjoining construction referred to in Subclause 5.8.1.2.(2)(b)(i). | Common Sentence | Yes | Sound Transmission
2015 | ON | NBC | Div B | 5.8.1.3.(1) | Compliance with Required Ratings | Same as above | obc2019_divb | Div B | 5.8.1.5.(1) | 5.8.1.5. Simplified Method for Calculating ASTC | This Article sets out the simplified method for calculating the ASTC ratings of separating assemblies and adjoining construction referred to in Subclause 5.8.1.2.(2)(b)(ii). | Common Sentence | Yes | Sound Transmission
2015 | ON | NBC | Div B | 5.8.1.3.(2) | 5.8.1.3. Compliance with Required Ratings | Compliance with the required ASTC ratings shall be demonstrated through (a) measurements or calculations carried out in accordance with Sentence 5.8.1.2.(2), or (b) the construction of separating assemblies conforming to those presented in Table 9.10.3.1.-A or 9.10.3.1.-B, as applicable, that have an STC rating of not less than 50 in conjunction with flanking assemblies constructed in accordance with Article 9.11.1.4. | obc2019_divb | Div B | 5.8.1.3.(2) | 5.8.1.3. Compliance with Required Ratings | Compliance with the required ASTC ratings shall be demonstrated through,(a) measurements or calculations carried out in accordance with Sentence 5.8.1.2.(2), or (b) the construction of separating assemblies conforming to Table 1 or 2 of MMAH Supplementary Standard SB-3, "Fire and Sound Resistance of Building Assemblies", as applicable, that have an STC rating not less than 50 in conjunction with flanking assemblies constructed in accordance with Article 9.11.1.4. | Common Sentence | Yes | Sound Transmission
2015 | ON | NBC | Div B | 5.8.1.4.(1) | 5.8.1.4. Detailed Method for Calculating ASTC | The sound transmission loss measured in accordance with ASTM E 90-09 Laboratory Measurement of Airborne Sound Transmission Loss of Building Partitions and Elements shall be used in lieu of the sound reduction index required in ISO 15712-1:2005 Building Acoustics - Estimation of Acoustic Performance of Buildings From the Performance of Elements - Part 1: Airborne Sound Insulation Between Rooms | obc2019_divb | Div B | 5.8.1.4.(2) | 5.8.1.4. Detailed Method for Calculating ASTC | The sound transmission loss measured in accordance with ASTM E90, "Laboratory Measurement of Airborne Sound Transmission Loss of Building Partitions and Elements", shall be used in lieu of the sound reduction index required in ISO 15712-1, "Building Acoustics - Estimation of Acoustic Performance of Buildings From the Performance of Elements - Part 1: Airborne Sound Insulation Between Rooms". | Common Sentence | No
2015 | ON | NBC | Div B | 5.8.1.4.(2) | 5.8.1.4. Detailed Method for Calculating ASTC | The vibration reduction index for the junctions between separating assemblies shall be determined using the equations presented in Annex E of ISO 15712-1:2005 Building Acoustics - Estimation of Acoustic Performance of Buildings From the Performance of Elements - Part 1: Airborne Sound Insulation Between Rooms or measured in accordance with Parts 1 to 4 of ISO 10848:2006 Acoustics - Laboratory Measurement of the Flanking Transmission of Airborne and Impact Sound Between Adjoining Rooms | obc2019_divb | Div B | 5.8.1.4.(3) | 5.8.1.4. Detailed Method for Calculating ASTC | The vibration reduction index for the junctions between separating assemblies shall be, (a) determined using the equations presented in Annex E of ISO 15712-1, "Building Acoustics - Estimation of Acoustic Performance of Buildings From the Performance of Elements - Part 1: Airborne Sound Insulation Between Rooms", or (b) measured in accordance with Parts 1 to 4 of ISO 10848, "Acoustics - Laboratory Measurement of the Flanking Transmission of Airborne and Impact Sound Between Adjoining Rooms". | Common Sentence | No
2015 | ON | NBC | Div B | 5.8.1.4.(2) | 5.8.1.5. Simplified Method for Calculating ASTC | The vibration reduction index for the junctions between separating assemblies shall be determined using the equations presented in Annex E of ISO 15712-1:2005 Building Acoustics - Estimation of Acoustic Performance of Buildings From the Performance of Elements - Part 1: Airborne Sound Insulation Between Rooms or measured in accordance with Parts 1 to 4 of ISO 10848:2006 Acoustics - Laboratory Measurement of the Flanking Transmission of Airborne and Impact Sound Between Adjoining Rooms | obc2019_divb | Div B | 5.8.1.5.(3) | 5.8.1.5. Simplified Method for Calculating ASTC | The vibration reduction index for the junctions between separating assemblies shall be, (a) determined using the equations presented in Annex E of ISO 15712-1, "Building Acoustics - Estimation of Acoustic Performance of Buildings From the Performance of Elements - Part 1: Airborne Sound Insulation Between Rooms", or (b) measured in accordance with Parts 1 to 4 of ISO 10848, "Acoustics - Laboratory Measurement of the Flanking Transmission of Airborne and Impact Sound Between Adjoining Rooms". | Common Sentence | No
2015 | ON | NBC | Div B | 5.8.1.4.(3) | 5.8.1.4. Detailed Method for Calculating ASTC | The normalized flanking level difference shall be measured in accordance with Parts 1 to 4 of ISO 10848:2006 Acoustics - Laboratory Measurement of the Flanking Transmission of Airborne and Impact Sound Between Adjoining Rooms | obc2019_divb | Div B | 5.8.1.4.(4) | 5.8.1.4. Detailed Method for Calculating ASTC | The normalized flanking level difference shall be measured in accordance with Parts 1 to 4 of ISO 10848, "Acoustics - Laboratory Measurement of the Flanking Transmission of Airborne and Impact Sound Between Adjoining Rooms". | Common Sentence | No
2015 | ON | NBC | Div B | 5.8.1.4.(4) | 5.8.1.4. Detailed Method for Calculating ASTC | The direct sound reduction index for the separating assembly in situ shall be determined using Clause 5.8.1.4.(4)(a) or 5.8.1.4.(4)(b), depending on the type of construction: (a) for a lightweight separating wall or floor assembly with wood or steel framing, the index shall be taken as equal to the sound transmission loss, without correction; (b) for a heavyweight separating wall or floor assembly of concrete or masonry, the index shall be determined in accordance with the detailed method for structure-borne transmission presented in ISO 15712-1:2005 Building Acoustics - Estimation of Acoustic Performance of Buildings From the Performance of Elements - Part 1: Airborne Sound Insulation Between Rooms | obc2019_divb | Div B | 5.8.1.4.(5) | 5.8.1.4. Detailed Method for Calculating ASTC | The direct sound reduction index for the separating assembly in situ shall be determined from sound transmission loss in accordance with Clause (a) or (b), depending on the type of construction: (a) for a lightweight separating wall or floor assembly with wood or steel framing, the index shall be taken as equal to the sound transmission loss, without correction, (b) for a heavyweight separating wall or floor assembly of concrete or masonry, the index shall be determined in accordance with the detailed method for structure-borne transmission presented in ISO 15712-1, "Building Acoustics - Estimation of Acoustic Performance of Buildings From the Performance of Elements - Part 1: Airborne Sound Insulation Between Rooms". | Common Sentence | No
2015 | ON | NBC | Div B | 5.8.1.4.(5) | 5.8.1.4. Detailed Method for Calculating ASTC | The flanking sound reduction index for each flanking path at each edge of the separating assembly shall be determined using Clause 5.8.1.4.(5)(a) , 5.8.1.4.(5)(b) or 5.8.1.4.(5)(c), depending on the type of construction: (a) for a lightweight separating wall or floor assembly with wood or steel framing and connected lightweight flanking assemblies with wood or steel framing, the index shall be taken as equal to the normalized flanking level difference re-normalized for the ASTC field situation in accordance with Annex F of ISO 15712-1:2005 Building Acoustics - Estimation of Acoustic Performance of Buildings From the Performance of Elements - Part 1: Airborne Sound Insulation Between Rooms; (b) for a heavyweight separating wall or floor assembly of concrete or masonry and connected flanking assemblies of concrete or masonry, the index shall be determined in accordance with the detailed method for structure-borne transmission presented in ISO 15712-1:2005 Building Acoustics - Estimation of Acoustic Performance of Buildings From the Performance of Elements - Part 1: Airborne Sound Insulation Between Rooms; (c) for a mixture of lightweight framed assemblies and heavyweight concrete or masonry assemblies, the index shall be determined in accordance with Sentence 5.8.1.4.(5) or 5.8.1.4.(5). | obc2019_divb | Div B | 5.8.1.4.(6) | 5.8.1.4. Detailed Method for Calculating ASTC | The flanking sound reduction index for each flanking path at each edge of the separating assembly shall be determined in accordance with Clause (a), (b) or (c), depending on the type of construction:(a) for a lightweight separating wall or floor assembly with wood or steel framing and connected lightweight flanking assemblies with wood or steel framing, the index shall be taken as equal to the normalized flanking level difference re-normalized for the ASTC field situation in accordance with Annex F of ISO 15712-1, "Building Acoustics - Estimation of Acoustic Performance of Buildings From the Performance of Elements - Part 1: Airborne Sound Insulation Between Rooms", (b) for a heavyweight separating wall or floor assembly of concrete or masonry and connected flanking assemblies of concrete or masonry, the index shall be determined in accordance with the detailed method for structure-borne transmission presented in ISO 15712-1, "Building Acoustics - Estimation of Acoustic Performance of Buildings From the Performance of Elements - Part 1: Airborne Sound Insulation Between Rooms", (c) for a mixture of lightweight framed assemblies and heavyweight concrete or masonry assemblies, the index shall be determined in accordance with Clause (a) or (b). | Common Sentence | No
2015 | ON | NBC | Div B | 5.8.1.4.(6) | 5.8.1.4. Detailed Method for Calculating ASTC | Once the pertinent indices and measurements referred to in Sentences 5.8.1.4.(1) to 5.8.1.4.(5) have been determined based on the type of construction, the apparent sound reduction index shall then be determined in accordance with ISO 15712-1:2005 Building Acoustics - Estimation of Acoustic Performance of Buildings From the Performance of Elements - Part 1: Airborne Sound Insulation Between Rooms | obc2019_divb | Div B | 5.8.1.4.(7) | 5.8.1.4. Detailed Method for Calculating ASTC | Once the pertinent indices and measurements referred to in Sentences (2) to (6) have been determined based on the type of construction, the apparent sound reduction index shall then be determined in accordance with ISO 15712-1, "Building Acoustics - Estimation of Acoustic Performance of Buildings From the Performance of Elements - Part 1: Airborne Sound Insulation Between Rooms". | Common Sentence | No
2015 | ON | NBC | Div B | 5.8.1.4.(7) | 5.8.1.4. Detailed Method for Calculating ASTC | The ASTC shall be calculated in accordance with ASTM E 413-10 Classification for Rating Sound Insulation using the apparent sound reduction index determined in Sentence 5.8.1.4.(6), which shall be treated as equivalent to the values of apparent sound transmission loss measured in accordance with ASTM E 336-11 Measurement of Airborne Sound Attenuation between Rooms in Buildings | obc2019_divb | Div B | 5.8.1.4.(8) | 5.8.1.4. Detailed Method for Calculating ASTC | The ASTC rating shall be calculated in accordance with ASTM E413, "Classification for Rating Sound Insulation", using the apparent sound reduction index determined in Sentence (7), which shall be treated as equivalent to the values of apparent sound transmission loss measured in accordance with ASTM E336, "Measurement of Airborne Sound Attenuation between Rooms in Buildings". | Common Sentence | No
2015 | ON | NBC | Div B | 5.8.1.5.(1) | 5.8.1.5. Simplified Method for Calculating ASTC | The STC rating shall be used in lieu of the weighted sound reduction index required in ISO 15712-1:2005 Building Acoustics - Estimation of Acoustic Performance of Buildings From the Performance of Elements - Part 1: Airborne Sound Insulation Between Rooms | obc2019_divb | Div B | 5.8.1.5.(2) | 5.8.1.5. Simplified Method for Calculating ASTC | The STC rating shall be used in lieu of the weighted sound reduction index required in ISO 15712-1, "Building Acoustics - Estimation of Acoustic Performance of Buildings From the Performance of Elements - Part 1: Airborne Sound Insulation Between Rooms". | Common Sentence | No
2015 | ON | NBC | Div B | 5.8.1.5.(3) | 5.8.1.5. Simplified Method for Calculating ASTC | The weighted normalized flanking level difference shall be determined in accordance with ASTM E 413-10 Classification for Rating Sound Insulation using the results from measurements carried out in accordance with Parts 1 to 4 of ISO 10848:2006 Acoustics - Laboratory Measurement of the Flanking Transmission of Airborne and Impact Sound Between Adjoining Rooms | obc2019_divb | Div B | 5.8.1.5.(4) | 5.8.1.5. Simplified Method for Calculating ASTC | The weighted normalized flanking level difference shall be determined in accordance with ASTM E413, "Classification for Rating Sound Insulation", using the results from measurements carried out in accordance with Parts 1 to 4 of ISO 10848, "Acoustics - Laboratory Measurement of the Flanking Transmission of Airborne and Impact Sound Between Adjoining Rooms". | Common Sentence | No
2015 | ON | NBC | Div B | 5.8.1.5.(4) | 5.8.1.5. Simplified Method for Calculating ASTC | The direct weighted sound reduction index for the separating assembly shall be taken as equal to the STC, without correction. | obc2019_divb | Div B | 5.8.1.5.(5) | 5.8.1.5. Simplified Method for Calculating ASTC | The direct weighted sound reduction index for the separating assembly shall be taken as equal to the STC rating, without correction. | Common Sentence | No
2015 | ON | NBC | Div B | 5.8.1.5.(5) | 5.8.1.5. Simplified Method for Calculating ASTC | The weighted flanking sound reduction index for each flanking path at each edge of the separating assembly shall be determined using Clause 5.8.1.5.(5)(a) or 5.8.1.5.(5)(b), depending on the type of construction: (a) for a lightweight separating wall or floor assembly with wood or steel framing and connected lightweight flanking assemblies with wood or steel framing, the index shall be taken as equal to the weighted normalized flanking level difference re-normalized for the ASTC field situation in accordance with Annex F of ISO 15712-1:2005 Building Acoustics - Estimation of Acoustic Performance of Buildings From the Performance of Elements - Part 1: Airborne Sound Insulation Between Rooms; (b) for a heavyweight separating wall or floor assembly of concrete or masonry and connected flanking assemblies of concrete or masonry, the index shall be determined in accordance with the simplified method for structure-borne transmission presented in ISO 15712-1:2005 Building Acoustics - Estimation of Acoustic Performance of Buildings From the Performance of Elements - Part 1: Airborne Sound Insulation Between Rooms | obc2019_divb | Div B | 5.8.1.5.(6) | 5.8.1.5. Simplified Method for Calculating ASTC | The weighted flanking sound reduction index for each flanking path at each edge of the separating assembly shall be determined in accordance with Clause (a) or (b), depending on the type of construction:(a) for a lightweight separating wall or floor assembly with wood or steel framing and connected lightweight flanking assemblies with wood or steel framing, the index shall be taken as equal to the weighted normalized flanking level difference re-normalized for the ASTC field situation in accordance with Annex F of ISO 15712-1, "Building Acoustics - Estimation of Acoustic Performance of Buildings From the Performance of Elements - Part 1: Airborne Sound Insulation Between Rooms", (b) for a heavyweight separating wall or floor assembly of concrete or masonry and connected flanking assemblies of concrete or masonry, the index shall be determined in accordance with the simplified method for structure-borne transmission presented in ISO 15712-1, "Building Acoustics - Estimation of Acoustic Performance of Buildings From the Performance of Elements - Part 1: Airborne Sound Insulation Between Rooms". | Common Sentence | No
2015 | ON | NBC | Div B | 5.8.1.5.(6) | 5.8.1.5. Simplified Method for Calculating ASTC | Once the pertinent indices and measurements referred to in Sentences 5.8.1.5.(1) to 5.8.1.5.(5) have been determined based on the type of construction, the ASTC shall then be calculated in accordance with ISO 15712-1:2005 Building Acoustics - Estimation of Acoustic Performance of Buildings From the Performance of Elements - Part 1: Airborne Sound Insulation Between Rooms | obc2019_divb | Div B | 5.8.1.5.(7) | 5.8.1.5. Simplified Method for Calculating ASTC | Once the pertinent indices and measurements referred to in Sentences (2) to (6) have been determined based on the type of construction, the ASTC rating shall then be calculated in accordance with ISO 15712-1, "Building Acoustics - Estimation of Acoustic Performance of Buildings From the Performance of Elements - Part 1: Airborne Sound Insulation Between Rooms". | Common Sentence | No
2015 | ON | NBC | Div B | 5.9.1.1.(1) | 5.9.1.1. Compliance with Applicable Standards | Except as provided in Sentence 5.9.1.1.(2) and elsewhere in this Part, materials and components, and their installation, shall conform to the requirements of the applicable standards in Table 5.9.1.1. where those materials or components are (a) incorporated into environmental separators or assemblies exposed to the exterior, and (b) installed to fulfill the requirements of this Part. | obc2019_divb | Div B | 5.10.1.1.(1) | 5.10.1.1. Compliance with Applicable Standards | Except as provided in Sentence (2) and elsewhere in this Part, materials and components, and their installation, shall conform to the requirements of the applicable standards in Table 5.10.1.1. where those materials or components are,(a) incorporated into environmental separators or assemblies exposed to the exterior, and (b) installed to fulfill the requirements of this Part. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 5.9.2.1.(1) | 5.9.2.1. General | This Subsection applies to windows, doors and skylights, including their components, that separate interior space from exterior space, or environmentally dissimilar interior spaces. | obc2019_divb | Div B | 5.10.2.1.(1) | 5.10.2.1. General | This Subsection applies to windows, doors and skylights, including their components, that separate,(a) interior space from exterior space, or (b) environmentally dissimilar interior spaces. | Common Sentence | No
2015 | ON | NBC | Div B | 5.9.2.1.(3) | 5.9.2.1. General | Where a wired glass assembly is installed in a required fire separation, it need not conform to the requirements of this Subsection. (See Note A-5.9.2.1.(3).) | obc2019_divb | Div B | 5.10.2.1.(3) | 5.10.2.1. General | Where a wired glass assembly is installed in a required fire separation, it need not conform to the requirements of this Subsection. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 5.9.2.2.(1) | 5.9.2.2. Applicable Standards | Windows, doors and skylights shall conform to the requirements in CSA AAMA/WDMA/CSA 101/I.S.2/A440-11 NAFS â€“ North American Fenestration Standard/Specification for Windows, Doors, and Skylights and CSA A440S1-17 Canadian Supplement to AAMA/WDMA/CSA 101/I.S.2/A440-11, NAFS â€“ North American Fenestration Standard/Specification for Windows, Doors, and Skylights | obc2019_divb | Div B | 5.10.2.2.(1) | 5.10.2.2. Applicable Standards | Windows, doors and skylights shall conform to the requirements in,(a) AAMA/WDMA/CSA 101/I.S.2/A440, "NAFS Ã¢â‚¬" North American Fenestration Standard/Specification for Windows, Doors, and Skylights", and (b) CSA A440S1, "Canadian Supplement to AAMA/WDMA/CSA 101/I.S.2/A440, NAFS Ã¢â‚¬" North American Fenestration Standard/Specification for Windows, Doors, and Skylights". | Common Sentence | No
2015 | ON | NBC | Div B | 5.9.2.2.(2) | 5.9.2.2. Applicable Standards | Performance grades for windows, doors and skylights shall be selected according to the Canadian Supplement referenced in Sentence 5.9.2.2.(1) so as to be appropriate for the conditions and geographic location in which the window, door or skylight will be installed. | obc2019_divb | Div B | 5.10.2.2.(2) | 5.10.2.2. Applicable Standards | Performance grades for windows, doors and skylights shall be selected according to the Canadian Supplement referenced in Clause (1)(b) so as to be appropriate for the conditions and geographic location in which the window, door or skylight will be installed. | Common Sentence | No
2015 | ON | NBC | Div B | 5.9.2.2.(3) | 5.9.2.2. Applicable Standards | Windows, doors and skylights shall conform to the performance grades selected in Sentence 5.9.2.2.(2) when tested in accordance with the Harmonized Standard referenced in Sentence 5.9.2.2.(1). | obc2019_divb | Div B | 5.10.2.2.(3) | 5.10.2.2. Applicable Standards | Windows, doors and skylights shall conform to the performance grades selected under Sentence (2) when tested in accordance with the standard referenced in Clause (1)(a). | Common Sentence | No
2015 | ON | NBC | Div B | 5.9.2.3.(1) | 5.9.2.3. Structural and Environmental Loads, Air Leakage and Water Penetration | Windows, doors, skylights and their components shall be designed and constructed in accordance with (a) Article 5.1.4.1., part 5. and part 5., or (b) Article 5.9.2.2., where they are covered in the scope of the standards listed in Sentence 5.9.2.2.(1). | obc2019_divb | Div B | 5.10.2.3.(1) | 5.10.2.3. Structural Loads, Air Leakage and Water Penetration | Windows, doors, skylights and their components shall be designed and constructed in accordance with,(a) Article 5.10.2.2., where they are covered in the scope of the standards listed in Sentence 5.10.2.2.(1), or (b) Article 5.1.4.1. and Sections 5.4. and 5.6., in other cases. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 5.9.2.4.(1) | 5.9.2.4. Heat Transfer | Windows, doors and skylights shall meet the heat transfer performance requirements stated in part 5. (See Note A-5.3.1.2.) | obc2019_divb | Div B | 5.10.2.4.(1) | 5.10.2.4. Heat Transfer | Windows, doors and skylights shall meet the heat transfer performance requirements in Section 5.3. | Common Sentence | No
2015 | ON | NBC | Div B | 5.9.2.4.(2) | 5.9.2.4. Heat Transfer | Except as provided in Sentence 5.9.2.4.(3), all metal-framed glazed assemblies separating interior conditioned space from interior unconditioned space or exterior space shall incorporate a thermal break to minimize condensation. | obc2019_divb | Div B | 5.10.2.4.(2) | 5.10.2.4. Heat Transfer | Except as provided in Sentence (3), all metal-framed glazed assemblies separating interior conditioned space from interior unconditioned space or exterior space shall incorporate a thermal break to minimize condensation. | Common Sentence | No
2015 | ON | NBC | Div B | 5.9.2.4.(3) | 5.9.2.4. Heat Transfer | Metal-framed glazed assemblies need not comply with Sentence 5.9.2.4.(2) where these assemblies are storm windows or doors, or windows or doors that are required to have a fire-protection rating. | obc2019_divb | Div B | 5.10.2.4.(3) | 5.10.2.4. Heat Transfer | Metal-framed glazed assemblies need not comply with Sentence (2) where these assemblies are, (a) storm windows or doors, or (b) windows or doors that are required to have a fire-protection rating. (See Appendix A.) | Common Sentence | No
2015 | ON | NBC | Div B | 5.9.3.1.(1) | 5.9.3.1. General | For the purpose of this Subsection, the term "other fenestration assemblies" refers to curtain walls, window walls, storefronts and glazed architectural structures. (See Note A-5.9.3.1.(1).) | obc2019_divb | Div B | 5.10.4.1.(1) | 5.10.4.1. Definition | In this Subsection,Other fenestration assemblies means curtain walls, window walls, storefronts and glazed architectural structures. | Common Sentence | No
2015 | ON | NBC | Div B | 5.9.3.2.(1) | 5.9.3.2. Structural and Environmental Loads | Other fenestration assemblies and their components shall be designed and constructed in accordance with part 5. | obc2019_divb | Div B | 5.10.4.2.(1) | 5.10.4.2. Structural and Environmental Loads | Other fenestration assemblies and their components shall be designed and constructed in accordance with ArticleÃ‚ 5.1.4.1. | Common Sentence | No
2015 | ON | NBC | Div B | 5.9.3.3.(1) | 5.9.3.3. Heat Transfer | Other fenestration assemblies and their components shall meet the heat transfer performance requirements stated in part 5. (See Note A-5.9.3.3.(1).) | obc2019_divb | Div B | 5.10.4.3.(1) | 5.10.4.3. Heat Transfer | Other fenestration assemblies and their components shall meet the heat transfer performance requirements set out in Section 5.3. | Common Sentence | No
2015 | ON | NBC | Div B | 5.9.3.3.(2) | 5.9.3.3. Heat Transfer | Other fenestration assemblies using metal framing that separate interior conditioned space from interior unconditioned space or exterior space shall incorporate a thermal break to minimize condensation. | obc2019_divb | Div B | 5.10.4.3.(2) | 5.10.4.3. Heat Transfer | Other fenestration assemblies that are metal-framed and separate interior conditioned space from interior unconditioned space or exterior space shall incorporate a thermal break to minimize condensation. | Common Sentence | No
2015 | ON | NBC | Div B | 5.9.3.4.(1) | 5.9.3.4. Air Leakage | Other fenestration assemblies and their components shall be designed and constructed in accordance with part 5. | obc2019_divb | Div B | 5.10.4.4.(1) | 5.10.4.4. Air Leakage | Other fenestration assemblies and their components shall be designed and constructed in accordance with SectionÃ‚ 5.4. | Common Sentence | No
2015 | ON | NBC | Div B | 5.9.3.4.(2) | 5.9.3.4. Air Leakage | Except as provided in Sentence 5.9.3.4.(3), other fenestration assemblies and their components shall have an air leakage characteristic, measured at an air pressure difference of 75 Pa, when tested in accordance with ASTM E 283-04 Determining Rate of Air Leakage Through Exterior Windows, Curtain Walls, and Doors Under Specified Pressure Differences Across the Specimen that is not greater than (a) 0.2 L/(sÂ·m2) for fixed portions, including any opaque portions, and (b) 1.5 L/(sÂ·m2) for operable portions. | obc2019_divb | Div B | 5.10.4.4.(2) | 5.10.4.4. Air Leakage | Except as provided in Sentence (3), other fenestration assemblies and their components shall have an air leakage characteristic, measured at an air pressure difference of 75 Pa and tested in accordance with ASTM E283, "Determining Rate of Air Leakage Through Exterior Windows, Curtain Walls, and Doors Under Specified Pressure Differences Across the Specimen", that is not greater than,(a) 0.2 L/(s*m 2) for fixed portions, including any opaque portions, and (b) 1.5 L/(s*m 2) for operable portions. | Common Sentence | No
2015 | ON | NBC | Div B | 5.9.3.4.(3) | 5.9.3.4. Air Leakage | The following systems need not comply with Sentence 5.9.3.4.(2): (a) interior windows and interior doors that do not serve as environmental separators, (b) vehicular access doors (garage doors), (c) storm windows and storm doors, (d) commercial entrance systems, (e) revolving doors,(f) smoke and relief air vents, (g) site-built door systems, and (h) commercial steel doors. | obc2019_divb | Div B | 5.10.4.4.(3) | 5.10.4.4. Air Leakage | The following need not comply with Sentence (2):(a) interior windows and interior doors that do not serve as environmental separators, (b) vehicular access doors, including garage doors, (c) storm windows and storm doors, (d) commercial entrance systems, (e) revolving doors, (f) smoke and relief air vents, (g) site-built door systems, and (h) commercial steel doors. | Common Sentence | No
2015 | ON | NBC | Div B | 5.9.3.5.(1) | 5.9.3.5. Water Penetration | Other fenestration assemblies and their components shall be designed and constructed in accordance with part 5. | obc2019_divb | Div B | 5.10.4.5.(1) | 5.10.4.5. Water Penetration | Other fenestration assemblies and their components shall be designed and constructed in accordance with SectionÃ‚ 5.6. | Common Sentence | No
2015 | ON | NBC | Div B | 5.9.3.5.(2) | 5.9.3.5. Water Penetration | Except as provided in Sentence 5.9.3.5.(4), other fenestration assemblies and their components not covered in Article 5.9.2.2. shall resist water penetration when tested in accordance with ASTM E 331-00 Water Penetration of Exterior Windows, Skylights, Doors, and Curtain Walls by Uniform Static Air Pressure Difference or ASTM E 547-00 Water Penetration of Exterior Windows, Skylights, Doors, and Curtain Walls by Cyclic Static Air Pressure Difference | obc2019_divb | Div B | 5.10.4.5.(2) | 5.10.4.5. Water Penetration | Except as provided in Sentence (4), other fenestration assemblies and their components shall resist water penetration when tested in accordance with,(a) ASTM E331, "Water Penetration of Exterior Windows, Skylights, Doors, and Curtain Walls by Uniform Static Air Pressure Difference", or (b) ASTM E547, "Water Penetration of Exterior Windows, Skylights, Doors, and Curtain Walls by Cyclic Static Air Pressure Difference". | Common Sentence | No
2015 | ON | NBC | Div B | 5.9.3.5.(3) | 5.9.3.5. Water Penetration | Tests referred to in Sentence 5.9.3.5.(2) shall be carried out at the driving rain wind pressure as calculated in accordance with CSA A440S1-17 Canadian Supplement to AAMA/WDMA/CSA 101/I.S.2/A440-11, NAFS - North American Fenestration Standard/Specification for Windows, Doors, and Skylights (See Note A-5.9.3.5.(3).) | obc2019_divb | Div B | 5.10.4.5.(3) | 5.10.4.5. Water Penetration | Testing described in Sentence (2) shall be carried out at the driving rain wind pressure as calculated in accordance with CSA A440S1, "Canadian Supplement to AAMA/WDMA/CSA 101/I.S.2/A440-11, NAFS - North American Fenestration Standard/Specification for Windows, Doors, and Skylights". | Common Sentence | No
2015 | ON | NBC | Div B | 5.9.3.5.(4) | 5.9.3.5. Water Penetration | The following systems need not comply with Sentence 5.9.3.5.(2): (a) interior windows and interior doors, (b) vehicular access doors (garage doors), (c) storm windows and storm doors, (d) commercial entrance systems, (e) revolving doors, (f) smoke and relief air vents, (g) site-built door systems, and (h) commercial steel doors. | obc2019_divb | Div B | 5.10.4.5.(4) | 5.10.4.5. Water Penetration | The following need not comply with Sentence (2): (a) interior windows and interior doors, (b) vehicular access doors, including garage doors, (c) storm windows and storm doors, (d) commercial entrance systems, (e) revolving doors, (f) smoke and relief air vents, (g) site-built door systems, and (h) commercial steel doors. | Common Sentence | No
2015 | ON | NBC | Div B | 5.9.4.1.(1) | 5.9.4.1. Structural Loads, Heat Transfer, Air Leakage, Vapour Diffusion and Water Penetration | Exterior insulation finish systems and their components shall comply with (a) Subsection 5.1.4 and Sections 5.3 to 5.6, and (b) CAN/ULC-S716.1-12 Exterior Insulation and Finish Systems (EIFS) - Materials and Systems where covered in the scope of that standard. | obc2019_divb | Div B | 5.10.3.1.(1) | 5.10.3.1. Applicable Standards | Where exterior insulation finish systems are installed, the systems and their components shall conform to,(a) Article 5.1.4.1. and Sections 5.3. to 5.6., and (b) CAN/ULC-S716.1, "Exterior Insulation and Finish Systems (EIFS)" Materials and Systems", if the systems are covered in the scope of that standard. | Common Sentence | No
2015 | ON | NBC | Div B | 6.2.1.1.(1) | Good Engineering Practice | Heating, ventilating and air-conditioning systems, including mechanical refrigeration equipment, shall be designed, constructed and installed in conformance with good engineering practice such as that described in, but not limited to, the ASHRAE Handbooks and Standards, the HRAI SAR-G1 HRAI Digest the Hydronics Institute Manuals, the NFPA Standards, the SMACNA Manuals, ACGIH 28th Edition Industrial Ventilation: A Manual of Recommended Practice for Design published by the ACGIH, CSA B214-16 Installation Code for Hydronic Heating Systems CSA CAN/CSA-Z317.2-10 Special Requirements for Heating, Ventilation, and Air-Conditioning (HVAC) Systems in Health Care Facilities and EPA 625/R-92/016 (1994) Radon Prevention in the Design and Construction of Schools and Other Large Buildings | obc2019_divb | Div B | 6.2.1.1.(1) | 6.2.1.1. Good Engineering Practice | Heating, ventilating and air-conditioning systems, including related mechanical refrigeration systems, shall be designed, constructed and installed to conform to good engineering practice appropriate to the circumstances such as described in,(a) the ASHRAE Handbooks as follows: (i) Fundamentals, (ii) Refrigeration, (iii) HVAC Applications, (iv) HVAC Systems and Equipment, and (v) ANSI/ASHRAE/IESNA 90.1, "Energy Standard for Buildings Except Low-Rise Residential Buildings", (b) CSA F280, "Determining the Required Capacity of Residential Space Heating and Cooling Appliances", and the outside winter design temperatures shall conform to MMAH Supplementary Standard SB-1, "Climatic and Seismic Data", (c) CAN/CSA-F326-M, "Residential Mechanical Ventilation Systems", (d) the NFPA Fire Codes, (e) the HRAI Digest, (f) the Hydronics Institute Manuals, (g) the SMACNA Manuals, (h) ACGIH, "Industrial Ventilation Manual", (i) CAN/CSA-Z317.2, "Special Requirements for Heating, Ventilation, and Air Conditioning (HVAC) Systems in Health Care Facilities", (j) reserved, (k) CCBFC NRCC 56191, "National Energy Code of Canada for Buildings", and (l) EPA/625/R-92/016, "Radon Prevention in the Design and Construction of Schools and Other Large Buildings". | Common Sentence | Yes | Design and Installation
2015 | ON | NBC | Div B | 6.2.1.2.(1) | Outdoor Design Conditions | The outdoor conditions to be used in designing heating, ventilating and air-conditioning systems shall be determined in conformance with Subsection 1.1.3. | obc2019_divb | Div B | 6.2.1.7.(1) | 6.2.1.7. Outside Design Conditions | The outside conditions to be used in designing heating, ventilating and air-conditioning systems shall be determined in conformance with MMAH Supplementary Standard SB-1, "Climatic and Seismic Data". | Common Sentence | Yes | Design and Installation
2015 | ON | NBC | Div B | 6.2.1.3.(1) | Expansion Contraction and System Pressure | Heating and cooling systems shall be designed to allow for expansion and contraction of the heat transfer fluid and to maintain the system pressure within the rated working pressure limits of all components of the system. | obc2019_divb | Div B | 6.2.1.9.(1) | 6.2.1.9. Expansion, Contraction and System Pressure | Heating and cooling systems shall be designed to allow for expansion and contraction of the heat transfer fluid and to maintain the system pressure within the rated working pressure limits of all components of the system | Common Sentence | No | Design and Installation
2015 | ON | NBC | Div B | 6.2.1.4.(1) | Structural Movement (See Note A-6.2.1.4.) | Mechanical systems and equipment shall be designed and installed to accommodate the maximum relative structural movement provided for in the construction of the building. | obc2019_divb | Div B | 6.2.1.3.(1) | 6.2.1.3. Structural Movement | Mechanical systems and equipment shall be designed and installed to accommodate the maximum relative structural movement provided for in the construction of the building | Common Sentence | No | Design and Installation
2015 | ON | NBC | Div B | 6.2.1.5.(1) | 6.2.1.5. Installation Standards | Except as provided in Articles 6.9.4.2. and Article 6.3.1.5., the installation of heating and air-conditioning equipment, including mechanical refrigeration equipment, and including provisions for mounting, clearances and air supply, shall conform to appropriate provincial or territorial requirements or, in the absence of such requirements, to the requirements of CSA B51-14 Boiler, Pressure Vessel, and Pressure Piping Code CSA B52-13 Mechanical Refrigeration Code CSA B139-09 Installation Code for Oil-Burning Equipment CSA B149.1-10 Natural Gas and Propane Installation Code CSA B365-17 Installation Code for Solid-Fuel-Burning Appliances and Equipment or CSA C22.1-12 Canadian Electrical Code, Part I | obc2019_divb | Div B | 6.2.1.4.(5) | 6.2.1.4. Installation Standards | The design and installation of solid fuel-burning stoves, ranges and space heaters, including the requirements for combustion air, shall conform to the requirements of CSA B365, “Installation Code for Solid-Fuel-Burning Appliances and Equipment” and the manufacturer’s installation instructions. | Common Sentence | No | Design and Installation
2015 | ON | NBC | Div B | 6.2.1.6.(1) | Installation - General | Equipment requiring periodic maintenance and forming part of a heating, ventilating or air-conditioning system shall be installed with provisions for access for inspection, maintenance, repair and cleaning. (See Note A-6.2.1.6.(1).) | obc2019_divb | Div B | 6.2.1.8.(1) | 6.2.1.8. Installation- General | Equipment requiring periodic maintenance and forming part of a heating, ventilating or air-conditioning system shall be installed with provision for access for inspection, maintenance, repair and cleaning. (See Appendix A.) | Common Sentence | No | Design and Installation
2015 | ON | NBC | Div B | 6.2.1.6.(2) | Installation -General | Mechanical equipment shall be provided with guards so as to prevent injury. | obc2019_divb | Div B | 6.2.1.8.(2) | 6.2.1.8. Installation - General | Mechanical equipment shall be provided with guards to prevent injury. | Common Sentence | No | Design and Installation
2015 | ON | NBC | Div B | 6.2.1.6.(3) | Installation -General | Heating, ventilating or air-conditioning systems shall be protected from freezing if they may be adversely affected by freezing temperatures. | obc2019_divb | Div B | 6.2.1.8.(3) | 6.2.1.8. Installation - General | Heating, ventilating or air-conditioning systems shall be protected from freezing if they may be adversely affected by freezing temperatures | Common Sentence | No | Design and Installation
2015 | ON | NBC | Div B | 6.2.1.7.(1) | Asbestos | Asbestos shall not be used in HVAC systems and equipment. | obc2019_divb | Div B | 6.2.1.10.(1) | 6.2.1.10. Asbestos | Asbestos shall not be used in heating, ventilating or air-conditioning systems or equipment. | Common Sentence | No | Design and Installation
2015 | ON | NBC | Div B | 6.2.2.1.(1) | Applicable Standard | The design, construction, installation and alteration of every indoor incinerator shall conform to NFPA 82 Incinerators and Waste and Linen Handling Systems and Equipment | obc2019_divb | Div B | 6.2.6.1.(1) | 6.2.6.1. Applicable Standard | The design, construction, installation and material alteration of every indoor incinerator shall conform to NFPA 82, "Incinerators and Waste and Linen Handling Systems and Equipment". | Common Sentence | No
2015 | ON | NBC | Div B | 6.2.3.1.(1) | Solid Fuel Storage Bins | A storage bin for solid fuel shall not be located above a sewer opening or drain opening. | obc2019_divb | Div B | 6.2.11.1.(3) | 6.2.11.1. Storage Bins | A storage bin for solid fuel shall not be located above a sewer opening or drain opening | Common Sentence | No | Storage Bins
2015 | ON | NBC | Div B | 6.2.3.1.(2) | Solid Fuel Storage Bins | Storage bins for solid fuel shall be designed and constructed so that the air temperature in the bin or the surface temperature of any part of the floor or walls is below 50°C. | obc2019_divb | Div B | 6.2.11.1.(4) | 6.2.11.1. Storage Bins | Storage bins for solid fuel shall be designed and constructed so that the air temperature in the bin or the surface temperature of any part of the floor or walls is below 50°C. | Common Sentence | No | Storage Bins
2015 | ON | NBC | Div B | 6.3.1.1.(1) | Required Ventilation | Except as provided in Sentence 6.3.1.1.(3), all buildings shall be ventilated in accordance with this Part. | obc2019_divb | Div B | 6.2.2.1.(1) | 6.2.2.1. Required Ventilation | Except as provided in Sentence (3), all buildings shall be ventilated in accordance with this Part. | Common Sentence | No | Ventilation
2015 | ON | NBC | Div B | 6.3.1.1.(2) | Required Ventilation | Except in storage garages covered by Article 6.3.1.4., the rates at which outdoor air is supplied in buildings by ventilation systems shall be not less than the rates required by ASHRAE ANSI/ASHRAE 62-2001 Ventilation for Acceptable Indoor Air Quality (except Addendum n). | obc2019_divb | Div B | 6.2.2.1.(2) | 6.2.2.1. Required Ventilation | Except in storage garages and repair garages covered by Article 6.2.2.3., the rates at which outdoor air is supplied in buildings by ventilation systems shall be not less than the rates required by ANSI/ASHRAE 62.1, "Ventilation for Acceptable Indoor Air Quality". (See Appendix A.) | Common Sentence | Yes | Ventilation
2015 | ON | NBC | Div B | 6.3.1.1.(3) | Required Ventilation | Self-contained heating-season mechanical ventilation systems serving only one dwelling unit shall comply with (a) this Part, or (b) Subsection 9.32.3. | obc2019_divb | Div B | 6.2.2.1.(3) | 6.2.2.1. Required Ventilation | Self-contained mechanical ventilation systems serving a house or an individual dwelling unit shall conform to, (a) this Part, or (b) Subsection 9.32.3. | Common Sentence | Yes | Ventilation
2015 | ON | NBC | Div B | 6.3.1.2.(1) | Crawl Spaces and Attic or Roof Spaces | Unconditioned and unoccupied crawl spaces and unconditioned and unoccupied attic or roof spaces shall be ventilated by natural or mechanical means as required by Part 5. (See Note A-6.3.1.2.(1).) |  | Div B | 6.2.2.7.(1) | 6.2.2.7 Crawl Spaces and Attic or Roof Spaces | Every crawl space and every attic or roof space shall be ventilated by natural or mechanical means. | Common Sentence | No | Ventilation
2015 | ON | NBC | Div B | 6.3.1.3.(1) | Natural Ventilation | Except as permitted by Sentence 6.3.1.3.(2), the ventilation required by Article 6.3.1.1. shall be provided by mechanical ventilation, except that it can be provided by natural ventilation or a combination of natural and mechanical ventilation in buildings of other than residential occupancy having an occupant load of not more than one person per 40 m2 during normal use, buildings of industrial occupancy where the nature of the processes contained therein permits or requires the use of large openings in the building envelope even during the winter, and seasonal buildings not intended to be occupied during the winter. | obc2019_divb | Div B | 6.2.2.2.(1) | 6.2.2.2. Natural Ventilation | Except as permitted by Sentence (2), the ventilation required by Article 6.2.2.1. shall be provided by mechanical ventilation except that it can be provided by natural ventilation or a combination of natural and mechanical ventilation in,(a) buildings of other than residential occupancy having an occupant load of not more than one person per 40 m² during normal use, (b) buildings of industrial occupancy where the nature of the process contained in them permits or requires the use of large openings in the building envelope even during the winter, or (c) seasonal buildings not intended to be occupied during the winter. | Common Sentence | No | Ventilation
2015 | ON | NBC | Div B | 6.3.1.3.(2) | Natural Ventilation | Where climatic conditions permit, buildings containing occupancies other than residential occupancies may be ventilated by natural ventilation methods in lieu of mechanical ventilation where engineering data demonstrates that such a method will provide the required ventilation for the type of occupancy. | obc2019_divb | Div B | 6.2.2.2.(2) | 6.2.2.2. Natural Ventilation | Where climatic conditions permit, buildings containing occupancies other than residential occupancies, may be ventilated by natural ventilation methods in lieu of mechanical ventilation where engineering data demonstrates that such a method will provide the required ventilation for the type of occupancy. | Common Sentence | No | Ventilation
2015 | ON | NBC | Div B | 6.3.1.4.(1) | Ventilation of Storage Garages | Except as provided in Sentences 6.3.1.4.(4) and 6.3.1.4.(6), an enclosed storage garage for five or more motor vehicles shall have a mechanical ventilation system designed to limit the concentration of carbon monoxide to not more than 100 parts per million parts of air, limit the concentration of nitrogen dioxide to not more than 3 parts per million parts of air, where the majority of the vehicles stored are powered by diesel-fuelled engines, or provide, during operating hours, a continuous supply of outdoor air at a rate of not less than 3.9 L/s for each square metre of floor area (see Article 3.3.1.20.). | obc2019_divb | Div B | 6.2.2.3.(1) | 6.2.2.3. Ventilation of Storage and Repair Garages | Except as provided in Sentences (4) and (6), an enclosed storage garage shall have a mechanical ventilation system designed to,(a) limit the concentration of carbon monoxide to not more than 100 parts per million of air when measured between 900 mm and 1‚ 800 mm from the floor, where the majority of the vehicles stored are powered by gasoline fuelled engines, (b) limit the concentration of nitrogen dioxide to not more than 3 parts per million parts of air when installed in accordance with manufacturer's instructions, where the majority of the vehicles stored are powered by diesel fuelled engines, or (c) provide, during operating hours, a continuous supply of outdoor air at a rate of not less than 3.9 L/s for each square metre of floor area. (See Appendix A.) | Common Sentence | Yes | Ventilation
2015 | ON | NBC | Div B | 6.3.1.4.(2) | Ventilation of Storage Garages | Mechanical ventilation systems provided in accordance with Sentence 6.3.1.4.(1) shall be controlled by carbon monoxide monitoring devices, and systems provided in accordance with Sentence 6.3.1.4.(1) shall be controlled by nitrogen dioxide or other acceptable monitoring devices. (See Note A-6.3.1.4.(2).) | obc2019_divb | Div B | 6.2.2.3.(2) | 6.2.2.3. Ventilation of Storage and Repair Garages | Mechanical ventilation systems provided in accordance with Clause (1)(a) shall be controlled automatically by carbon monoxide monitoring devices and systems provided in accordance with Clause (1)(b) shall be controlled automatically by nitrogen dioxide or other acceptable monitoring devices, located so as to provide full protection throughout the storage garage. (See Appendix A.) | Common Sentence | Yes | Ventilation
2015 | ON | NBC | Div B | 6.3.1.4.(3) | Ventilation of Storage Garages | Mechanical ventilation systems provided in accordance with Sentence 6.3.1.4.(1) shall be designed such that the pressure in the storage garage is less than the pressure in adjoining buildings of other occupancy, or in adjacent portions of the same building having a different occupancy. | obc2019_divb | Div B | 6.2.2.3.(3) | 6.2.2.3. Ventilation of Storage and Repair Garages | Mechanical ventilation systems provided in accordance with Sentence (1) shall be designed such that the pressure in the storage garage is less than the pressure in adjoining buildings of other occupancy, or in adjacent portions of the same building having a different occupancy. | Common Sentence | No | Ventilation
2015 | ON | NBC | Div B | 6.3.1.4.(4) | Ventilation of Storage Garages | In storage garages subject to the requirements of Sentences 6.3.1.4.(1) and 6.3.1.4.(2), where motor vehicles are parked by mechanical means, the ventilation requirements may be reduced by one half. | obc2019_divb | Div B | 6.2.2.3.(4) | 6.2.2.3. Ventilation of Storage and Repair Garages | In storage garages subject to the requirements of Sentence (1), where motor vehicles are parked by mechanical means, the ventilation requirements may be reduced by one half. | Common Sentence | Yes | Ventilation
2015 | ON | NBC | Div B | 6.3.1.4.(5) | Ventilation of Storage Garages | Except as provided in Sentence 6.3.1.4.(6), ticket and attendant booths of storage garages shall be pressurized with a supply of uncontaminated air. | obc2019_divb | Div B | 6.2.2.3.(5) | 6.2.2.3. Ventilation of Storage and Repair Garages | Except as provided in Sentence (6), ticket and attendant booths of storage garages shall be pressurized with a supply of outdoor air. | Common Sentence | Yes | Ventilation
2015 | ON | NBC | Div B | 6.3.1.4.(6) | Ventilation of Storage Garages | The requirements of Sentences 6.3.1.4.(1) to 6.3.1.4.(5) shall not apply to open-air storeys in a storage garage. | obc2019_divb | Div B | 6.2.2.3.(6) | 6.2.2.3. Ventilation of Storage and Repair Garages | The requirements of Sentences (1) to (5) shall not apply to open-air storeys in a storage garage. | Common Sentence | No | Ventilation
2015 | ON | NBC | Div B | 6.3.1.5.(1) | Heat Recovery Ventilators | Heat recovery ventilators with rated capacities of not less than 25 L/s and not more than 200 L/s shall be installed in accordance with Subsection 9.32.3 | obc2019_divb | Div B | 6.2.1.6.(1) | 6.2.1.6. Heat Recovery Ventilators | Except as provided in Sentence (2), heat recovery ventilators with rated capacities of not less than 25 L/s and not more than 200 L/s shall be installed in accordance with Article 9.32.3.11. | Common Sentence | No | Ventilation
2015 | ON | NBC | Div B | 6.3.1.6.(1) | Indoor Air Contaminants | Air contaminants of concern that are released within buildings shall be removed insofar as is possible at their points of origin, and not be permitted to accumulate in concentrations greater than those permitted by applicable provincial or territorial requirements or, in the absence of such requirements, by good engineering practice such as that described in the publications listed in Sentence 6.2.1.1.(1), measured using the methodology described therein. | obc2019_divb | Div B | 6.2.2.4.(1) | 6.2.2.4. Indoor Air Contaminants (See Appendix A.) | Air contaminants released within buildings shall be removed insofar as possible at their points of origin and shall not be permitted to accumulate in concentrations greater than permitted by good engineering practice appropriate to the circumstances such as that described in the publications listed in Article 6.2.1.1." (See Appendix A.) | Common Sentence | Yes | Ventilation
2015 | ON | NBC | Div B | 6.3.1.6.(2) | Indoor Air Contaminants | Systems serving spaces that contain sources of contamination and systems serving other occupied parts of the building but located in or running through spaces that contain sources of contamination shall be designed in such a manner as to prevent the spread of such contamination to other occupied parts of the building. | obc2019_divb | Div B | 6.2.2.4.(2) | 6.2.2.4. Indoor Air Contaminants (See Appendix A.) | Systems serving spaces that contain sources of contamination and systems serving other occupied parts of the building but located in or running through spaces that contain sources of contamination shall be designed in such a manner as to prevent the spread of such contamination to other occupied parts of the building. (See Appendix A.) | Common Sentence | No | Ventilation
2015 | ON | NBC | Div B | 6.3.1.6.(3) | Indoor Air Contaminants | Heating, ventilating and air-conditioning systems shall be designed to minimize the growth and spread of bio-contaminants. | obc2019_divb | Div B | 6.2.2.4.(3) | 6.2.2.4. Indoor Air Contaminants (See Appendix A.) | Heating, ventilating and air-conditioning systems shall be designed to minimize growth and spread of bio-contaminants. | Common Sentence | No | Ventilation
2015 | ON | NBC | Div B | 6.3.1.7.(1) | Commercial Cooking Equipment | Except as provided in Article 3.6.3.5 (2)., systems for the ventilation of commercial cooking equipment shall be designed, constructed and installed to conform to NFPA 96 Ventilation Control and Fire Protection of Commercial Cooking Operations | obc2019_divb | Div B | 6.2.2.6.(1) | 6.2.2.6. Commercial Cooking Equipment | Except as provided in Article 3.6.3.5., all commercial cooking equipment shall be provided with ventilation systems designed, constructed and installed to conform to NFPA 96, "Ventilation Control and Fire Protection of Commercial Cooking Operations". | Common Sentence | No | Ventilation
2015 | ON | NBC | Div B | 6.3.2.1.(1) | Application | This Subsection applies to the design, construction and installation of air duct distribution systems serving heating, ventilating and air-conditioning systems other than those in dwelling units covered by Part 9. | obc2019_divb | Div B | 6.2.3.1.(1) | 6.2.3.1. Application | Except as provided in Sentence (2), this Subsection applies to the design, construction and installation of air duct distribution systems serving heating, ventilating and air-conditioning systems. | Common Sentence | No | Ventilation
2015 | ON | NBC | Div B | 6.3.2.1.(1) | Application | This Subsection applies to the design, construction and installation of air duct distribution systems serving heating, ventilating and air-conditioning systems other than those in dwelling units covered by Part 9. | obc2019_divb | Div B | 6.2.3.1.(2) | 6.2.3.1. Application | This Subsection does not apply to the design, construction and installation of air duct distribution systems serving heating, ventilating and air-conditioning systems that serve a house or an individual dwelling unit within the scope of Part 9. | Common Sentence | No | Air Duct Systems
2015 | ON | NBC | Div B | 6.3.2.1.(1) | Application | This Subsection applies to the design, construction and installation of air duct distribution systems serving heating, ventilating and air-conditioning systems other than those in dwelling units covered by Part 9. | obc2019_divb | Div B | 6.2.4.1.(1) | 6.2.4.1. Application | The requirements of this Subsection apply to the design, construction and installation of air duct distribution systems serving heating, ventilating and air-conditioning systems that serve a house or an individual dwelling unit within the scope of Part 9. | Common Sentence | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 6.3.2.10.(1) | Exhaust Ducts and Outlets | Except as provided in Sentence 6.3.2.10.(2), exhaust ducts of non-mechanical ventilating systems serving separate rooms or spaces shall not be combined. | obc2019_divb | Div B | 6.2.3.8.(1) | 6.2.3.8. Exhaust Ducts and Outlets | Except as provided in Sentence (2), exhaust ducts of nonmechanical ventilating systems serving separate rooms or spaces shall not be combined. | Common Sentence | No | Air Duct Systems
2015 | ON | NBC | Div B | 6.3.2.10.(10) | Exhaust Ducts and Outlets | Except as provided in Sentence 6.3.2.10.(12) and except for self-contained systems serving individual dwelling units, exhaust ducts serving rooms containing water closets, urinals, basins, showers or slop sinks shall be independent of other exhaust ducts. | obc2019_divb | Div B | 6.2.3.8.(8) | 6.2.3.8. Exhaust Ducts and Outlets | Except as provided in Sentence (10) and except for self-contained systems serving individual dwelling units, exhaust ducts serving rooms containing water closets, urinals, basins, showers or slop sinks shall be independent of other exhaust ducts. | Common Sentence | No | Air Duct Systems
2015 | ON | NBC | Div B | 6.3.2.10.(11) | Exhaust Ducts and Outlets | Except as provided in Sentence 6.3.2.10.(12) and except for self-contained systems serving individual dwelling units, exhaust ducts serving rooms containing residential cooking equipment shall be independent of other exhaust ducts. | obc2019_divb | Div B | 6.2.3.8.(9) | 6.2.3.8. Exhaust Ducts and Outlets | Except as provided in Sentence (10) and except for self-contained systems serving individual dwelling units, exhaust ducts serving rooms containing residential cooking equipment shall be independent of other exhaust ducts. | Common Sentence | No | Air Duct Systems
2015 | ON | NBC | Div B | 6.3.2.10.(12) | Exhaust Ducts and Outlets | Two or more exhaust systems described in Sentences 6.3.2.10.(10) and 6.3.2.10.(11) may be interconnected or connected with exhaust ducts serving other areas of the building, provided the connections are made at the inlet of an exhaust fan, and all interconnected systems are equipped with suitable back pressure devices to prevent the passage of odours from one system to another when the fan is not in operation, or the exhaust ducts discharge to a shaft that is served by an exhaust fan having a capacity that is equal to or greater than the combined capacity of the exhaust fans discharging to the plenum multiplied by the operation diversity factor, provided that the exhaust fan serving the shaft operates continuously (see Note A-6.3.2.10.(12)(b)). | obc2019_divb | Div B | 6.2.3.8.(10) | 6.2.3.8. Exhaust Ducts and Outlets | Two or more exhaust systems described in Sentences (8) and (9) may be interconnected or connected with exhaust ducts serving other areas of the building provided,(a) the connections are made at the inlet of an exhaust fan, and all interconnected systems are equipped with suitable back pressure devices to prevent passage of odours from one system to another when the fan is not in operation, or (b) the exhaust ducts discharge to a shaft that is served by an exhaust fan having a capacity that is equal to or greater than the combined capacity of the exhaust fans discharging to the plenum multiplied by the operation diversity factor, provided that the exhaust fan serving the shaft operates continuously. (See Appendix A.) | Common Sentence | No | Air Duct Systems
2015 | ON | NBC | Div B | 6.3.2.10.(13) | Exhaust Ducts and Outlets | Where exhaust ducts containing air from conditioned spaces pass through or are adjacent to unconditioned spaces, the ducts shall be constructed to prevent condensation from forming on the inside or outside of the ducts. | obc2019_divb | Div B | 6.2.3.8.(11) | 6.2.3.8. Exhaust Ducts and Outlets | Where exhaust ducts containing air from conditioned spaces pass through or are adjacent to unconditioned spaces, the ducts shall be constructed to prevent condensation from forming inside or outside of the ducts. | Common Sentence | No | Air Duct Systems
2015 | ON | NBC | Div B | 6.3.2.10.(2) | Exhaust Ducts and Outlets | Exhaust ducts of non-mechanical ventilating systems serving similar occupancies may be combined immediately below the point of final delivery to the outdoors, such as at the base of a roof ventilator. | obc2019_divb | Div B | 6.2.3.8.(2) | 6.2.3.8. Exhaust Ducts and Outlets | Exhaust ducts of nonmechanical ventilating systems serving similar occupancies may be combined immediately below the point of final delivery to the outside, such as at the base of a roof ventilator. | Common Sentence | No | Air Duct Systems
2015 | ON | NBC | Div B | 6.3.2.10.(5) | Exhaust Ducts and Outlets | Except as permitted in Sentence 6.3.2.10.(6), exhaust systems shall discharge directly to the outdoors. (See Note A-6.3.2.10.(5).) | obc2019_divb | Div B | 6.2.3.8.(5) | 6.2.3.8. Exhaust Ducts and Outlets | Except as permitted in Sentence (6), exhaust systems shall discharge directly to the outdoors. (See Appendix A.) | Common Sentence | No | Air Duct Systems
2015 | ON | NBC | Div B | 6.3.2.10.(7) | Exhaust Ducts and Outlets | Exhaust ducts connected to laundry-drying equipment shall be independent of other exhaust ducts, accessible for inspection and cleaning, and constructed of a smooth corrosion-resistant material. | obc2019_divb | Div B | 6.2.3.8.(7) | 6.2.3.8. Exhaust Ducts and Outlets | Exhaust ducts connected to laundry drying equipment shall be,(a) independent of other exhaust ducts, (b) designed and installed so that the entire duct can be cleaned, and (c) constructed of smooth corrosion-resistant material. (See Appendix A.) | Common Sentence | No | Air Duct Systems
2015 | ON | NBC | Div B | 6.3.2.10.(8) | Exhaust Ducts and Outlets | Where collective venting of multiple installations of laundry-drying equipment is used, the ventilation system shall be connected to a common exhaust duct that is vented by one central exhaust fan and incorporates one central lint trap, include an interlock to activate the central exhaust fan when laundry-drying equipment is in use, and be provided with make-up air. | obc2019_divb | Div B | 6.2.3.8.(18) | 6.2.3.8. Exhaust Ducts and Outlets | Where collective venting of multiple installations of laundry-drying equipment is used, the ventilation system shall, (a) be connected to a common exhaust duct that is vented by one central exhaust fan, (b) incorporate one central lint trap, (c) include an interlock to activate the central exhaust fan when laundry-drying equipment is in use, and (d) be provided with make-up air. (See Appendix Note A-6.2.3.8.(7)) | Common Sentence | No | Air Duct Systems
2015 | ON | NBC | Div B | 6.3.2.12.(1) | Underground Ducts | Underground ducts shall be constructed and installed to provide interior drainage from and access to all low points, not be connected directly to a sewer, and be installed and constructed of materials recommended by ASHRAE and SMACNA Standards and HRAI Manuals. | obc2019_divb | Div B | 6.2.3.5.(1) | 6.2.3.5. Underground Ducts | Underground ducts shall,(a) be constructed and installed with a slope to provide interior drainage to all low points, (b) not be connected directly to a sewer, and (c) be installed and constructed of materials in conformance with ASHRAE Handbooks, SMACNA Manuals and the HRAI Digest. | Common Sentence | Yes | Air Duct Systems
2015 | ON | NBC | Div B | 6.3.2.12.(1) | Underground Ducts | Underground ducts shall be constructed and installed to provide interior drainage from and access to all low points, not be connected directly to a sewer, and be installed and constructed of materials recommended by ASHRAE and SMACNA Standards and HRAI Manuals. | obc2019_divb | Div B | 6.2.4.3.(13) | 6.2.4.3. Construction and Installation of Ducts and Plenums | Underground ducts shall, (a) be constructed and installed with a slope to provide interior drainage to all low points, (b) not be connected directly to a sewer, and (c) be installed and constructed of materials in conformance with ASHRAE Handbooks, SMACNA Manuals and the HRAI Digest. | Common Sentence | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 6.3.2.12.(2) | Underground Ducts |  | obc2019_divb | Div B | 6.2.3.5.(2) | 6.2.3.5. Underground Ducts |  | Common Sentence | No | Air Duct Systems
2015 | ON | NBC | Div B | 6.3.2.12.(2) | Underground Ducts |  | obc2019_divb | Div B | 6.2.4.3.(14) | 6.2.4.3. Construction and Installation of Ducts and Plenums |  | Common Sentence | No | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 6.3.2.13.(1) | Filters | Air filters for air duct systems shall conform to the requirements for Class 2 air filter units as described in ULC CAN/ULC-S111 Fire Tests for Air Filter Units | obc2019_divb | Div B | 6.2.3.13.(1) | 6.2.3.13. Filters and Odour Removal Equipment | Air filters for air duct systems shall conform to the requirements for Class 2 air filter units as described in CAN/ULC-S111, "Fire Tests for Air Filter Units". | Common Sentence | No | Ventilation
2015 | ON | NBC | Div B | 6.3.2.13.(2) | Filters | When electrostatic-type filters are used, they shall be installed so as to ensure that the electric circuit is automatically de-energized when filter access doors are opened or, in dwelling units, when the furnace circulation fan is not operating. | obc2019_divb | Div B | 6.2.3.13.(2) | 6.2.3.13. Filters and Odour Removal Equipment | When electrostatic-type filters are used, they shall be installed so as to ensure that the electric circuit is automatically de-energized when filter access doors are opened and, in dwelling units, when the system circulating fan is not operating. | Common Sentence | Yes | Ventilation
2015 | ON | NBC | Div B | 6.3.2.15.(1) | Evaporative Cooling Towers, Evaporative Fluid Coolers and Evaporative | Discharge from evaporative cooling towers to ventilation air intakes shall comply with Sentence 6.3.2.9.(2), and CSA CAN/CSA-Z317.2-10 Special Requirements for Heating, Ventilation, and Air-Conditioning (HVAC) Systems in Health Care Facilities | obc2019_divb | Div B | 6.2.3.14.(1) | 6.2.3.14. Evaporative Cooling Towers, Evaporative Fluid Coolers | Discharge from evaporative cooling towers to ventilation air intakes shall comply with CAN/CSA-Z317.2, "Special Requirements for Heating, Ventilation, and Air Conditioning (HVAC) Systems in Health Care Facilities". | Common Sentence | Yes | Ventilation
2015 | ON | NBC | Div B | 6.3.2.15.(2) | Evaporative Cooling Towers, Evaporative Fluid Coolers and Evaporative |  | obc2019_divb | Div B | 6.2.3.14.(2) | 6.2.3.14. Evaporative Cooling Towers, Evaporative Fluid Coolers |  | Common Sentence | No | Ventilation
2015 | ON | NBC | Div B | 6.3.2.15.(4) | Evaporative Cooling Towers, Evaporative Fluid Coolers and Evaporative | Water treatment equipment for biological growth control shall be provided in accordance with Sub-Section 7.6.2. of ASHRAE Guideline 12, “Minimizing the Risk of Legionellosis Associated with Building Water Systems.” | obc2019_divb | Div B | 6.2.3.14.(3) | 6.2.3.14. Evaporative Cooling Towers, Evaporative Fluid Coolers | Evaporative cooling towers, evaporative fluid coolers and evaporative condensers shall be provided with water treatment equipment for biological growth control in accordance with Subsection 7.6.2. of ASHRAE Guideline 12, "Minimizing the Risk of Legionellosis Associated with Building Water Systems". | Common Sentence | No | Ventilation
2015 | ON | NBC | Div B | 6.3.2.15.(6) | Evaporative Cooling Towers, Evaporative Fluid Coolers and Evaporative | Evaporative cooling towers, evaporative fluid coolers and evaporative condensers shall be provided with access ports, service platforms, fixed ladders and restraint connections to allow visual inspection, maintenance and testing. | obc2019_divb | Div B | 6.2.3.14.(4) | 6.2.3.14. Evaporative Cooling Towers, Evaporative Fluid Coolers | Evaporative cooling towers, evaporative fluid coolers and evaporative condensers shall be provided with access ports, service platforms, fixed ladders and restraint connections to allow visual inspection, maintenance and testing. | Common Sentence | No | Ventilation
2015 | ON | NBC | Div B | 6.3.2.16.(1) | Evaporative Air Coolers, Misters, Atomizers, | The filter and water evaporation medium of every air washer and evaporative air cooler enclosed within a building shall be made of noncombustible material. | obc2019_divb | Div B | 6.2.3.14A.(1) | 6.2.3.14A. Evaporative Cooling Sections, Evaporative Air Coolers, Misters, Atomizers, Air Washers andHumidifiers | The filter and water evaporation medium of every air washer and evaporative cooling section enclosed within a building shall be made of noncombustible material. | Common Sentence | No | Ventilation
2015 | ON | NBC | Div B | 6.3.2.16.(2) | Evaporative Air Coolers, Misters, Atomizers, | Sumps for air washers and evaporative air coolers shall be constructed and installed so that they can be flushed and drained. | obc2019_divb | Div B | 6.2.3.14A.(2) | 6.2.3.14A. Evaporative Cooling Sections, Evaporative Air Coolers, | Sumps for air washer and evaporative cooling sections shall be constructed and installed so that they can be flushed and drained. | Common Sentence | No | Ventilation
2015 | ON | NBC | Div B | 6.3.2.16.(3) | Evaporative Air Coolers, Misters, Atomizers, | Evaporative air coolers, misters, atomizers, air washers and humidifiers shall be designed in accordance with Sections 8 and 9 of ASHRAE Guideline 12, Minimizing the Risk of Legionellosis Associated with Building Water Systems | obc2019_divb | Div B | 6.2.3.14A.(3) | 6.2.3.14A. Evaporative Cooling Sections, Evaporative Air Coolers, | Evaporative air coolers, misters, atomizers, air washers and humidifiers shall be designed in accordance with Sections 8 and 9 of ASHRAE Guideline 12, "Minimizing the Risk of Legionellosis Associated with Building Water Systems". | Common Sentence | Yes | Ventilation
2015 | ON | NBC | Div B | 6.3.2.17.(1) | Fans and Associated Air-Handling Equipment | Fans for heating, ventilating and air-conditioning systems shall be located and installed so that their operation a) does not adversely affect the draft required for proper operation of fuel-fired appliances, and b) does not allow the air in the duct system to be contaminated by air or gases from the boiler room or furnace room. | obc2019_divb | Div B | 6.2.3.15.(1) | 6.2.3.15. Fans and Associated Air Handling Equipment | Fans for heating, ventilating and air-conditioning systems shall be located and installed so that their operation, (a) does not adversely affect the draft required for proper operation of fuel-fired appliances, and (b) does not allow the air in the air duct system to be contaminated by air or gases from the boiler-room or furnaceroom. | Common Sentence | No | Ventilation
2015 | ON | NBC | Div B | 6.3.2.17.(2) | Fans and Associated Air Handling Equipment |  | obc2019_divb | Div B | 6.2.3.15.(2) | 6.2.3.15. Fans and Associated Air Handling Equipment |  | Common Sentence | No | Ventilation
2015 | ON | NBC | Div B | 6.3.2.18.(1) | Vibration Isolation Connectors | Using text search: ROW 3016 AND 3017 combined (3.6.5.2.(1) and 3.6.5.2.(2) Excel National file// Vibration isolation connectors in air duct systems shall be noncombustible, except that combustible fabric connectors are permitted provided they, (a)do not exceed 250 mm in length, (b)comply with the flame-resistance requirements of CAN/ULC-S109, “Flame Tests of Flame-Resistant Fabrics and Films”, and (c)are not used in a location where they are exposed to heated air or radiation from heat sources that may cause the exposed surface to exceed a temperature of 120°C.// Row 4468 using S# Vibration isolation connectors in air duct systems shall comply with Article 3.6.5.2. | obc2019_divb | Div B | 6.2.3.16.(1) | Vibration Isolation Connectors | Vibration isolation connectors in air duct systems shall be noncombustible, except that combustible fabric connectors are permitted provided they, (a)do not exceed 250 mm in length, (b)comply with the flame-resistance requirements of CAN/ULC-S109, “Flame Tests of Flame-Resistant Fabrics and Films”, and (c)are not used in a location where they are exposed to heated air or radiation from heat sources that may cause the exposed surface to exceed a temperature of 120°C. | Common Sentence | No | Air Duct Systems
2015 | ON | NBC | Div B | 6.3.2.19.(1) | Tape | Tape used for sealing joints in air ducts, plenums and other parts of air duct systems shall comply with Article 3.6.5.3. | obc2019_divb | Div B | 6.2.3.17.(1) | Tape | Tape used for sealing joints in air ducts, plenums and other parts of air duct systems shall meet the flame-resistance requirements for fabric in CAN/ULC-S109, “Flame Tests of Flame-Resistant Fabrics and Films”. | Common Sentence | No | Air Duct Systems
2015 | ON | NBC | Div B | 6.3.2.2.(1) | Drain Pans | Dehumidifying cooling coil assemblies and condensate-producing heat exchangers shall be equipped with drain pans beneath them that are designed in accordance with Section 5.11, Drain Pans, of ASHRAE ANSI/ASHRAE 62.1, Ventilation for Acceptable Indoor Air Quality provided with an outlet that is piped to the outside of the airstream in a location where condensate can be eliminated, and installed so that water drains freely from the pan. | obc2019_divb | Div B | 6.2.3.1A.(1) | 6.2.3.1A. Drain Pans | Dehumidifying cooling coil assemblies and condensate-producing heat exchangers shall be equipped with drain pans beneath them that are,(a) designed in accordance with Section 5.11, Drain Pans, of ANSI/ASHRAE 62.1, "Ventilation for Acceptable Indoor Air Quality", (b) provided with an outlet that is piped to the outside of the airstream in a location where condensate can be eliminated, (c) installed so that water drains freely from the pan, and (d) provided with a drain line that is indirectly connected to a drainage system in accordance with Article 7.4.2.1. | Common Sentence | Yes | Air Duct Systems
2015 | ON | NBC | Div B | 6.3.2.3(2) | 6.3.2.3 Materials in Air Duct Systems | Ducts that are used in a location where they may be subjected to excessive moisture shall have no appreciable loss of strength when wet and shall be resistant to moisture induced corrosion. | obc2019_divb | Div B | 6.2.3.2.(5) | 6.2.3.2. Materials in Air Duct Systems | Materials in Sentences (1) to (4) installed in a location where they may be subjected to excessive moisture shall have no appreciable loss of strength when wet and shall be corrosion-resistant. | Common Sentence | No | Air Duct Systems
2015 | ON | NBC | Div B | 6.3.2.3.(3) | Materials in Air Duct Systems | All ductwork and fittings shall be constructed and installed as recommended in SMACNA Manuals and ASHRAE Standards. | obc2019_divb | Div B | 6.2.3.2.(6) | 6.2.3.2. Materials in Air Duct Systems | All ductwork and fittings shall be constructed and installed in conformance with SMACNA Manuals and ASHRAE Handbooks. | Common Sentence | No | Air Duct Systems
2015 | ON | NBC | Div B | 6.3.2.3.(4) | Materials in Air Duct Systems | All duct materials shall be suitable for exposure to the temperature and humidity of the air being carried and shall be resistant to corrosion caused by contaminants in the air being conveyed in the duct. | obc2019_divb | Div B | 6.2.3.2.(7) | 6.2.3.2. Materials in Air Duct Systems | All duct materials and fittings shall be,(a) suitable for exposure to the temperature and humidity of the air being conveyed, and (b) resistant to corrosion due to contaminants in the air being conveyed in the duct. | Common Sentence | No | Air Duct Systems
2015 | ON | NBC | Div B | 6.3.2.6.(1) | Clearance of Ducts and Plenums | The,clearance of ducts and plenums from comustible plenums shall comply with Article 3.6.5.6. The clearance of furnace plenums from combustible material shall conform to the requirements of the appropriate standards referenced in Sentence 6.2.1.5.(1). If the plenum clearance required in accordance with Sentence (1) is not more than 75mm, the clearance between a supply duct and combustible material shall be not less than (a) therequired plenum clearance within a horizontal distance of 450 mm from the plenum, and (b) 12 mm at a horizontal distance of 450 mm or more from the plenum, except that this clearance is permitted to be reduced to zero beyond a bend or offset in the duct sufficiently large to shield the remainder of the supply duct from direct radiation from the furnace heat exchanger. (See Note A-3.6.5.6.(2).) If the plenum clearance required in accordance with Sentence (1) is more than 75 mm but not more than 150 mm, the clearance between a supply duct and combustible material shall be not less than (a) the required plenum clearance within a horizontal distance of 800 mm from the plenum, and (b) 12 mm at a horizontal distance of 1 800 mm or more from the plenum, except that this distance is permitted to be reduced to zero beyond a bend or offset in the duct sufficiently large to shield the remainder of the supply duct from direct radiation from the furnace heat exchanger. (See Note A-3.6.5.6.(3).) If the plenum clearance required in accordance with Sentence (1) is more than 150 mm, the clearance between a supply duct and combustible material shall be not less than (a) the required plenum clearance within a horizontal distance of 1 000 mm from the plenum, (b) 150 mm within a horizontal distance between 1 000 mm and 1 800 mm from the plenum, and (c) 25 mm at a horizontal distance of 1 800 mm or more from the plenum, except that this distance is permitted to be reduced to 8 mm beyond a bend or offset in the duct sufficiently large to shield the remainder of the supply duct from direct radiation from the furnace heat exchanger. (See Note A-3.6.5.6.(4).) If a register is installed in a floor directly over a pipeless furnace, a double-walled register box with not less than 100 mm between walls, or a register box with the warm-air passage completely surrounded by the cold-air passage, shall be permitted instead of the clearances listed in Sentences (2), (3) and (4). |  | Div B | 6.2.3.19.(1) | 6.2.3.19 Clearances of Ducts and Plenums | The clearances from combustible material and supply plenums, supply ducts, boots and register boxes of heating systems shall conform to the requirements of Subsection 6.2.4. | Common Sentence | No
2015 | ON | NBC | Div B | 6.3.2.7.(1) | Interconnection of Systems | In a care or residential occupancy, air from one suite shall not be circulated to any other suite or to a public corridor. | obc2019_divb | Div B | 6.2.3.9.(1) | 6.2.3.9. Interconnection of Systems | In a residential occupancy, air from one suite shall not be circulated to any other suite or to a public corridor or public stairway. | Common Sentence | Yes | Air Duct Systems
2015 | ON | NBC | Div B | 6.3.2.7.(2) | Interconnection of Systems | Except as permitted by Sentences 6.3.2.7.(3) and 6.3.2.10.(6), air duct systems serving storage garages shall not be directly interconnected with other parts of the building. | obc2019_divb | Div B | 6.2.3.9.(2) | 6.2.3.9. Interconnection of Systems | Except as permitted by Sentence (3) and Sentence 6.2.3.8.(6), air duct systems serving storage garages shall not be directly interconnected with ductwork serving other areas of the building. | Common Sentence | No | Air Duct Systems
2015 | ON | NBC | Div B | 6.3.2.7.(2) | Interconnection of Systems | Except as permitted by Sentences 6.3.2.7.(3)and 6.3.2.10.(6), air duct systems serving storage garages shall not be directly interconnected with other parts of the building. | obc2019_divb | Div B | 6.2.4.4.(10) | 6.2.4.4.Warm-Air Supply Outlets | Air duct systems serving storage garages shall not be interconnected with other parts of the building. | Common Sentence | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 6.3.2.7.(3) | Interconnection of Systems | Exhaust ducts referred to in Sentence 6.3.2.10.(10) are permitted to exhaust through an enclosed storage garage prior to exhausting to the outdoors, provided the storage garage's exhaust system runs continuously, the capacity of the storage garage's exhaust system is equal to or exceeds the volume of the exhaust entering the garage, and a leakage rate 1 smoke/fire damper rated in accordance with ULC CAN/ULC-S112.1 Leakage Rated Dampers for Use in Smoke Control Systems is provided near the duct outlet location in the storage garage to prevent air from the storage garage from entering the exhaust ductwork system in the event the building's exhaust fan is shut down. | obc2019_divb | Div B | 6.2.3.9.(3) | 6.2.3.9. Interconnection of Systems | Where exhaust ducts are provided in conformance with Sentence 6.2.3.8.(6), they may exhaust through an enclosed storage garage prior to exhausting to the outdoors provided, (a) the storage garage exhaust system runs continuously, (b) the capacity of the storage garage exhaust system is equal to or exceeds the volume of the exhaust entering the garage, and (c) a leakage rate 1 smoke/fire damper rated in accordance with CAN/ULC-S112.1, "Leakage Rated Dampers for Use in Smoke Control Systems", is provided near the duct outlet location in the storage garage to prevent air from the storage garage from entering the exhaust ductwork system in the event the building's exhaust fan is shut down. | Common Sentence | No | Air Duct Systems
2015 | ON | NBC | Div B | 6.3.2.8.(1) | Makeup Air | In ventilating systems that exhaust air to the outdoors, provision shall be made for the admission of a supply of makeup air in sufficient quantity so that the operation of the exhaust system and other exhaust equipment or combustion equipment is not adversely affected. | obc2019_divb | Div B | 6.2.3.11.(1) | 6.2.3.11. Make-up Air | In ventilating systems that exhaust air to the outdoors, provision shall be made for the admission of a supply of make-up air in sufficient quantity so that the operation of the exhaust system and other exhaust equipment or combustion equipment is not adversely affected. | Common Sentence | No | Ventilation
2015 | ON | NBC | Div B | 6.3.2.8.(2) | Makeup Air | Makeup air facilities required by Sentence 6.3.2.8.(1) shall be interlocked with the exhaust devices they serve so that both operate together. | obc2019_divb | Div B | 6.2.3.11.(2) | 6.2.3.11. Make-up Air | Make-up air facilities required by Sentence (1) shall be interlocked with the exhaust devices they serve so that both operate together. | Common Sentence | No | Ventilation
2015 | ON | NBC | Div B | 6.3.2.8.(3) | Makeup Air | Where makeup air facilities are intended to introduce air directly from the outdoors to occupied parts of the building in winter, they shall incorporate means of tempering that air to maintain the indoor design temperature. | obc2019_divb | Div B | 6.2.3.11.(3) | 6.2.3.11. Make-up Air | Where make-up air facilities are intended to introduce air directly from the outdoors to occupied parts of the building in winter, they shall incorporate means of tempering that air to maintain the indoor design temperature. | Common Sentence | No | Ventilation
2015 | ON | NBC | Div B | 6.3.2.9.(1) | Supply, Return, Intake and Exhaust Air Openings | Supply, return and exhaust air openings located less than 2 m above the floor in rooms or spaces in buildings shall be protected by grilles having openings of a size that will not allow the passage of a 15 mm diam sphere. | obc2019_divb | Div B | 6.2.3.12.(1) | 6.2.3.12. Supply, Return, Intake and Exhaust Air Openings | Supply, return and exhaust air openings located less than 2 000 mm above the floor in rooms or spaces in buildings shall be protected by grilles having openings of a size that will not allow the passage of a 15 mm diameter sphere. | Common Sentence | No | Air Duct Systems
2015 | ON | NBC | Div B | 6.3.2.9.(2) | Supply, Return, Intake and Exhaust Air Openings | Outdoor air intakes shall be located so that the quality of the air entering the building complies with Sentences 6.2.1.2.(2) and 6.2.1.2.(3), and they are separated a minimum distance from sources of contaminants in accordance with Table 6.3.2.9. | obc2019_divb | Div B | 6.2.3.12.(2) | 6.2.3.12. Supply, Return, Intake and Exhaust Air Openings | Outdoor air intakes and exhaust outlets on the exterior of buildings shall be designed or located so that the air entering the building system will not contain more contaminants than the normal exterior air of the locality in which the building is situated. | Common Sentence | Yes | Air Duct Systems
2015 | ON | NBC | Div B | 6.3.2.9.(2) | Supply, Return, Intake and Exhaust Air Openings | Outdoor air intakes shall be located so that the quality of the air entering the building complies with Sentences 6.2.1.2.(2) and 6.2.1.2.(3), and they are separated a minimum distance from sources of contaminants in accordance with Table 6.3.2.9. | obc2019_divb | Div B | 6.2.3.12.(6) | 6.2.3.12. Supply, Return, Intake and Exhaust Air Openings | Outdoor air intakes shall be located so that they are separated a minimum distance from sources of contaminants in accordance with Table 6.2.3.12. | Common Sentence | Yes | Air Duct Systems
2015 | ON | NBC | Div B | 6.3.2.9.(2) | Supply, Return, Intake and Exhaust Air Openings | Outdoor air intakes shall be located so that the quality of the air entering the building complies with Sentences 6.2.1.2.(2) and 6.2.1.2.(3), and they are separated a minimum distance from sources of contaminants in accordance with Table 6.3.2.9. | obc2019_divb | Div B | 6.2.4.13.(2) | 6.2.4.13. Supply, Return, Intake and Exhaust Air Openings | Outdoor air intakes and exhaust outlets at the building exterior shall be designed or located so that the air entering the building system will not contain more contaminants than the normal exterior air. | Common Sentence | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 6.3.2.9.(4) | Supply, Return, Intake and Exhaust Air Openings | Exterior openings for outdoor air intakes and exhaust outlets shall be shielded from the entry of snow and rain and shall be fitted with corrosion-resistant screens of mesh having openings not larger than 15 mm, except where experience has shown that climatic conditions require larger openings to prevent the screen openings from icing over. | obc2019_divb | Div B | 6.2.3.12.(3) | 6.2.3.12. Supply, Return, Intake and Exhaust Air Openings | Exterior openings for outdoor air intakes and exhaust outlets shall be shielded from the entry of snow and rain and shall be fitted with corrosion-resistant screens of mesh having openings not larger than 15 mm, except where experience has shown that climatic conditions require larger openings to avoid icing over of the screen openings. | Common Sentence | No | Air Duct Systems
2015 | ON | NBC | Div B | 6.3.2.9.(5) | Supply, Return, Intake and Exhaust Air Openings | Screens required in Sentence 6.3.2.9.(4) shall be accessible for maintenance. | obc2019_divb | Div B | 6.2.3.12.(4) | 6.2.3.12. Supply, Return, Intake and Exhaust Air Openings | Screens required in Sentence (3) shall be accessible for maintenance. | Common Sentence | No | Air Duct Systems
2015 | ON | NBC | Div B | 6.3.2.9.(5) | Supply, Return, Intake and Exhaust Air Openings | Screens required in Sentence 6.3.2.9.(4) shall be accessible for maintenance. | obc2019_divb | Div B | 6.2.4.13.(4) | 6.2.4.13. Supply, Return, Intake and Exhaust Air Openings | Screens required in Sentence (3) shall be accessible for maintenance. | Common Sentence | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 6.3.2.9.(6) | Supply, Return, Intake and Exhaust Air Openings | Combustible grilles, diffusers and other devices covering supply, return, intake and exhaust openings shall comply with Article 3.6.5.7. 3.6.5.7.(1) Combustible grilles, diffusers, and other devices for supply, return and exhaust air openings shall conform to the flame spresd rating and smoke developped classification requirements for the interior finish of the surface on which hey are installed. | obc2019_divb | Div B | 6.2.3.12.(5) | 6.2.3.12. Supply, Return, Intake and Exhaust Air Openings | Combustible grilles, diffusers and other devices for supply, return and exhaust air openings in rooms shall conform to the flame-spread rating and smoke developed classification requirements for the interior finish of the surface on which they are installed. | Common Sentence | Yes | Air Duct Systems
2015 | ON | NBC | Div B | 6.3.3.1.(1) | Requirement for Venting | Except as provided in Articles 6.3.3.2. and 6.3.3.3., the products of combustion from oil-, gas- and solid-fuel-burning appliances shall be vented in conformance with the requirements in the applicable appliance installation standard listed in Article 6.2.1.5. | obc2019_divb | Div B | 6.3.1.1.(1) | 6.3.1.1. Requirement for Venting | Except as provided in Articles 6.3.1.2. and 6.3.1.3., the products of combustion from solid fuel-burning appliances shall be vented in conformance with the requirements in the applicable appliance installation standards listed in Article 6.2.1.4. | Common Sentence | Yes | Chimneys and Venting Equipment
2015 | ON | NBC | Div B | 6.3.3.2.(1) | Masonry or Concrete Chimneys | Rectangular masonry or concrete chimneys not more than 12 m in height shall conform to part 9. if they serve appliances with a combined total rated heat output of 120 kW or less, or fireplaces. | obc2019_divb | Div B | 6.3.1.2.(1) | 6.3.1.2. Masonry or Concrete Chimneys | Rectangular masonry or concrete chimneys not more than 12 m in height shall conform to Part 9 if they serve,(a) appliances with a combined total rated heat output of 120 kW or less, or (b) fireplaces. | Common Sentence | No | Chimneys and Venting Equipment
2015 | ON | NBC | Div B | 6.3.3.2.(2) | Masonry or Concrete Chimneys | Masonry or concrete chimneys other than those described in Sentence 6.3.3.2.(1) shall be designed and installed in conformance with the appropriate requirements in NFPA 211, Chimneys, Fireplaces, Vents, and Solid Fuel-Burning Appliances | obc2019_divb | Div B | 6.3.1.2.(2) | 6.3.1.2. Masonry or Concrete Chimneys | Masonry or concrete chimneys other than those described in Sentence (1) shall be designed and installed in conformance with the appropriate requirements in NFPA 211, "Chimneys, Fireplaces, Vents and Solid Fuel-Burning Appliances". | Common Sentence | No | Chimneys and Venting Equipment
2015 | ON | NBC | Div B | 6.3.3.3.(1) | Metal Smoke Stacks | Single wall metal smoke stacks shall be designed and installed in conformance with NFPA 211, Chimneys, Fireplaces, Vents, and Solid Fuel-Burning Appliances | obc2019_divb | Div B | 6.3.1.3.(1) | 6.3.1.3. Metal Smoke Stacks | Single wall metal smoke stacks shall be designed and installed in conformance with NFPA 211, "Chimneys, Fireplaces, Vents and Solid Fuel-Burning Appliances". | Common Sentence | No | Chimneys and Venting Equipment
2015 | ON | NBC | Div B | 6.3.3.4.(1) | Access Ladders |  | obc2019_divb | Div B | 6.3.1.5.(1) | 6.3.1.5. Access Ladders |  | Common Sentence | No | Chimneys and Venting Equipment
2015 | ON | NBC | Div B | 6.3.3.4.(2) | Access Ladders | Rungs for external ladders shall begin at not less than 2.5 m from ground level. | obc2019_divb | Div B | 6.3.1.5.(2) | 6.3.1.5. Access Ladders | Rungs for external ladders shall begin at not less than 2 500 mm from ground level. | Common Sentence | No | Chimneys and Venting Equipment
2015 | ON | NBC | Div B | 6.3.4.1.(1) | Application | This Subsection applies to laboratories where dangerous goods, including flammable liquids and combustible liquids, are used in normal laboratory operations in quantities or in a manner that creates a fire or explosion hazard. | obc2019_divb | Div B | 6.2.13.1.(1) | 6.2.13.1. Application | This Subsection applies to laboratories intended as a location where flammable liquids and combustible liquids are used in normal laboratory operations in quantities or in a manner that create a fire or explosion hazard. | Common Sentence | Yes | Ventilation for Laboratories
2015 | ON | NBC | Div B | 6.3.4.2.(1) | General Ventilation | A laboratory shall be provided with continuous mechanical ventilation designed to ensure that dangerous goods vapours and particles do not accumulate in the laboratory, are prevented from migrating to other parts of the building, do not accumulate in the ventilation system, are exhausted to the outdoors, and are not returned to the building. | obc2019_divb | Div B | 6.2.13.2.(1) | 6.2.13.2. General Ventilation | A laboratory shall be provided with continuous mechanical ventilation designed to ensure that flammable vapours,(a) do not accumulate in the laboratory, (b) are prevented from migrating to other parts of the building, (c) do not accumulate in the ventilation system, (d) are exhausted to the outdoors, and (e) are not returned to the building. | Common Sentence | Yes | Ventilation for Laboratories
2015 | ON | NBC | Div B | 6.3.4.2.(2) | General Ventilation | A ventilation system required by this Subsection shall be provided with monitoring devices to indicate that the ventilation system is in operation, and sound an alarm if the ventilation system is malfunctioning. | obc2019_divb | Div B | 6.2.13.2.(2) | 6.2.13.2. General Ventilation | A ventilation system required in this Subsection shall be provided with monitoring devices that,(a) indicate that the ventilation system is in operation, and (b) sound an alarm if the ventilation system is malfunctioning. | Common Sentence | No | Ventilation for Laboratories
2015 | ON | NBC | Div B | 6.3.4.4.(1) | Enclosure Construction | The power-ventilated enclosure required by Sentence 5.5.4.2.(1) of Division B of the NFC and its exhaust duct system shall except as provided in Sentences 6.3.4.4.(2) and 6.3.4.4.(3), be constructed of noncombustible materials compatible with and chemically resistant to the dangerous goods vapours and particles being exhausted, and be provided with access doors to permit inspection and maintenance of the fan assembly and exhaust ducts. | obc2019_divb | Div B | 6.2.13.5.(1) | 6.2.13.5. Enclosure Construction | The power-ventilated enclosure referred to in Article 6.2.13.3. and its exhaust duct system shall,(a) except as provided in Sentences (2) and (3), be constructed of noncombustible materials compatible with and chemically resistant to the flammable vapours and particles being exhausted, and (b) be provided with access doors to permit inspection and maintenance of the fan assembly and exhaust ducts. | Common Sentence | Yes | Ventilation for Laboratories
2015 | ON | NBC | Div B | 6.3.4.4.(2) | Enclosure Construction | Combustible materials are permitted in systems described in Sentence 6.3.4.4.(1) if such materials are required by the corrosive or reactive properties of the dangerous goods being used, and their flame-spread rating is not more than 25. | obc2019_divb | Div B | 6.2.13.5.(2) | 6.2.13.5. Enclosure Construction | Combustible materials are permitted in the power-ventilated enclosure described in Sentence (1) and its exhaust duct system if,(a) such materials are required by the corrosive or reactive properties of the chemicals or liquids being used, and (b) their flame-spread rating is not more than 25. | Common Sentence | Yes | Ventilation for Laboratories
2015 | ON | NBC | Div B | 6.3.4.4.(3) | Enclosure Construction | The flame-spread rating required by Sentence 6.3.4.4.(2) is permitted to be greater than 25 if an automatic fire suppression system is provided inside the power-ventilated enclosure and its exhaust duct system. | obc2019_divb | Div B | 6.2.13.5.(3) | 6.2.13.5. Enclosure Construction | The flame-spread rating required in Sentence (2) is permitted to be greater than 25 if an automatic fire suppression system is provided inside the power-ventilated enclosure and its exhaust duct system. | Common Sentence | No | Ventilation for Laboratories
2015 | ON | NBC | Div B | 6.4.1.1.(1) | Location of Appliances | Except for appliances installed in dwelling units, fuel-fired heating appliances shall be located, enclosed or separated from the remainder of the building in conformance with part 3. (See also part 9.) | obc2019_divb | Div B | 6.2.5.1.(1) | 6.2.5.1. Location of Appliances | Except for appliances installed in dwelling units, fuel-fired heating appliances shall be located, enclosed or separated from the remainder of the building in conformance with Section 3.6. | Common Sentence | No | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 6.4.1.2.(1) | Appliances Installed Outside the Building |  | obc2019_divb | Div B | 6.2.5.2.(1) | 6.2.5.2. Appliances Installed Outside the Building |  | Common Sentence | Yes | Heating Appliances, General
2015 | ON | NBC | Div B | 6.4.2.1.(1) | Clearances | Every unit heater using either steam or hot water as the heating medium shall be installed such that the clearances between the appliance and adjacent combustible material conform to Table 6.7.1.2. | obc2019_divb | Div B | 6.2.7.1.(1) | 6.2.7.1. Clearances | Every unit heater using either steam or hot water as the heating medium shall be installed such that the clearances between the appliance and adjacent combustible material conform to Table 6.2.9.3. | Common Sentence | No | Unit Heaters
2015 | ON | NBC | Div B | 6.4.3.1.(1) | Lining or Backing |  | obc2019_divb | Div B | 6.2.8.1.(1) | 6.2.8.1. Lining or Backing |  | Common Sentence | No | Radiators
2015 | ON | NBC | Div B | 6.4.3.1.(2) | Lining or Backing | Every steam or hot water radiator and convector shall be installed so as to conform to the clearance requirements of Table 6.7.1.2. | obc2019_divb | Div B | 6.2.8.1.(2) | 6.2.8.1. Lining or Backing | Every steam or hot water radiator and convector shall be installed to conform to the clearance requirements of Table 6.2.9.3. | Common Sentence | No | Radiators
2015 | ON | NBC | Div B | 6.5.1.1.(2) | Insulation and Coverings |  | obc2019_divb | Div B | 6.2.9.2.(1) | 6.2.9.2. Insulation and Coverings |  | Common Sentence | No | Piping for Heating and Cooling Systems
2015 | ON | NBC | Div B | 6.5.1.1.(3) | Insulation and Coverings | Exposed piping or equipment subject to human contact shall be insulated so that the temperature of the exposed surface does not exceed 70° C. (See Note A-6.5.1.1.(3).) | obc2019_divb | Div B | 6.2.9.2.(6) | 6.2.9.2. Insulation and Coverings | Exposed piping or equipment subject to human contact shall be insulated so that the temperature of the exposed surface does not exceed 70° C. (See Appendix A.) | Common Sentence | No | Piping for Heating and Cooling Systems
2015 | ON | NBC | Div B | 6.6.1.1.(1) | Cooling Units | Where a cooling unit is combined with a fuel-fired fumace in the same duct system, the cooling unit shall be installed a) in parallel with the heating furnace, b) upstream of the fumnce, provided the fumace is designed for such application, or c) downstream of the furnace, provided the cooling unit is designed to prevent excessive temperature or pressure in the refrigeration system. | obc2019_divb | Div B | 6.2.10.1.(1) | Cooling Units | Where a cooling unit is combined with a fuel-fired furnace in the same duct system, the cooling unit shall be installed, (a) in parallel with the heating furnace, (b) upstream of the furnace, provided the furnace is designed for such application, or (c) downstream of the furnace, provided the cooling unit is designed to prevent excessive temperature or pressure in the refrigeration system. | Common Sentence | No | Refrigerating Systems and Equipment for Air-Conditioning
2015 | ON | NBC | Div B | 6.7.1.1.(1) | 6.7.1.1 Piping Materials and Installation | Piping shall be made from materials designed to withstand the effects of temperatures and pressures that may occur in the system. (See Articles 3.1.5.19., 3.1.9.1., 9.10.9.6. and 9.10.9.7. for fire safety requirements.) | obc2019_divb | Div B | 6.2.9.1.(1) | 6.2.9.1. Piping Materials and Installation | Piping shall be made from materials designed to withstand the effects of temperatures and pressures that may occur in the system. | Common Sentence | Yes | Piping for Heating and Cooling Systems
2015 | ON | NBC | Div B | 6.7.1.1.(2) | 6.7.1.1 Piping Materials and Installation |  | obc2019_divb | Div B | 6.2.9.1.(2) | 6.2.9.1. Piping Materials and Installation |  | Common Sentence | No | Piping for Heating and Cooling Systems
2015 | ON | NBC | Div B | 6.7.1.1.(3) | 6.7.1.1 Piping Materials and Installation |  | obc2019_divb | Div B | 6.2.9.1.(3) | 6.2.9.1. Piping Materials and Installation |  | Common Sentence | No | Piping for Heating and Cooling Systems
2015 | ON | NBC | Div B | 6.7.1.2.(1) | Clearances | Clearances between combustible material and bare pipes carrying steam or hot water shall conform to Table 6.7.1.2. | obc2019_divb | Div B | 6.2.9.3.(1) | 6.2.9.3. Clearances | Clearances between combustible material and bare pipes carrying steam or hot water shall conform to Table 6.2.9.3. | Common Sentence | No | Piping for Heating and Cooling Systems
2015 | ON | NBC | Div B | 6.7.1.3.(1) | Surface Temperature |  | obc2019_divb | Div B | 6.2.9.4.(1) | Surface Temperature |  | Common Sentence | No | Piping for Heating and Cooling Systems
2015 | ON | NBC | Div B | 6.7.1.4.(1) | Protection | Where a pipe carrying steam or hot water at a temperature above l20°C passes through a combustible floor, ceiling or wall, the construction shall be protected by a sleeve of metal or other noncombustible material not less than 50 mm larger in diameter than the pipe. | obc2019_divb | Div B | 6.2.9.5.(1) | Protection | Where a pipe carrying steam or hot water at a temperature above 120°C passes through a combustible floor, ceiling or wall, the construction shall be protected by a sleeve of metal or other noncombustible material not less than 50 mm larger in diameter than the pipe. | Common Sentence | No | Piping for Heating and Cooling Systems
2015 | ON | NBC | Div B | 6.7.1.5.(1) | Piping in Shafts |  | obc2019_divb | Div B | 6.2.9.6.(1) | Piping in Shafts |  | Common Sentence | No | Piping for Heating and Cooling Systems
2015 | ON | NBC | Div B | 6.7.2.1.(1) | Storage Bins | Service pipes passing through a storage bin for solid fuel shall be protected or so located as to avoid damage to the pipes. | obc2019_divb | Div B | 6.2.11.1.(1) | 6.2.11.1. Storage Bins | Service pipes passing through a storage bin for solid fuel shall be protected or so located as to avoid damage to the pipes. | Common Sentence | No | Storage Bins
2015 | ON | NBC | Div B | 6.7.2.1.(2) | Storage Bins | Except for fuel-thawing pipes, every pipe designed to operate at a temperature of 50°C or above shall be located where solid fuel cannot be stored in contact with it. | obc2019_divb | Div B | 6.2.11.1.(2) | 6.2.11.1. Storage Bins | Except for fuel-thawing pipes, every pipe designed to operate at a temperature of 50°C or above shall be located where fuel cannot be stored in contact with it. | Common Sentence | No | Storage Bins
2015 | ON | NBC | Div B | 6.8.1.1.(1) | Access Openings | Any covering of an access opening through which a person could enter shall be openable from the inside without the use of keys where there is a possibility of the opening being accidentally closed while the system or equipment is being serviced. | obc2019_divb | Div B | 6.2.1.11.(1) | 6.2.1.11. Access Openings | Any covering of an access opening through which a person could enter shall be openable from the inside without the use of keys where there is a possibility of the opening being accidentally closed while the system or equipment is being serviced. | Common Sentence | No | Design and Installation
2015 | ON | NBC | Div B | 6.8.1.2.(1) | Openings in Air Duct Systems | Air duct systems shall have no openings other than those required for the proper operation and maintenance of the system. | obc2019_divb | Div B | 6.2.3.3.(1) | 6.2.3.3. Connections and Openings in Air Duct Systems | Air duct systems shall have,(a) tight-fitting connections throughout, and (b) no openings other than those required for proper operation, inspection and maintenance of the system. | Common Sentence | Yes | Air Duct Systems
2015 | ON | NBC | Div B | 6.8.1.2.(2) | Openings in Air Duct Systems |  | obc2019_divb | Div B | 6.2.3.3.(2) | 6.2.3.3. Connections and Openings in Air Duct Systems |  | Common Sentence | No | Air Duct Systems
2015 | ON | NBC | Div B | 6.9.1.2.(1) | Hazardous Gases, Dusts or Liquids | Except as provided in Subsection 6., systems serving spaces that contain hazardous gases, dusts or liquids shall be designed, constructed and installed to conform to the requirements of the applicable provincial or territorial regulations or municipal bylaws or, in the absence of such regulations or bylaws, to good engineering practice such as that described in the publications of the National Fire Protection Association and in the NFC. (See Note A-6.9.1.2.(1).) | obc2019_divb | Div B | 6.2.2.5.(1) | 6.2.2.5 Hazardous gases, Dusts or Liquids | Except as provided in Subsection 6.2.13., systems serving spaces that contain hazardous gases, dusts or liquids shall be designed, constructed and installed in conformance with the provisions of the Fire Code made under the Fire Protection and Prevention Act, 1997, or in the absence of requirements pertinent to such systems in the Fire Code, to good engineering practice such as is described in the publications of the National Fire Protection Association and in the CCBFC NRCC 56192, "National Fire Code of Canada". (See Appendix A.) | Common Sentence | Yes | Ventilation
2015 | ON | NBC | Div B | 6.9.1.2.(2) | Hazardous Gases, Dusts or Liquids | When indoor piping for Class I flammable liquids is installed in a trench, the trench shall be provided with positive ventilation to the outdoors, or designed to prevent the accumulation of flammable vapours. | obc2019_divb | Div B | 6.2.2.5.(2) | 6.2.2.5. Hazardous Gases, Dusts or Liquids | When indoor piping for Class I flammable liquids is installed in a trench, the trench shall be,(a) provided with positive ventilation to the outdoors, or (b) designed to prevent the accumulation of flammable vapours. | Common Sentence | No | Ventilation
2015 | ON | NBC | Div B | 6.9.1.3.(1) | Commercial Cooking Equipment | Fire protection systems for commercial cooking equipment referred to in Sentence 6.3.1.7.(1) using vegetable oil or animal fat shall conform to UL ANSI/UL 300, Fire Testing of Fire Extinguishing Systems for Protection of Commercial Cooking Equipment or ULC ULC/ORD-C1254.6, Fire Testing of Restaurant Cooking Area Fire Extinguishing System Units | obc2019_divb | Div B | 6.2.2.6.(2) | 6.2.2.6. Commercial Cooking Equipment | Fire protection systems for high efficiency, high temperature commercial cooking equipment using vegetable oil or animal fat shall conform to,(a) ANSI/UL 300, "Fire Extinguishing Systems for Protection of Commercial Cooking Equipment", or (b) ULC/ORD-C1254.6, "Fire Testing of Restaurant Cooking Area Fire Extinguishing System Units". | Common Sentence | Yes | Ventilation
2015 | ON | NBC | Div B | 6.9.2.1.(1) | Fire Dampers | Fire dampers shall conform to Article 3.1.8.10. | obc2019_divb | Div B | 6.2.3.6.(1) | 6.2.3.6. Fire Dampers | Fire dampers shall conform to the requirements of Subsection 3.1.8. | Common Sentence | Yes | Air Duct Systems
2015 | ON | NBC | Div B | 6.9.2.2.(1) | Smoke Detectors | Air handling systems shall incorporate smoke detectors where and as required by Article 3.2.4.12. | obc2019_divb | Div B | 6.2.3.7.(1) | 6.2.3.7. Smoke Detector Control | Air handling systems shall incorporate smoke detector control where required by Article 3.2.4.13. | Common Sentence | No | Air Duct Systems
2015 | ON | NBC | Div B | 6.9.2.3.(1) | Exhaust Ducts and Outlets | Where an exhaust duct system is used for smoke removal in a high building, the requirements of Article 3.2.6.6. shall apply. | obc2019_divb | Div B | 6.2.3.8.(12) | 6.2.3.8. Exhaust Ducts and Outlets | Where an exhaust duct system is used for smoke removal in a high building, the requirements of Article 3.2.6.6. shall apply. 6.2.3.9.(12) | Common Sentence | No | Air Duct Systems
2015 | ON | NBC | Div B | 6.9.2.3.(2) | Exhaust Ducts and Outlets | Where exhaust duct systems from more than one fire compartment are connected to an exhaust duct in a vertical service space, the requirements of Article 3.6.3.4. shall apply. | obc2019_divb | Div B | 6.2.3.8.(13) | 6.2.3.8. Exhaust Ducts and Outlets | Where exhaust duct systems from more than one fire compartment are connected to an exhaust duct in a vertical service space, the requirements of Article 3.6.3.4. shall apply. 6.2.3.9.(13) | Common Sentence | No | Air Duct Systems
2015 | ON | NBC | Div B | 6.9.2.4.(1) | Ducts in Exits | Where ducts penetrate fire separations separating exits from the remainder of the building, they shall be in accordance with Article 3.4.4.4. | obc2019_divb | Div B | 6.2.3.10.(1) | 6.2.3.10. Ducts in Exits | Except as permitted in Sentence (2), duct penetration of fire separations separating exits from the remainder of the building shall be in accordance with Article 3.4.4.4. | Common Sentence | Yes | Air Duct Systems
2015 | ON | NBC | Div B | 6.9.3.1.(1) | Carbon Monoxide Alarms | This Article applies to every building that contains a residential occupancy, a care occupancy with individual suites, or a care occupancy containing sleeping rooms not within a suite, and that also contains a) a fuel-burning appliance, or b) a storage garage. | obc2019_divb | Div B | 6.2.12.1.(1) | 6.2.12.1. Application | This Subsection applies to every building that, (a) contains a residential occupancy, and (b) contains a fuel-burning appliance or a storage garage. | Common Sentence | Yes | Carbon Monoxide Alarms
2015 | ON | NBC | Div B | 6.9.3.1.(2) | Carbon Monoxide Alarms | Carbon monoxide (CO) alarms required by this Article shall conform to CSA CAN/CSA-6.19, Residential Carbon Monoxide Alarming Devices be equipped with an integral alarm that satisfies the audibility requirements of CSA CAN/CSA-6.19, Residential Carbon Monoxide Alarming Devices have no disconnect switch between the overcurrent device and the CO alarm, where the CO alarm is powered by the electrical system serving the suite (see Note A-6.9.3.1.(2)(c)), and be mechanically fixed at a height above the floor as recommended by the manufacturer. | obc2019_divb | Div B | 6.2.12.3.(1) | 6.2.12.3. Installation and Conformance to Standards | The carbon monoxide alarms required by Article 6.2.12.2. shall,(a) except as permitted in Sentence (2), be permanently connected to an electrical circuit and shall have no disconnect switch between the overcurrent device and the carbon monoxide alarm, (b) be wired so that its activation will activate all carbon monoxide alarms within the suite, where located within a suite of residential occupancy, (c) be equipped with an alarm that is audible within bedrooms when the intervening doors are closed, where located in a suite of residential occupancy, and (d) conform to, (i) CAN/CSA-6.19, "Residential Carbon Monoxide Alarming Devices", or (ii) UL 2034, "Single and Multiple Station Carbon Monoxide Alarms". | Common Sentence | Yes | Carbon Monoxide Alarms
2015 | ON | NBC | Div B | 6.9.3.1.(3) | Carbon Monoxide Alarms | Where a fuel-burning appliance is installed in a suite of residential occupancy or in a suite of care occupancy, a CO alarm shall be installed a) inside each bedroom, or b) outside each bedroom, within 5 m of each bedroom door, measured following corridors and doorways. | obc2019_divb | Div B | 6.2.12.2.(1) | 6.2.12.2. Location of Carbon Monoxide Alarms | Where a fuel-burning appliance is installed in a suite of residential occupancy, a carbon monoxide alarm shall be installed adjacent to each sleeping area in the suite. | Common Sentence | Yes | Carbon Monoxide Alarms
2015 | ON | NBC | Div B | 6.9.3.1.(4) | Carbon Monoxide Alarms | Where a fuel-burning appliance is installed in a service room that is not in a suite of residential occupancy nor in a suite of care occupancy, a CO alarm shall be installed a) either inside each bedroom, or if outside, within 5 m of each bedroom door, measured following corridors and doorways, in every suite of residential occupancy or suite of care occupancy that shares a wall or floor/ceiling assembly with the service room, and b) in the service room. | obc2019_divb | Div B | 6.2.12.2.(2) | 6.2.12.2. Location of Carbon Monoxide Alarms | Where a fuel-burning appliance is installed in a service room that is not in a suite of residential occupancy, a carbon monoxide alarm shall be installed, (a) adjacent to each sleeping area in every suite of residential occupancy that is adjacent to the service room, and (b) in the service room. | Common Sentence | Yes | Carbon Monoxide Alarms
2015 | ON | NBC | Div B | 6.9.3.1.(5) | Carbon Monoxide Alarms | For each suite of residential occupancy or suite of care occupancy that shares a wall or floor/ceiling assembly with a storage garage or that is adjacent to an attic or crawl space to which the storage garage is also adjacent, a CO alarm shall be installed a) inside each bedroom, or b) outside each bedroom, within 5 m of each bedroom door, measured following corridors and doorways. | obc2019_divb | Div B | 6.2.12.2.(3) | 6.2.12.2. Location of Carbon Monoxide Alarms | Where a storage garage is located in a building containing a residential occupancy, a carbon monoxide alarm shall be installed adjacent to each sleeping area in every suite of residential occupancy that is adjacent to the storage garage. | Common Sentence | Yes | Carbon Monoxide Alarms
2015 | ON | NBC | Div B | 6.9.4.1.(1) | Ash Storage Bins | Every ash storage bin shall be constructed of noncombustible material. | obc2019_divb | Div B | 6.2.11.2.(1) | 6.2.11.2 Ash Storage Bins | Every ash storage bin shall be constructed of noncombustible material. | Common Sentence | No | Storage Bins
2015 | ON | NBC | Div B | 6.9.4.1.(2) | Ash Storage Bins | Every opening in an ash storage bin shall be protected by a tight-fitting metal door with metal frame securely fastened to the bin. | obc2019_divb | Div B | 6.2.11.2.(2) | 6.2.11.2 Ash Storage Bins | Every opening in an ash storage bin shall be protected by a tight-fitting metal door with metal frame securely fastened to the bin | Common Sentence | No | Storage Bins
2015 | ON | NBC | Div B | 6.9.4.2.(1) | Fireplaces | Fireplaces shall conform to the requirements of Section 9.22. | obc2019_divb | Div B | 6.2.1.5.(1) | 6.2.1.5. Fireplaces | Fireplaces shall conform to the requirements of Section 9.22. | Common Sentence | No | Design and Installation
2015 | ON | NBC | Div B | 7.1.1.2.(1) | Application | This Part applies to the design, construction, extension, alteration, renewal or repair of plumbing systems. |  |  | 7.1.2.1.(1) | 7.1.2.1. Application | Except as provided in Sentence (2), this Part applies to the design and construction of plumbing. | Common Sentence | Yes | Application and General Requirements
2015 | ON | NBC | Div B | 7.1.3.1.(1) | All Buildings Except Dwelling Units | Buildings shall be equipped with plumbing facilities as required in part 3. and Article 3.8.2.8. |  |  | 7.1.4.1.(1) | 7.1.4.1. Facilities Required | Plumbing facilities shall be provided in accordance with Subsection 3.7.4. and Section 9.31. | Common Sentence | Yes | Application and General Requirements
2015 | ON | NBC | Div B | 9.32.3.11.(3) | Ducts | Where an exhaust duct passes through an unheated space or is not separated from an unheated space by an insulated building assembly, the duct shall be insulated to not less than RSI 0.5. | obc2019_divb | Div B | 6.2.4.11.(1) | 6.2.4.11. Exhaust Ducts and Outlets | Where an exhaust duct passes through or is adjacent to unheated space, the duct shall be insulated to prevent moisture or condensation in the duct. | Common Sentence | No | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.10.(1) | Warm Air Supply Outlets and Return Outlets - General | Supply outlets and return openings in the dwelling unit, when located less than 2 m above the floor, shall be protected by grilles having openings of a size that will not allow the passage of a 15 mm diam sphere. | obc2019_divb | Div B | 6.2.4.13.(1) | 6.2.4.13. Supply, Return, Intake and Exhaust Air Openings | Supply, return and exhaust air openings in rooms or spaces shall be protected by grilles having openings of a size that will not allow the passage of a 15 mm diameter sphere. | Common Sentence | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.10.(2) | Warm-Air Supply Outlets and Return Inlets - General | Combustible grilles, diffusers and other devices for the supply and return air openings installed in walls and ceilings shall have a flame-spread rating of a) not more than 200 in bathrooms, and b) not more than 150 in rooms or spaces other than bathrooms | obc2019_divb | Div B | 6.2.4.13.(5) | 6.2.4.13. Supply, Return, Intake and Exhaust Air Openings | Combustible grilles, diffusers and other devices for supply, return and exhaust air openings in rooms shall conform to the flame-spread rating and smoke developed classification requirements for the interior finish of the surface on which they are installed. 6.2.4.12 | Common Sentence | No
2015 | ON | NBC | Div B | 9.33.6.13.(1) | Return-Air System | The return-air system shall be designed so that the negative pressure from the circulating fan cannot affect the furnace combustion air supply, nor draw combustion products from joints or openings in the furnace or flue pipe. | obc2019_divb | Div B | 6.2.3.20.(5) | 6.2.3.20. Return-Air System Ducts and Plenums | The return-air system shall be designed so that the negative pressure from the circulating fan cannot affect the furnace combustion air supply nor draw combustion products from joints or openings in the furnace or flue pipe. | Common Sentence | Yes | Air Duct Systems
2015 | ON | NBC | Div B | 9.33.6.13.(1) | Return-Air System | The return-air system shall be designed to handle the entire air supply. | obc2019_divb | Div B | 6.2.3.20.(1) | 6.2.3.20. Return-Air System Ducts and Plenums | The return-air system shall be designed to handle the entire air supply. | Common Sentence | Yes | Air Duct Systems
2015 | ON | NBC | Div B | 9.33.6.13.(2) |  | Where any part of a return duct will be exposed to radiation from the furnace heat exchanger or other radiating part within the furnace, such part of a return duct directly above or within 600 mm of the outside furnace casing shall be noncombustible. | obc2019_divb | Div B | 6.2.4.7.(3) | 6.2.4.7. Return-Air System | Where any part of a return duct will be exposed to radiation from the heat exchanger or other radiating part within the furnace, such part of a return duct directly above or within 600 mm of the outside furnace casing shall be noncombustible. | Common Sentence | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.14.(1) | Filters and Odour Removal Equipment | Air filters for air duct systems shall conform to the requirements for Class 2 air filter units as described in ULC CAN/ULC-S111 Fire Tests for Air Filter Units | obc2019_divb | Div B | 6.2.4.14.(1) | 6.2.4.14. Air Filters and Equipment | Air filters for air duct systems shall conform to the requirements for Class 2 air filter units as described in CAN/ULC-S111, "Fire Tests For Air Filter Units". | Common Sentence | No
2015 | ON | NBC | Div B | 9.33.6.14.(2) | Filters and Odour Removal Equipment | When electrostatic-type filters are used, they shall be installed so as to ensure that the electric circuit is automatically de-energized when filter access doors are opened or, in dwelling units, when the furnace circulation fan is not operating. | obc2019_divb | Div B | 6.2.4.14.(2) | 6.2.4.14. Air Filters and Equipment | When electrostatic-type filters are used, they shall be installed so as to ensure that the electric circuit is automatically de-energized when filter access doors are opened or when the system circulating fan is not operating. | Common Sentence | No | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.2.(1) | Materials in Air Duct Systems | Except as provided in Sentences (2) to (6) and in Article 3.6.4.3., all ducts, duct connectors, associated fittings and plenums used in air duct systems shall be constructed of steel, aluminum alloy, copper, clay or similar noncombustible material. | obc2019_divb | Div B | 6.2.4.2.(1) | 6.2.4.2. Duct Design | Except as provided in Sentences (2) to (4) and in Article 3.6.4.3., all ducts, duct connectors, associated fittings and plenums used in air duct systems shall be constructed of steel, aluminum alloy, copper, clay or similar noncombustible material. 6.2.3.3.(1) | Common Sentence | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.3.(1) |  | Tape used for sealing duct joints in air ducts, plenums and other parts of air duct systems shall meet the flame-resistance requirements for fabric in CAN/ULC-S109, “Flame Tests of Flame-Resistant Fabrics and Films.” | obc2019_divb | Div B | 6.2.4.9.(1) | 6.2.4.9. Tape | Tape used for sealing joints in air ducts, plenums and other parts of air duct systems shall meet the flame-resistance requirements for fabric in CAN/ULC-S109, "Flame Tests of Flame-Resistant Fabrics and Films". 6.2.3.3.(17) | Common Sentence | No | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.4.(5) |  | Except as provided in Sentences (6) and (7), foamed plastic insulation shall not be used as part of an air duct or for insulating an air duct. | obc2019_divb | Div B | 6.2.4.8.(1) | 6.2.4.8. Coverings, Linings and Insulation | Except as provided in Sentence (5), foamed plastic insulation shall not be used as part of an air duct or for insulating an air duct. 6.2.4.5.(4) | Common Sentence | No | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.4.(6) |  | Foamed plastic insulation conforming to Article 9.25.2.2. is permitted to be used to insulate a galvanized steel, stainless steel or aluminum air duct, provided a) the foamed plastic insulation applied to supply ductwork is not less than 3 m from the furnace bonnet, b) the temperature within the ductwork where the insulation is installed is not greater than 50°C, c) duct joints are taped with a product conforming to Sentence 9.33.6.3.(1), d) return air plenums are separated from the foamed plastic insulation, and e) the foamed plastic insulation is protected i) by one of the interior finishes described in Subsections 9.29.4. to 9.29.9., ii) provided the building does not contain a Group C major occupancy, by sheet metal that is mechanically fastened to the supporting assembly independent of the insulation, is not less than 0.38 mm thick and has a melting point of 650°C or more, or iii) by any thermal barrier that meets the requirements of Clause 3.1.5.15.(2)(e). | obc2019_divb | Div B | 6.2.4.8.(1) | 6.2.4.8. Cov1.1) Foamed plastic insulation conforming to Article 9.25.2.2. is permitted to be used to insulate a galvanized steel, stainless steel or aluminum air duct provided, (a) the foamed plastic insulation applied to the supply ductwork is not less than 3 m from the furnace bonnet, (b) the temperature within the ductwork where the insulation is installed is not greater than 50°C, (c) duct joints are taped with a product conforming to Sentence 6.2.4.9.(1), (d) return air plenums are separated from the foamed plastic insulation, and (e) the foamed plastic insulation is protected in accordance with Article 9.10.17.10.erings, Linings and Insulation | 1.1) Foamed plastic insulation conforming to Article 9.25.2.2. is permitted to be used to insulate a galvanized steel, stainless steel or aluminum air duct provided, (a) the foamed plastic insulation applied to the supply ductwork is not less than 3 m from the furnace bonnet, (b) the temperature within the ductwork where the insulation is installed is not greater than 50°C, (c) duct joints are taped with a product conforming to Sentence 6.2.4.9.(1), (d) return air plenums are separated from the foamed plastic insulation, and (e) the foamed plastic insulation is protected in accordance with Article 9.10.17.10. 6.2.4.8.(3) | Common Sentence | No | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.4.(7) |  | Foamed plastic insulation is permitted to be used in a ceiling space that acts as a return air plenum provided the foamed plastic insulation is protected from exposure to the plenum in accordance with Sentence 3.1.5.14.(4). | obc2019_divb | Div B | 6.2.4.8.(1) | 6.2.4.8. Coverings, Linings and Insulation | 0.1) Except as permitted in Sentences (1) and (1.1), foamed plastic insulation shall not be used as part of an air duct or for insulating an air duct. | Common Sentence | No | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.4.(9) |  | Linings of ducts shall be installed so that they will not interfere with the operation of volume or balancing dampers or of fire dampers, fire stop stop flaps and other closures. | obc2019_divb | Div B | 6.2.4.8.(2) | 6.2.4.8. Coverings, Linings and Insulation | Linings of ducts shall be installed so that they will not interfere with the operation of volume or balancing dampers. 6.2.4.8.(4) | Common Sentence | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.4.(9) | Coverings, Linings, Adhesives and Insulation | Linings of ducts shall be installed so that they will not interfere with the operation of volume or balancing dampers or of fire dampers, fire stop flaps and other closures. | obc2019_divb | Div B | 6.2.3.4.(7) | 6.2.3.4. Duct Coverings, Linings, Adhesives and Insulation | Linings of ducts shall be installed so that they will not interfere with the operation of volume or balancing dampers, fire dampers, fire stop flaps and other closures. 6.2.3.5.(7) | Common Sentence | Yes | Air Duct Systems
2015 | ON | NBC | Div B | 9.33.6.5.(1) | Galvanized Steel or Aluminium Supply Ducts | Galvanized steel or aluminum supply ducts shall conform to Table 9.33.6.5. | obc2019_divb | Div B | 6.2.4.2.(2) | 6.2.4.2. Duct Design | Materials in supply ducts shall conform to Article 6.2.3.2. | Common Sentence | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.5.(2) | Galvanized Steel or Aluminium Supply Ducts | The design of fittings for ducts shall conform to SMACNA ANSI/SMACNA 006-2006 HVAC Duct Construction Standards – Metal and Flexible except that metal thicknesses shall conform to Table 9.33.6.5. | obc2019_divb | Div B | 6.2.4.2.(3) | 6.2.4.2. Duct Design | Galvanized steel or aluminum supply ducts shall conform to Table 6.2.4.2. | Common Sentence | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.6.(1) | Construction of Ducts and Plenums | Where the installation of heating supply ducts in walls and floors creates a space between the duct and construction material, the space shall be fire stopped with noncombustible material at each end. | obc2019_divb | Div B | 6.2.4.3.(2) | 6.2.4.3. Construction and Installation of Ducts and Plenums | Where the installation of heating supply ducts in walls and floors creates a space between the duct and construction material, the space shall be fire stopped with noncombustible material at each end. AND 6.2.3.20.(2) | Common Sentence | No | Air Duct Systems
2015 | ON | NBC | Div B | 9.33.6.6.(2) | Construction of Ducts and Plenums | Ducts shall be securely supported by metal hangers, straps, lugs or brackets, except that, where zero clearance is permitted, wooden brackets are permitted to be used. | obc2019_divb | Div B | 6.2.3.18.(3) | 6.2.3.18. Construction and Installation of Ducts and Plenums | Ducts shall be securely supported by metal hangers, straps, lugs or brackets, except that where zero clearance is permitted, wooden brackets may be used. | Common Sentence | Yes | Air Duct Systems
2015 | ON | NBC | Div B | 9.33.6.6.(2) | Construction of Ducts and Plenums | Ducts shall be securely supported by metal hangers, straps, lugs or brackets, except that, where zero clearance is permitted, wooden brackets are permitted to be used. | obc2019_divb | Div B | 6.2.4.3.(3) | 6.2.4.3. Construction and Installation of Ducts and Plenums | Ducts shall be securely supported by metal hangers, straps, lugs or brackets, except that where zero clearance is permitted, wooden brackets may be used. / AND 6.2.3.20.(3) | Common Sentence | No | Air Duct Systems
2015 | ON | NBC | Div B | 9.33.6.6.(3) | Construction of Ducts and Plenums | All round duct joints shall be tight-fitting and lapped not less than 25 mm. | obc2019_divb | Div B | 6.2.4.3.(4) | 6.2.4.3. Construction and Installation of Ducts and Plenums | All round duct joints shall be tight-fitting and lapped not less than 25 mm. AND 6.2.3.20.(4) | Common Sentence | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.6.(3) | Construction of Ducts and Plenums | All round duct joints shall be tight-fitting and lapped not less than 25 mm. | obc2019_divb | Div B | 6.2.3.18.(4) | 6.2.3.18. Construction and Installation of Ducts and Plenums | All round duct joints shall be tight-fitting and lapped not less than 25 mm. | Common Sentence | Yes | Air Duct Systems
2015 | ON | NBC | Div B | 9.33.6.6.(4) | Construction of Ducts and Plenums | Rectangular duct connections shall be made with S and drive cleats or equivalent mechanical connections. | obc2019_divb | Div B | 6.2.4.3.(5) | 6.2.4.3. Construction and Installation of Ducts and Plenums | Rectangular duct connections shall be made with S and drive cleats. | Common Sentence | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.6.(4) | Construction of Ducts and Plenums | Rectangular duct connections shall be made with S and drive cleats or equivalent mechanical connections. | obc2019_divb | Div B | 6.2.3.18.(5) | 6.2.3.18. Construction and Installation of Ducts and Plenums | Rectangular duct connections shall be made with S and drive cleats. | Common Sentence | Yes | Air Duct Systems
2015 | ON | NBC | Div B | 9.33.6.7.(2) | Installation of Ducts and Plenums | Trunk supply ducts shall not be nailed directly to wood members. | obc2019_divb | Div B | 6.2.4.3.(6) | 6.2.4.3. Construction and Installation of Ducts and Plenums | Trunk supply ducts shall not be nailed directly to wood members. AND 6.2.3.18(6) | Common Sentence | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.7.(3) | Installation of Ducts and Plenums | Branch ducts shall be supported at suitable spacings to maintain alignment and prevent sagging. | obc2019_divb | Div B | 6.2.3.18.(7) | 6.2.3.18. Construction and Installation of Ducts and Plenums | Branch ducts shall be supported at suitable spacings to maintain alignment and prevent sagging. | Common Sentence | Yes | Air Duct Systems
2015 | ON | NBC | Div B | 9.33.6.7.(3) | Installation of Ducts and Plenums | Rectangular duct connections shall be made with S and drive cleats or equivalent mechanical connections. | obc2019_divb | Div B | 6.2.4.3.(7) | 6.2.4.3. Construction and Installation of Ducts and Plenums | Rectangular duct connections shall be made with S and drive cleats. 6.2.4.3.(5) AND 6.2.3.20.(5) | Common Sentence | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.7.(6) | Installation of Ducts and Plenums | Ducts in or beneath concrete slabs-on-ground shall be watertight and corrosion-, decay-, and mildew-resistant. | obc2019_divb | Div B | 6.2.4.3.(9) | 6.2.4.3. Construction and Installation of Ducts and Plenums | Ducts in or beneath concrete slabs-on-ground shall be watertight, corrosion-, decay- and mildew-resistant. | Common Sentence | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.8.(2) | Clearances of Ducts and Plenums | Where the plenum clearance required in Sentence (1) is 75 mm or less, the clearance between a supply duct and combustible material shall a) be equal to the required plenum clearance within 450 mm of the plenum, and b) be not less than 12 mm at a distance of 450 mm or more from the plenum, except that this clearance may be reduced to zero beyond a bend or offset in the duct sufficiently large to shield the remainder of the supply duct from direct radiation from the furnace heat exchanger. (See Note A-3.6.5.6.(2).) | obc2019_divb | Div B | 6.2.4.10.(1) | 6.2.4.10. Clearances of Ducts and Plenums | Where the plenum clearance is 75 mm or less, the clearance between a supply duct and combustible material shall, (a) be equal to the required plenum clearance within 450 mm of the plenum, and (b)be not less than 12 mm at a distance of 450 mm or more from the plenum, except that this clearance may be reduced to zero beyond a bend or offset in the duct sufficiently large to shield the remainder of the duct from direct radiation from the furnace heat exchanger. | Common Sentence | No | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.8.(3) | Clearances of Ducts and Plenums | Where the plenum clearance required in Sentence (1) is more than 75 mm but not more than 150 mm, the clearance between a supply duct and combustible material shall be a) equal to the required plenum clearance within a horizontal distance of 1.8 m of the plenum, and b) not less than 12 mm at a horizontal distance of 1.8 m or more from the plenum, except that this distance may be reduced to zero beyond a bend or offset in the duct sufficiently large to shield the remainder of the duct from direct radiation from the furnace heat exchanger. (See Note A-3.6.5.6.(3).) | obc2019_divb | Div B | 6.2.4.10.(2) | 6.2.4.10. Clearances of Ducts and Plenums | Where the plenum clearance is more than 75 mm but not more than 150 mm, the clearance between a supply duct and combustible material shall,(a) be equal to the required plenum clearance within a horizontal distance of 1 800 mm of the plenum, and (b) be not less than 12 mm at a horizontal distance of 1 800 mm or more from the plenum, except that this distance may be reduced to zero beyond a bend or offset in the duct sufficiently large to shield the remainder of the duct from direct radiation from the furnace heat exchanger. | Common Sentence | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.8.(4) | Clearances of Ducts and Plenums | Where the plenum clearance required in Sentence (1) is more than 150 mm, the clearance between a supply duct and combustible material shall be a) equal to the required plenum clearance within a horizontal distance of 1 m of the plenum, b) not less than 150 mm within a horizontal distance between 1 m and 1.8 m from the plenum, and c) not less than 25 mm at a horizontal distance of 1.8 m or more from the plenum, except that this distance may be reduced to 8 mm beyond a bend or offset in the duct sufficiently large to shield the remainder of the supply duct from direct radiation from the furnace heat exchanger. (See Note A-3.6.5.6.(4).) | obc2019_divb | Div B | 6.2.4.10.(3) | 6.2.4.10. Clearances of Ducts and Plenums | Where the plenum clearance is more than 150 mm, the clearance between a supply duct and combustible material shall,(a) be equal to the required plenum clearance within a horizontal distance of 1 000 mm of the plenum, (b) be not less than 150 mm within a horizontal distance between 1 000 mm and 1 800 mm from the plenum, and (c) be not less than 25 mm at a horizontal distance of 1 800 mm or more from the plenum, except that this distance may be reduced to 8 mm beyond a bend or offset in the duct sufficiently large to shield the remainder of the supply duct from direct radiation from the furnace heat exchanger. | Common Sentence | No | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.8.(5) | Clearances of Ducts and Plenums | Where a register is installed in a floor directly over a pipeless furnace, a double-walled register box with not less than 100 mm between walls, or a register box with the warm-air passage completely surrounded by the cold-air passage, shall be permitted in lieu of the clearances listed in Sentences (2), (3) and (4). | obc2019_divb | Div B | 6.2.4.10.(4) | 6.2.4.10. Clearances of Ducts and Plenums | Where a register is installed in a floor directly over a pipeless furnace, a double-walled register box with not less than 100 mm between walls, or a register box with the warm-air passage completely surrounded by the cold-air passage, shall be permitted in lieu of the clearances listed in Sentences (1), (2) and (3). | Common Sentence | No | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.9.(1) | Adjustable Dampers and Balance Stops | All branch supply ducts that are not fitted with diffusers with adjustable balance stops shall be supplied with adjustable dampers and fitted with devices to indicate the positions of the dampers. | obc2019_divb | Div B | 6.2.4.6.(1) | 6.2.4.6.Adjustable Dampers and Balance Stops | All branch supply ducts that are not fitted with diffusers with adjustable balance stops shall be supplied with accessible dampers that can be adjusted and fixed in their adjusted positions and that include devices to indicate the positions of the dampers. 9.32.3.7.(9) | Common Sentence | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.8.4.(2) | Protection | Unprotected steam or hot water pipes that pass through a storage space shall be covered with not less than 25 mm thickness of noncombustible insulation to prevent direct contact with the material stored. | obc2019_divb | Div B | 6.2.9.5.(2) | Protection | Unprotected steam or hot water pipes that pass through a storage space shall be covered with not less than 25 mm of noncombustible insulation to prevent direct contact with the material stored. | Common Sentence | No | Piping for Heating and Cooling Systems
2015 | ON | NBC | Div B | 3.6.5.4.(6) | Coverings, Linings, Adhesives and Insulation | Foamed plastic insulation is permitted to be installed in a ceiling space that is used as a return air plenum provided the foamed plastic insulation is protected from exposure to the plenum in accordance with Article 3.1.5.14. | obc2019_divb | Div B | 6.2.3.4.(5) | 6.2.3.4. Duct Coverings, Linings, Adhesives and Insulation |  | National Only | No | Air Duct Systems
2015 | ON | NBC | Div B | 3.6.5.8.(2) | Return-Air System | If any part of a return duct will be exposed to radiation from the furnace heat exchanger or other radiating part within the furnace, that part of a return duct directly above or within 600 mm of the outside furnace casing shall be noncombustible. | obc2019_divb | Div B | 6.2.3.20.(2) | 6.2.3.20. Return-Air System Ducts and Plenums |  | National Only | No | Air Duct Systems
2015 | ON | NBC | Div B | 3.6.5.8.(3) | Return-Air System | Return ducts serving solid-fuel-burning furnaces shall be constructed of noncombustible material. | obc2019_divb | Div B | 6.2.3.20.(3) | 6.2.3.20. Return-Air System Ducts and Plenums |  | National Only | No | Air Duct Systems
2015 | ON | NBC | Div B | 3.6.5.8.(4) | Return-Air System | Combustiblereturn ducts shall be lined with noncombustible material below floor registers, at the bottom of vertical ducts, and under furnaces having a bottom return. | obc2019_divb | Div B | 6.2.3.20.(4) | 6.2.3.20. Return-Air System Ducts and Plenums |  | National Only | No | Air Duct Systems
2015 | ON | NBC | Div B | 3.9.1.1.(1) | Definition | For the purpose of this Section,the term “self-service storage building” shall mean a building that is open to the public for the sole purpose of providing individual self-service storage units. | obc2019_divb | Div B |  |  |  | National Only | Yes | Self-service Storage Buildings
2015 | ON | NBC | Div B | 4.1.1.3.(4) | Design Requirements | Falsework, scaffolding, and formwork shall be designed in conformance with a) CSA S269.1, “Falsework for Construction Purposes,” (b) CSAS269.2,“Access Scaffolding for Construction Purposes,”or (c) CAN/CSA-S269.3-M, “Concrete Formwork.” | obc2019_divb | Div B |  |  |  | National Only | Yes | Temporary Works
2015 | ON | NBC | Div B | 4.2.3.2.(2) | Preservation Treatment of Wood | Where timber has been treated as required in Sentence (1) ,it shall be cared for as provided in AWPA M4,“Care of Preservative-Treated Wood Products,”as revised by Clause 6 of CAN/CSA-O80 Series,“WoodPreservation.” | obc2019_divb | Div B |  |  |  | National Only | Yes | Preservation Treatment of Wood
2015 | ON | NBC | Div B | 6.2.1.2.(2) | Outdoor Design Conditions | Except as provided in Sentence 6.3.2.14.(1), the outdoor air quality conditions of the geographic area of the building site to be used in designing ventilation systems shall conform to appropriate provincial or territorial requirements or, in the absence of such requirements, shall be equal to or less than the maximum acceptable levels stated in the Canada-wide Standards for Particulate Matter (PM)and Ozone as follows: (a) a 24 hour average of 30 µg/m3 for particulate matter that is 2.5 µm or less in diameter (PM2.5), and (b) an 8 hour average of 65ppb for ground-level ozone. (See Note A-6.2.1.2.(2).) | obc2019_divb | Div B |  |  |  | National Only | Yes | Ventilation
2015 | ON | NBC | Div B | 6.2.1.2.(3) | Outdoor Design Conditions | The outdoor air quality conditions of the local area of the building site to be used in designing ventilation systems shall conform to appropriate provincial or territorial requirements or,in the absence of such requirements, to the requirements of Sentence 6.3.2.14.(2). (See Note A-6.2.1.2.(3).) | obc2019_divb | Div B |  |  |  | National Only | Yes | Design and Installation
2015 | ON | NBC | Div B | 6.3.1.2.(1) | Crawl Spaces and Attic or Roof Spaces | Unconditioned and unoccupied crawl spaces and unconditioned and unoccupied attic or roof spaces shall be ventilated by natural or mechanical means as required by Part 5. (See Note A-6.3.1.2.(1).) | obc2019_divb | Div B |  |  |  | National Only | Yes | Ventilation
2015 | ON | NBC | Div B | 6.3.2.11.(1) | Return-Air System | Return-air systems shall comply with Article 3.6.5.8. | obc2019_divb | Div B |  |  |  | National Only | Yes | Air Duct Systems
2015 | ON | NBC | Div B | 6.3.2.11.(2) | Return-Air System | Where a ceiling space is used as a return-air plenum, the requirements of Article 3.6.4.3. shall apply. | obc2019_divb | Div B |  |  |  | National Only | Yes | Air Duct Systems
2015 | ON | NBC | Div B | 6.3.2.11.(3) | Return-Air System | A public corridor or exit shall not be used as a return-air plenum. |  | Div B |  |  |  | National Only | Yes | Air Duct Systems
2015 | ON | NBC | Div B | 6.3.2.14.(1) | Cleaning Devices | Where outdoor air quality conditions do not meet the requirements of Sentence 6.2.1.2.(2), ventilation required by Sentence 6.3.1.1.(1) shall be provided by a ventilation system designed to include devices that reduce particles and gases to the maximum acceptable levels described in Sentence 6.2.1.2.(2)prior to the introduction of outdoor air to indoor occupied spaces. | obc2019_divb | Div B |  |  |  | National Only | Yes | Ventilation
2015 | ON | NBC | Div B | 6.3.2.14.(2) | Cleaning Devices | Where contaminants of concern are present in the outdoor air of the local area of the building site, ventilation required by Sentence 6.3.1.1.(1)shall be provided by a ventilation system designed to include devices that reduce the concentrations of contaminants to those permitted in the ACGIH’s “Industrial Ventilation: A Manual of Recommended Practice for Design” prior to the introduction of outdoor air to indoor occupied spaces. | obc2019_divb | Div B |  |  |  | National Only | Yes | Ventilation
2015 | ON | NBC | Div B | 6.3.2.15.(3) | Evaporative Cooling Towers, Evaporative Fluid Coolers and Evaporative | Make-up water connections shall be equipped with backflow prevention devices that conform to Article2.6.2.1. of Division B of the NPC. | obc2019_divb | Div B |  |  |  | National Only | Yes | Ventilation
2015 | ON | NBC | Div B | 6.3.2.15.(5) | Evaporative Cooling Towers, Evaporative Fluid Coolers and Evaporative | Drains, overflows and blow-downs shall be connected to the building’s drainage system in accordance with Clause 2.4.2.1.(1)(e) of Division B of the NPC. | obc2019_divb | Div B |  |  |  | National Only | Yes | Ventilation
2015 | ON | NBC | Div B | 6.3.2.16.(1) | Evaporative Air Coolers, Misters, Atomizers, | The filter and water evaporation medium of every air washer and evaporative air cooler enclosed within a building shall be made of noncombustible material. |  | Div B |  |  |  | National Only | Yes | Ventilation
2015 | ON | NBC | Div B | 6.3.2.4.(1) | Connections in Air Duct Systems | Air duct systems shall have tight-fitting connections throughout. | obc2019_divb | Div B |  |  |  | National Only | Yes | Air Duct Systems
2015 | ON | NBC | Div B | 6.3.2.5.(1) | Duct Coverings and Linings | Coverings,linings and associated adhesives and insulation used in air ducts, plenums and other parts of air duct systems shall comply with Article 3.6.5.4. | obc2019_divb | Div B |  |  |  | National Only | Yes | Air Duct Systems
2015 | ON | NBC | Div B | 6.3.2.5.(2) | Duct Coverings and Linings | Duct linings shall be installed so that they will not interfere with the operation of volume or balancing dampers or of fire dampers, firestop flaps and other closures. | obc2019_divb | Div B |  |  |  | National Only | Yes | Air Duct Systems
2015 | ON | NBC | Div B | 6.3.2.6.(1) | Clearance of Ducts and plenums | The clearance of ducts and plenums from combustible materials shall comply with Article 3.6.5.6. | obc2019_divb | Div B |  |  |  | National Only | Yes | Air Duct Systems
2015 | ON | NBC | Div B | 6.3.3.1.(2) | Requirement for Venting | Except as provided in Article 6.2.1.5., vented products of combustion, other than those referred to in Sentence (1), shall be discharged away from the building, so as not to re-enter it, to a distance not less than a) 2.15 m above sidewalks and driveways, b) 3m from outdoor air intakes, c) 3 m horizontally or vertically from doors and operable windows, and d) 3 m horizontally or vertically from occupiable outdoor spaces, excluding maintenance spaces. (See Note A-6.3.3.1.(2).) | obc2019_divb | Div B |  |  |  | National Only | Yes | Chimneys and Venting Equipment
2015 | ON | NBC | Div B | 6.3.4.2.(3) | General Ventilation | A ventilation system required by this Subsection shall be maintained in conformance with Article 5.5.4.1. of Division B of the NFC. | obc2019_divb | Div B |  |  |  | National Only | Yes | Ventilation for Laboratories
2015 | ON | NBC | Div B | 6.8.1.3.(1) | Odour Removal Equipment | When odour removal equipment of the adsorption type is used,it shall be (a) installed to allow access so that adsorption material can be reactivated or renewed, and (b) protected from dust accumulation by air filters installed on the inlet side | obc2019_divb | Div B |  |  |  | National Only | Yes | Design and Installation
2015 | ON | NBC | Div B | 6.8.1.3.(2) | Odour Removal Equipment | Facilities for flushing and drainage shall be provided where filters are designed to be washed in place. | obc2019_divb | Div B |  |  |  | National Only | Yes | Design and Installation
2015 | ON | NBC | Div B | 6.9.1.1.(1) | Fire Safety Requirements | The fire safety characteristics of heating, ventilating and air-conditioning systems shall comply with Subsection 3.6.5. | obc2019_divb | Div B |  |  |  | National Only | Yes | Air Duct Systems
2015 | ON | NBC | Div B | 6.9.1.1.(2) | Fire Safety Requirements | Characteristics referred to in Sentence (1)include but are not limited to (a) use of combustible materials in duct systems, (b) flame-spreadratings and smoke-developed ratings of duct and pipe materials and coverings, c) installation of equipment relative to property lines, and (d) requirements for fire dampers and fire stop flaps. | obc2019_divb | Div B |  |  |  | National Only | Yes | Air Duct Systems
2015 | ON | NBC | Div B | 7.1.2.1.(1) | Conformance with Regulations or National Plumbing Code | Every plumbing system shall be designed and installed in conformance with appropriate provincial or territorial regulations or municipal bylaws, in the absence of such regulations or bylaws, in conformance with the NPC. | [5 empty] | National Only | Yes | Application and General Requirements
2015 | ON | NBC | Div B | 7.1.3.2.(1) | Dwelling Units | Dwelling units shall be equipped with plumbing facilities as required in Section 9.31 | [5 empty] | National Only | Yes | Application and General Requirements
2015 | ON | NBC | Div B | 9.33.6.11.(1) |  | 1) In a dwelling unit, a warm-air supply outlet shall be provided in each finished room that is located adjacent to unheated space. | obc2019_divb | Div B | 6.2.4.4.(1) | 6.2.4.4.Warm-Air Supply Outlets |  | National Only | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.11.(2) |  | 2) Except as provided in Sentence (3), when a room described in Sentence (1) is located adjacent to exterior walls, such outlet shall be located so as to bathe at least one exterior wall or window with warm air, except in bathrooms, utility rooms or kitchens, where this may not be practical. | obc2019_divb | Div B | 6.2.4.4.(2) | 6.2.4.4.Warm-Air Supply Outlets |  | National Only | No | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.11.(3) |  | 3) Where the heating system is also designed to provide ventilation air, ceiling outlets or outlets located high on interior walls are permitted to be installed, provided the outlets are designed for this purpose and are installed with diffusers. | obc2019_divb | Div B | 6.2.4.4.(3) | 6.2.4.4.Warm-Air Supply Outlets |  | National Only | No | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.11.(4) |  | 4) At least one warm-air supply outlet shall be provided for each 40 m2 of floor surface area in unfinished basements serving dwelling units, and it shall be located so as to provide adequate distribution of warm air throughout the basement. | obc2019_divb | Div B | 6.2.4.4.(4) | 6.2.4.4.Warm-Air Supply Outlets |  | National Only | No | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.11.(5) |  | 5) At least one warm-air supply outlet shall be provided for each 80 m2 of floor surface area in heated crawl spaces serving dwelling units, and it shall be located so as to provide adequate distribution of warm air throughout the crawl space. | obc2019_divb | Div B | 6.2.4.4.(5) | 6.2.4.4.Warm-Air Supply Outlets |  | National Only | No | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.11.(6) |  | 6) Except for pipeless furnaces, the capacity of warm-air supply outlets serving dwelling units shall be not less than the design heat loss from the area served and shall not exceed 3 kW per outlet. | obc2019_divb | Div B | 6.2.4.4.(6) | 6.2.4.4.Warm-Air Supply Outlets |  | National Only | No | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.11.(7) |  | 7) In basements and heated crawl spaces, the calculated heat gain from the supply ducts and plenum surfaces is permitted to be considered in calculating the design heat loss. | obc2019_divb | Div B | 6.2.4.4.(7) | 6.2.4.4.Warm-Air Supply Outlets |  | National Only | No | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.11.(8) |  | 8) The temperature of supply air at warm-air supply outlets shall not exceed 70°C. | obc2019_divb | Div B | 6.2.4.4.(8) | 6.2.4.4.Warm-Air Supply Outlets |  | National Only | No | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.11.(9) |  | 9) Warm-air supply outlets located in finished areas shall be provided with diffusers and adjustable openings and shall not be located on a furnace plenum. | obc2019_divb | Div B | 6.2.4.4.(9) | 6.2.4.4.Warm-Air Supply Outlets |  | National Only | No | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.12.(1) |  | 1) Return-air inlets shall not be installed in an enclosed room or crawl space that provides combustion air to a furnace. | obc2019_divb | Div B | 6.2.4.7.(13) | 6.2.4.7. Return-Air System |  | National Only | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.12.(2) |  | 2) Except for unfinished areas and floor levels which are less than 900 mm above or below an adjacent floor level which is provided with a return-air inlet, at least one return-air inlet shall be provided in each floor level in a dwelling unit. | obc2019_divb | Div B | 6.2.4.7.(11) | 6.2.4.7. Return-Air System |  | National Only | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.12.(3) |  | 3) Provision shall be made for the return of air from all rooms by leaving gaps beneath doors, using louvred doors or installing return duct inlets. | obc2019_divb | Div B | 6.2.4.7.(12) | 6.2.4.7. Return-Air System |  | National Only | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.13.(1) |  | 1) The return-air system shall be designed to handle the entire air supply. | obc2019_divb | Div B | 6.2.4.7.(1) | 6.2.4.7. Return-Air System |  | National Only | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.13.(3) |  | 3) Return ducts serving solid-fuel-burning furnaces shall be constructed of noncombustible material. | obc2019_divb | Div B | 6.2.4.7.(4) | 6.2.4.7. Return-Air System |  | National Only | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.13.(4) |  | 4) Combustible return ducts shall be lined with noncombustible material a) below floor registers, b) at the bottom of vertical ducts, and c) under furnaces having a bottom return. | obc2019_divb | Div B | 6.2.4.7.(5) | 6.2.4.7. Return-Air System |  | National Only | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.13.(5) |  | 5) Spaces between studs or joists used as return ducts shall be separated from the unused portions of such spaces by tight-fitting metal stops or wood blocking. | obc2019_divb | Div B | 6.2.4.7.(6) | 6.2.4.7. Return-Air System |  | National Only | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.13.(6) |  | 6) A vertical return duct shall have openings to return air on not more than one floor. | obc2019_divb | Div B | 6.2.4.7.(7) | 6.2.4.7. Return-Air System |  | National Only | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.13.(7) |  | 7) The return-air system shall be designed so that the negative pressure from the circulating fan cannot a) affect the furnace combustion air supply, nor b) draw combustion products from joints or openings in the furnace or flue pipe. | obc2019_divb | Div B | 6.2.4.7.(9) | 6.2.4.7. Return-Air System |  | National Only | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 9.33.6.7.(5) | Installation of Ducts and Plenums | Duct systems shall have no openings other than those required for the proper operation and maintenance of the system. | obc2019_divb | Div B | 6.2.4.3.(8) | 6.2.4.3. Construction and Installation of Ducts and Plenums |  | National Only | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B | 5.7.2.1.(1) | Application |  | obc2019_divb | Div B | 5.1.4.2.(3) | 5.1.4.2. Resistance to Deterioration | Design and construction of assemblies separating dissimilar environments and assemblies exposed to the exterior shall be in accordance with good practice, such as described in CSA S478, "Guideline on Durability in Buildings". | P/T Only | Yes | Durability
2015 | ON | NBC | Div B | 9.33.1.1.(3) |  |  | obc2019_divb | Div B | 6.2.4.7.(10) | 6.2.4.7. Return-Air System | Except as provided in Sentence (14), return-air from a dwelling unit shall not be recirculated to any other dwelling unit. | P/T Only | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B |  |  |  |  | Div B | 5.6.2.3.(1) | 5.6.2.3. Solar Collector System | A solar collector system is permitted to be installed above roofing materials conforming to Table 5.10.1.1. | P/T Only | Yes | Precipitation Management
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.4.3.(1) | 6.2.4.3. Construction and Installation of Ducts and Plenums | Rectangular panels in plenums and ducts more than 300 mm wide shall be shaped to provide sufficient stiffness./// occurrs twice in P/T OBC 6.2.3.18.(1) | P/T Only | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.3.18.(8) | 6.2.3.18. Construction and Installation of Ducts and Plenums | Ducts in or beneath concrete slabs-on-ground shall be watertight, corrosion-, decay- and mildew-resistant. | P/T Only | Yes | Air Duct Systems
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 4.4.3.1.(1) | 4.4.3.1. Guards over Retaining Walls | Every retaining wall that is designated in Sentence 1.3.1.1.(1) of Division A shall be protected by guards on all open sides where the public has access to open space at the top of the retaining wall. | P/T Only | Yes | Guards over Retaining Walls
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 4.4.4.1.(1) | 4.4.4.1. Anchor Systems on Building Exterior | Where suspended maintenance and window cleaning operations are intended to be carried out on the exterior of a building described in Article 1.1.2.2. of Division A, anchor systems shall be provided where any portion of the roof is more than 8 m above adjacent ground level. | P/T Only | Yes | Anchor Systems
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 4.4.4.1.(2) | 4.4.4.1. Anchor Systems on Building Exterior | Except as provided in Sentence (3), the anchor systems in Sentence (1) shall be designed, installed and tested in conformance with CAN/CSA-Z91, “Health and Safety Code for Suspended Equipment Operations”. | P/T Only | Yes | Anchor Systems
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 4.4.4.1.(3) | 4.4.4.1. Anchor Systems on Building Exterior | Other anchor systems may be used where such systems provide an equal level of safety. | P/T Only | Yes | Anchor Systems
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 4.4.4.1.(4) | 4.4.4.1. Anchor Systems on Building Exterior | The anchor system material shall be made of stainless steel, or other corrosion resistant base material, or from steel that is hot dipped galvanised, in accordance with CAN/CSA-G164-M, “Hot Dip Galvanizing of Irregularly Shaped Articles”. | P/T Only | Yes | Anchor Systems
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 4.4.5.1.(1) | 4.4.5 Liquid Manure Storage | (1) Liquid manure storage tanks shall be constructed of steel, reinforced concrete or prestressed concrete. (2) Liquid manure storage tank walls, bases and appurtenances, including piping for the conveyance of liquid manure and associated connections and joints, shall be designed and constructed to prevent leakage of contents. (3) Concrete for liquid manure storage tanks shall, (a) be made from HS or HSb cement, (b) have a 28-day strength of at least 32 MPa, and (c) have a water/cement materials ratio of not more than 0.45. (4) Liquid manure storage tanks shall be placed on undisturbed soil free of any organic, deleterious and extraneous materials and capable of supporting the superimposed design loads from the tanks. (5) Where granular fills are used between the bases of liquid manure storage tanks and the undisturbed soil, the granular fills shall be compacted to a Standard Proctor density of not less than 95%. | P/T Only | Yes | Liquid Manure Storage Tanks
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.1.1.(1) | 3.11.1.1. Application | This Section applies to every public pool. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.1.1.(2) | 3.11.1.1. Application | This Section applies to the design and construction of site assembled and manufactured pools that are intended for use as public pools. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.1.1.(3) | 3.11.1.1. Application | Where material alterations to a public pool or the equipment installed in a public pool affect the bottom slope, the water volume or the capacity of the recirculation system, the adversely affected portions shall comply with the requirements of this Division. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.1.1.(4) | 3.11.1.1. Application | Where material alterations or repairs concern any pool fitting passing water and/or air in or out of the pool tank, the affected fitting shall comply with Sentences 3.11.8.1.(14) to (20). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.2.1.(1) | 3.11.2.1. Pool Designations | Every public pool shall be designated as being either a Class A pool or a Class B pool in accordance with Sentence (2) or (3). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.2.1.(2) | 3.11.2.1. Pool Designations | A Class A pool is a public pool to which the general public is admitted or that is, operated in conjunction with or as a part of a program of an educational, instructional, physical fitness or athletic institution or association, supported in whole or in part by public funds or public subscription, or operated on the premises of a recreational camp, for use by campers and their visitors and camp personnel. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.2.1.(3) | 3.11.2.1. Pool Designations | A Class B pool is a public pool that is, operated in conjunction with six or more dwelling units, suites, single family residences, or any combination of them for the use of occupants or residents and their visitors, operated in conjunction with a mobile home park for the use of residents or occupants and their visitors, operated on the premises of a hotel for the use of its guests and their visitors, operated on the premises of a campground for the use of its tenants and their visitors, operated in conjunction with a club for the use of its members and their visitors, or operated in conjunction with an establishment or institution classified in Table 3.1.2.1. as, Group B, Division 1, major occupancy, or Group B, Division 2 or 3, major occupancy, for the use of residents or occupants and their visitors. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.3.1.(1) | 3.11.3.1. Construction Requirements | Except as otherwise required in Subsections 3.11.4., 3.11.5., 3.11.6. and 3.11.7. or otherwise exempted in Sentences (2) and (3), Class A pools and Class B pools shall be designed and constructed to comply with Sentences (2) to (26) and Articles 3.11.3.2. and 3.11.3.3. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.3.1.(2) | 3.11.3.1. Construction Requirements | Where a Class B pool is constructed for use solely in conjunction with a club, child care facility, day camp or establishment or institution for the care of persons who are infirm, aged or in custodial care, the pool shall be exempt from the requirements of Clause (9)(a) and Sentences (13) and (14). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.3.1.(3) | 3.11.3.1. Construction Requirements | Where a Class B pool is constructed for use solely in conjunction with an establishment or institution for the treatment of persons with disabilities or persons who are ill, the pool shall be exempt from the requirements of Sentences (6) and (7), Clause (9)(a) and Sentences (13) and (14). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.3.1.(4) | 3.11.3.1. Construction Requirements | A public pool shall be constructed to have a water depth of not less than 750 mm except for, a modified pool, a wave action pool, a pool for therapeutic use, a beach entry ramp, and a pool described in Sentence 3.11.5.2.(1). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.3.1.(5) | 3.11.3.1. Construction Requirements | The beach entry ramp permitted in Clause (4)(d) shall be protected with permanent barriers between 900 mm to 1 200 mm along the pool deck to prevent entry into the pool until the minimum water pool depth is 750 mm. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.3.1.(6) | 3.11.3.1. Construction Requirements | Except for a modified pool, a wave action pool and a pool used exclusively for scuba diving, the slope of the bottom of any portion of a public pool shall not exceed, 8% where the water depth is 1 350 mm or less, 33% where the water depth is more than 1 350 mm and less than 2 000 mm, and 50% where the water depth is 2 000 mm or more. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.3.1.(7) | 3.11.3.1. Construction Requirements | Except for a modified pool and wave action pool, where the slope of any portion of the bottom of a public pool is more than 8%, the walls of the pool shall be equipped with recessed fittings to which a safety line supported by buoys can be attached across the surface of the water and the recessed fittings shall be installed at a horizontal distance of at least 300 mm measured from the vertical projection of the top of the slope in the direction of the shallow end of the pool. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.3.1.(8) | 3.11.3.1. Construction Requirements | Except for a modified pool, wave action pool and a pool described in Sentence 3.11.5.2.(1), the side and end walls of a public pool shall be vertical from the top of the walls to within 150 mm of the bottom except at steps or recessed ladders or in water depths of 1 350 mm or more. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.3.1.(9) | 3.11.3.1. Construction Requirements | Except for a modified pool and wave action pool and except as provided in Sentence (11), a public pool shall be surrounded by a hard-surfaced pool deck that shall, except for a pool described in Sentence 3.11.5.2.(1), be not less than 1 800 mm wide, in the case of an outdoor pool, be sloped away from the pool to waste drains or to adjacent lower ground at a slope of between 2% and 4%, and in the case of an indoor pool, be impervious and sloped away from the pool to waste drains at a slope of between 1% and 4%. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.3.1.(10) | 3.11.3.1. Construction Requirements | Where a public pool is constructed with a ledge, the ledge shall, be placed only in parts of the pool where the water depth is 1 350 mm or more, be not more than 200 mm wide, be at least 1 000 mm below the water surface, where located on the side of the pool, be gradually tapered towards the shallow end of the pool in such a manner as to prevent a harmful obstruction, and have a band of contrasting colour along the entire juncture of the side and top of the ledge. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.3.1.(11) | 3.11.3.1. Construction Requirements | Notwithstanding Sentences (12) to (16), where a public pool is constructed on any level surface with walls rising above that surface and has a constant water depth not exceeding 1 100 mm and a water surface area not exceeding 100 m2, the pool deck may be an elevated platform surrounding the pool if it has, an unobstructed width of not less than 900 mm, a height of at least 75 mm above grade or pavement elevation, 6 mm wide openings for drainage, and a non-slip surface that is capable of being kept clean and disinfected. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.3.1.(12) | 3.11.3.1. Construction Requirements | Except for a modified pool and wave action pool, where a pool deck projects over the water surface, the projection shall not exceed 50 mm. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.3.1.(13) | 3.11.3.1. Construction Requirements | Except for a modified pool and wave action pool, the pool deck shall be separated from any adjacent spectator area or gallery and from any spectator access to such area or gallery by a gate or other barrier. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.3.1.(14) | 3.11.3.1. Construction Requirements | Except for a modified pool and wave action pool, the perimeter of the pool deck shall be clearly delineated by a tactile attention indicator conforming to Article 3.8.3.18. and located where any area contiguous to the pool deck may be confused with the deck. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.3.1.(15) | 3.11.3.1. Construction Requirements | Perimeter drainage shall be provided where necessary to prevent surface run-off from draining onto the pool deck. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.3.1.(16) | 3.11.3.1. Construction Requirements | Except for a modified pool, one or more hose bibbs shall be installed near the perimeter of the pool deck in locations convenient for flushing the pool deck. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.3.1.(17) | 3.11.3.1. Construction Requirements | Except for a modified pool and wave action pool, where access to the pool enclosure is over any surface that is not subject to regular cleaning and sanitizing, a foot spray to wash feet by means of a spray running freely to waste shall be provided at each such access. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.3.1.(18) | 3.11.3.1. Construction Requirements | Except for a modified pool and wave action pool, at least, one ladder or set of steps shall be provided in both the deep and shallow areas of a public pool for entry into and egress from the pool water, and one barrier-free access shall be provided for entry into and egress from the water of a public pool as required by Article 3.11.3.3. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.3.1.(19) | 3.11.3.1. Construction Requirements | The pool deck, the submerged parts of a public pool, the walls or partitions adjacent to a pool deck and the pavement or floor adjacent to a pool deck shall have surfaces that permit thorough cleaning. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.3.1.(20) | 3.11.3.1. Construction Requirements | Except for markings for safety or competition purposes, submerged surfaces in public pools shall be finished white or light in colour. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.3.1.(21) | 3.11.3.1. Construction Requirements | Except in a modified pool, a black disc 150 mm in diameter on a white background shall be affixed to the bottom of a public pool within the area of its greatest depth. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.3.1.(22) | 3.11.3.1. Construction Requirements | A public pool shall be equipped with lockable doors or other barriers capable of preventing public access to the pool deck. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.3.1.(23) | 3.11.3.1. Construction Requirements | Except for a modified pool, wave action pool or a pool installed at a recreational camp, a Class A pool shall be provided with, where the water surface area is greater than 150 m2 but not greater than 230 m2, at least one lifeguard control station, and where the water surface area is greater than 230 m2, at least two lifeguard control stations. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.3.1.(24) | 3.11.3.1. Construction Requirements | Except for a modified pool, every public pool shall display on the deck clearly marked figures, not less than 100 mm high, that set out, the water depths indicating the deep points, the breaks between gentle and steep bottom slopes and the shallow points, the words SHALLOW AREA at one or more appropriate locations, and where the water depth exceeds 2 500 mm, the words DEEP AREA at one or more appropriate locations. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.3.1.(25) | 3.11.3.1. Construction Requirements | Except for a modified pool and a pool to which Sentence 3.11.5.2.(2) applies, every public pool having a maximum water depth of 2 500 mm or less shall display a warning notice posted in a location clearly visible to divers on which are printed in letters at least 150 mm high the words CAUTION — AVOID DEEP DIVES or SHALLOW WATER — NO DIVING. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.3.1.(26) | 3.11.3.1. Construction Requirements | Except where no space is provided between ladder treads and the pool wall, the space between the pool wall and submerged portions of any treads of a ladder for entry into and egress from the water shall be not more than 150 mm and not less than 75 mm. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.3.2.(1) | 3.11.3.2. Barrier-Free Path of Travel for Outdoor Pool Deck | Where an outdoor pool is provided, a barrier-free path of travel shall be provided to and throughout the normally occupied portions of the pool deck. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.3.3.(1) | 3.11.3.3. Access into Public Pools | Access for entry into and egress from the water of a public pool provided in a storey that is required by Article 3.8.2.1. to have a barrier-free path of travel shall be barrier-free and shall be provided by, a ramp conforming to, Article 3.11.5.1., and Article 3.11.5.2., in the case of a pool described in Sentence 3.11.5.2.(1), or a pool lift conforming to the manufacturer’s specifications and installation instructions and conforming to Sentences (2) to (6). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.3.3.(2) | 3.11.3.3. Access into Public Pools | Except where the entire pool depth is greater than 1 220 mm, where a pool lift is installed, at least one lift shall be located where the water level does not exceed 1 220 mm. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.3.3.(3) | 3.11.3.3. Access into Public Pools | The centre line of the seat for the pool lift shall be located over the deck and a minimum of 400 mm from the edge of the pool when in the raised position. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.3.3.(4) | 3.11.3.3. Access into Public Pools | A clear deck space located parallel with the seat for the pool lift and on the side of the seat opposite the water shall, be at least 915 mm wide, and extend forward not less than 1 220 mm from a line located 305 mm behind the rear edge of the seat. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.3.3.(5) | 3.11.3.3. Access into Public Pools | The pool lift shall be, designed to be operable without assistance from both the deck and water, and designed so that, when in use, its controls and operating mechanisms are unobstructed. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.3.3.(6) | 3.11.3.3. Access into Public Pools | The pool lift shall, have a weight capacity of at least 135 kg, and be capable of sustaining a static load of at least 1.5 times the rated load. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.4.1.(1) | 3.11.4.1. Diving Boards or Platforms | No diving board or diving platform shall be installed in a public pool unless the requirements of Sentences (5) to (17) are met but the requirements for a diving platform do not apply to a starting platform. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.4.1.(2) | 3.11.4.1. Diving Boards or Platforms | No diving board or diving platform shall be installed in a modified pool or a wave action pool. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.4.1.(3) | 3.11.4.1. Diving Boards or Platforms | Where a public pool is equipped with a diving board or a diving platform, the board or platform shall have a non-slip surface. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.4.1.(4) | 3.11.4.1. Diving Boards or Platforms | Where a diving board or a diving platform in a public pool is more than 600 mm above the water surface, the board or platform shall be equipped with one or more adjacent handrails. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.4.1.(5) | 3.11.4.1. Diving Boards or Platforms | Where a public pool is equipped with a diving board or a diving platform not more than 3 m in height above the water surface, the pool shall be designed and constructed in conformance with Sentences (6) to (15). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.4.1.(6) | 3.11.4.1. Diving Boards or Platforms | The depth of water in the area directly below a horizontal semi-circle in front of a diving board or diving platform having a radius of 3 m measured from any point on the front end of the board or platform shall not be less than, 2 750 mm, where a board is 600 mm or less in height above the water surface, 3 m, where a board or platform is greater than 600 mm but not more than 1 000 mm in height above the water surface, and 3.65 m, where a board or platform is greater than 1 000 mm but not more than 3 m in height above the water surface. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.4.1.(7) | 3.11.4.1. Diving Boards or Platforms | Except as permitted in Sentence (8), the water depth in a public pool shall be at least 1 350 mm at the horizontal arc having a radius of 9 m measured from any point on the front end of the diving board or diving platform and intersecting the vertical projections of the walls of the pool. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.4.1.(8) | 3.11.4.1. Diving Boards or Platforms | Where a Class B pool is equipped with a diving board 600 mm or less in height above the water, the water depth shall be at least 1 350 mm at the horizontal arc having a radius of 7.5 m measured from any point on the front end of the diving board, and a warning notice, on which is printed in letters at least 150 mm high, the words DANGER — AVOID DEEP OR LONG DIVES, shall be posted in a location clearly visible to divers. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.4.1.(9) | 3.11.4.1. Diving Boards or Platforms | The slope of the bottom of a public pool having a diving board or diving platform shall not change by more than 17% where the water depth is less than the applicable depth set out in Sentence (6) and greater than the depth set out in Sentence (7) or (8), as applicable. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.4.1.(10) | 3.11.4.1. Diving Boards or Platforms | The horizontal distance between the vertical projection of the centre line of a diving board or diving platform and the vertical projection of the centre line of another board or platform shall be at least 2 750 mm. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.4.1.(11) | 3.11.4.1. Diving Boards or Platforms | The horizontal distance between the centre line of a diving board or diving platform and the vertical projection of the closest side or any ledge on the closest side of a public pool shall be at least, 3 m, where a diving board or diving platform is 1 000 mm or less in height above the water surface, and 3.6 m, where a diving board or diving platform is greater than 1 000 mm in height above the water surface. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.4.1.(12) | 3.11.4.1. Diving Boards or Platforms | A diving board or a diving platform 600 mm or less in height above the water surface shall project over the water a horizontal distance of at least 900 mm from the vertical projection of a pool wall under it. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.4.1.(13) | 3.11.4.1. Diving Boards or Platforms | A diving board greater than 600 mm in height above the water surface shall project over the water a horizontal distance of at least 1 500 mm from the vertical projection of the pool wall under it. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.4.1.(14) | 3.11.4.1. Diving Boards or Platforms | A diving platform greater than 600 mm in height above the water surface shall project a horizontal distance of at least 1 200 mm from the vertical projection of the pool wall under it. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.4.1.(15) | 3.11.4.1. Diving Boards or Platforms | The space above a diving board or diving platform shall be unobstructed and shall consist of at least, a space having a width of 2 500 mm on each side of the centre line of the board or platform, a length equal to the sum of the horizontal distance the board or platform projects over the water plus 3 m, and a height of, 3.65 m above a diving board 3.65 m or less in length, 5 m above a diving board greater than 3.65 m in length, or 3 m above a diving platform, and the space below the planes originating from the front and sides of the uppermost horizontal plane of the space determined under Clause (a) and sloping downwards at 30° from the horizontal. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.4.1.(16) | 3.11.4.1. Diving Boards or Platforms | A diving board or diving platform greater in height than 3 m above the water surface shall be equipped with a gate, barrier or other device capable of preventing access to the diving board or diving platform. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.4.1.(17) | 3.11.4.1. Diving Boards or Platforms | Where a public pool is to be equipped with diving boards or diving platforms greater than 3 m in height above the water surface, the design of the diving boards or diving platforms and the corresponding water depths and clearances shall be in accordance with FINA, "Rules and Regulations - FINA Facilities Rules 2009-2013 - FR5 Diving Facilities". | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.5.1.(1) | 3.11.5.1. Ramps into Public Pools | Where barrier-free access for entry into and egress from the water of a public pool is provided by a ramp as required by Clause 3.11.3.3.(1)(a), the pool shall be designed and constructed in accordance with Sentences (2) to (4). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.5.1.(2) | 3.11.5.1. Ramps into Public Pools | A ramp shall have, along each side a handrail that, has a height of not less than 865 mm and not more than 965 mm, and runs parallel to the slope of the ramp, a width of at least 1 100 mm, a curb or other means to prevent a wheelchair from falling off the side of the ramp, surface finishes capable of being kept clean, sanitary and free from slipperiness, and a landing at the bottom at least 1 500 mm in length and the same width as the ramp. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.5.1.(3) | 3.11.5.1. Ramps into Public Pools | Where a ramp that is not submerged is adjacent to the pool wall and is used for access to the water, the pool shall be constructed so that, the landing at the bottom of the ramp is at least 450 mm but not more than 550 mm below the top of the wall separating the ramp from the pool, the landing is equipped with a floor drain at its lowest point, the top of the wall between the pool and the ramp is at least 250 mm and not more than 300 mm in width, the pool deck is capable of accommodating a movable barrier separating the deck from the ramp, the water depth at the landing is accurately and clearly marked at the landing in figures at least 100 mm high on the top of the wall separating the pool from the ramp, and the ramp has a slope not exceeding 1 in 12. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.5.1.(4) | 3.11.5.1. Ramps into Public Pools | Where a submerged ramp is adjacent to the pool wall and is used for access to the water, the pool shall be constructed so that, the water depth at the bottom of the ramp is at least 600 mm and not greater than 900 mm, a hard-surfaced area that is at least 750 mm wide is contiguous to the entire length of the part of the submerged ramp that pierces any part of the deck, (See Appendix A.) the area described in Clause (b) is capable of accommodating a movable barrier separating the area from the deck, the finishes in submerged portions of the ramps and curbs are different in colour or shade from each other and from that of the pool walls and bottom, and the submerged ramp has a slope not exceeding 1 in 9. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.5.2.(1) | 3.11.5.2. Public Pools in Group B, Division 2 or 3 Major Occupancies | Despite Sentences 3.11.3.1.(4) and (8) and Clause 3.11.3.1.(9)(a), where a public pool is constructed in a building containing a Group B, Division 2 or 3 major occupancy and has a water depth not exceeding 1 500 mm and a water surface area not exceeding 100 m2, the pool deck contiguous to not more than 50% of the total perimeter of the pool may be replaced by one or more ramps that will permit a bather seated in a wheelchair to enter the water with or without the wheelchair. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.5.2.(2) | 3.11.5.2. Public Pools in Group B, Division 2 or 3 Major Occupancies | Despite Sentence 3.11.3.1.(25), a warning notice, on which are printed in letters at least 150 mm high the words CAUTION — NO DIVING, shall be posted conspicuously on each wall or fence line enclosing a pool described in Sentence (1). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.5.2.(3) | 3.11.5.2. Public Pools in Group B, Division 2 or 3 Major Occupancies | There shall be a curb along the perimeter of a pool described in Sentence (1) except at steps, ladders and ramp entrances. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.5.2.(4) | 3.11.5.2. Public Pools in Group B, Division 2 or 3 Major Occupancies | The curb required by Sentence (3) shall have, a height of 50 mm, rounded edges, a coved base, and a raised nosing at the top to serve as a fingerhold for a bather in the water. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.6.1.(1) | 3.11.6.1. Construction Requirements | A modified pool is exempt from Sentences 3.11.3.1.(4) to (9), (12), (13), (14), (16), (17), (18), (21), (23), (24) and (25), Sentence 3.11.8.1.(12) and Article 3.11.3.3. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.6.1.(2) | 3.11.6.1. Construction Requirements | A modified pool shall be designed and constructed to comply with Sentences (3) to (9). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.6.1.(3) | 3.11.6.1. Construction Requirements | A modified pool and its pool deck shall be constructed of hard-surfaced material that permits thorough cleaning. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.6.1.(4) | 3.11.6.1. Construction Requirements | The slope of the bottom of any portion of a modified pool shall not exceed 1 in 12. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.6.1.(5) | 3.11.6.1. Construction Requirements | The depth of the water in any portion of a modified pool shall not be more than 1 800 mm. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.6.1.(6) | 3.11.6.1. Construction Requirements | A modified pool shall be surrounded on all sides by a hard-surfaced pool deck that shall, be at least 3 m wide, have a continuous crest surrounding the pool at least 100 mm above the pool water surface, and be sloped to shed water from the crest to the outer perimeter of the pool deck. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.6.1.(7) | 3.11.6.1. Construction Requirements | A modified pool shall be provided with two or more drain fittings covered with protective grilles with openings having an aggregate area of at least 10 times the internal cross-sectional area of the outlet pipe or pipes connected to the recirculation system that is capable of completely draining the pool. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.6.1.(8) | 3.11.6.1. Construction Requirements | Provision shall be made for lifeguard control stations adjacent to the edge of the water at intervals of not more than 60 m. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.6.1.(9) | 3.11.6.1. Construction Requirements | The bottom of a modified pool shall be marked with continuous black contour lines, 150 mm wide located where the water depth is 600 mm, and 300 mm wide located where the water depth is 1 200 mm. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.7.1.(1) | 3.11.7.1. Construction Requirements | A wave action pool is exempt from Sentences 3.11.3.1.(4) to (9), (12), (13), (14), (17), (18) and (23), Sentence 3.11.8.1.(12) and Article 3.11.3.3. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.7.1.(2) | 3.11.7.1. Construction Requirements | A wave action pool shall be designed and constructed to comply with Sentences (3) to (11). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.7.1.(3) | 3.11.7.1. Construction Requirements | The slope of the bottom of any portion of a wave action pool, shall not exceed 1 in 12 where the still water depth is less than 1 000 mm, and shall not exceed 1 in 9 where the still water depth is 1 000 mm or more. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.7.1.(4) | 3.11.7.1. Construction Requirements | The walls of a wave action pool shall be vertical from the water surface to within 150 mm of the bottom. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.7.1.(5) | 3.11.7.1. Construction Requirements | There shall be a hard-surfaced pool deck at least 3 m wide immediately adjacent to the pool wall at the shallow end of the pool and at least 1 500 mm wide immediately adjacent to all walls of the pool. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.7.1.(6) | 3.11.7.1. Construction Requirements | Provision shall be made for two or more lifeguard control stations on each side of the pool deck adjacent to which the still water depth exceeds 1 000 mm. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.7.1.(7) | 3.11.7.1. Construction Requirements | Sets of steps or ladders recessed into pool side walls and having continuous vertical grab bars on each side of them shall be located at intervals of not more than 7.5 m along portions of the pool where the still water depth exceeds 1 000 mm, except that no steps or ladders shall be located within 3 m of the corners at the deep end of the pool. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.7.1.(8) | 3.11.7.1. Construction Requirements | Except at recessed steps or ladders, the pool deck along each side of a wave action pool adjacent to which the water depth is 2 300 mm or less shall be equipped with a barrier supported by posts or a wall that, is 1 000 mm in height, is located 1 000 mm or less from the side of the pool, and has warning notices affixed to the barrier or wall at intervals not exceeding 7.5 m signifying clearly that jumping and diving are prohibited along the sides of the pool. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.7.1.(9) | 3.11.7.1. Construction Requirements | Skimming devices shall be designed and suitably located to remove surface film when no waves are induced in a wave action pool. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.7.1.(10) | 3.11.7.1. Construction Requirements | A system capable of deactivating the wave-making equipment shall be installed with readily accessible push buttons located on the pool deck not more than 30 m apart, adjacent to each side and the deep end of the pool. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.7.1.(11) | 3.11.7.1. Construction Requirements | A wave action pool shall be equipped with a first-aid room located within 50 m of the pool. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.8.1.(1) | 3.11.8.1. Recirculation Systems | Every public pool shall be equipped with a recirculation system. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.8.1.(2) | 3.11.8.1. Recirculation Systems | For the purposes of this Subsection, the water in a public pool and its recirculation system is deemed not to be potable water. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.8.1.(3) | 3.11.8.1. Recirculation Systems | The water in a public pool and its recirculation system shall be separated from the potable water supply and from the sewer or drainage system into which it drains by air gaps or other devices that prevent, the water in the pool or its recirculation system from flowing back into the potable water supply, and the water in the sewer or drainage system from flowing back into the pool or its recirculation system. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.8.1.(4) | 3.11.8.1. Recirculation Systems | The recirculation system of a public pool shall be designed, constructed and equipped to comply with Sentences (5) to (20). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.8.1.(5) | 3.11.8.1. Recirculation Systems | The recirculation system of a public pool shall be capable of filtering, disinfecting and passing through the pool each day a volume of water of at least, in the case of a Class A pool, other than a modified pool or a wave action pool, six times the total water volume of the pool, in the case of a Class B pool, other than a wave action pool, four times the total water volume of the pool, in the case of a modified pool, three times the total water volume of the pool, and in the case of a wave action pool, six times the total water volume of the pool. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.8.1.(6) | 3.11.8.1. Recirculation Systems | A recirculation system shall be equipped with a flow meter registering the rate of water flow. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.8.1.(7) | 3.11.8.1. Recirculation Systems | All pools shall be provided with automatic make-up water devices and provided with water meters to register the volume of all make-up water added to a public pool or its recirculation system. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.8.1.(8) | 3.11.8.1. Recirculation Systems | Equipment shall be installed to continuously disinfect the water in a public pool by means of, a chlorination or hypochlorination system provided with a chemical controller for regulating the dosage of chlorine and capable of providing not less than, in the case of an outdoor pool, other than a wave action pool, 300 g of chlorine per day per 10 000 L of total pool capacity, in the case of an indoor pool, other than a wave action pool, 200 g of chlorine per day per 10 000 L of total pool capacity, in the case of an outdoor wave action pool, 1 200 g of chlorine per day per 10 000 L of total pool capacity, and in the case of an indoor wave action pool, 800 g of chlorine per day per 10 000 L of total pool capacity, or a bromination system capable of maintaining in the pool water a total bromine residual of 3 mg/L. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.8.1.(9) | 3.11.8.1. Recirculation Systems | Chlorination equipment for a public pool shall contain a mechanism whereby the chlorine feed shall automatically terminate whenever the recirculation system ceases to supply clean water to the pool. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.8.1.(10) | 3.11.8.1. Recirculation Systems | All exposed potable water piping and chlorine piping within a public pool water treatment service room shall be colour coded by means of, painting the entire outer surface of the piping, or coloured bands at least 25 mm in width that are spaced along the piping at intervals of not more than 1 200 mm. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.8.1.(11) | 3.11.8.1. Recirculation Systems | The colour coding referred to in Sentence (10) shall be yellow for chlorine and green for potable water. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.8.1.(12) | 3.11.8.1. Recirculation Systems | Except for a modified pool and wave action pool, a public pool shall be equipped with overflow gutters or surface skimmers connected to the recirculation system that are capable of removing surface film from the surface of the water and withdrawing each day and discharging to the waste drains up to 15% of the total volume of pool water. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.8.1.(13) | 3.11.8.1. Recirculation Systems | A public pool shall be equipped with clean water inlets arranged in conjunction with surface skimmers or overflow gutters to provide uniform distribution and circulation of clean water. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.8.1.(14) | 3.11.8.1. Recirculation Systems | Except as permitted in Sentence (19), all fittings at or below the water surface that allow water and/or air to be passed to or from the public pool shall, have a maximum opening of 7 mm in one direction, and be securely held in place by corrosion resistance fastening that require a tool for removal and are galvanically compatible with the fittings and grilles or covers. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.8.1.(15) | 3.11.8.1. Recirculation Systems | Except as provided in Sentence 3.11.6.1.(7) for a modified pool, all fittings below the water surface that provide suction or gravity flow in a public pool shall, be provided with a minimum of two suction or gravity outlets interconnected to a full size manifold, and be separated by a clear distance of not less than 1 200 mm. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.8.1.(16) | 3.11.8.1. Recirculation Systems | Except as provided in Sentence 3.11.6.1.(7) for a modified pool, water in all public pools shall be capable of being emptied through the pool drains in 12 hours or less. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.8.1.(17) | 3.11.8.1. Recirculation Systems | Except as provided in Sentence 3.11.6.1.(7) for a modified pool, openings in suction or gravity fittings shall, be such that the flow of water does not exceed 0.45 m/s and the velocity is calculated assuming all possible sources of suction flow are present at one time, and be such that every suction fitting located within 1 000 mm of the water surface, except for skimmers and gutter fittings, contain openings with a minimum aggregate area of 0.2 m2. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.8.1.(18) | 3.11.8.1. Recirculation Systems | Except for skimmers and gutters, all submerged suction and gravity fittings shall be clearly and permanently marked with a 50 mm wide band in a contrasting colour. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.8.1.(19) | 3.11.8.1. Recirculation Systems | Fittings returning water and/or air to the pool tank that are located within 300 mm of the water surface are permitted to have openings with one dimension more than 7 mm but shall contain no openings more than 25 mm in diameter. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.8.1.(20) | 3.11.8.1. Recirculation Systems | Submerged skimmer equalizer fittings and vacuum fittings are not permitted in public pools. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.9.1.(1) | 3.11.9.1. Dressing Rooms and Sanitary Facilities | Except as otherwise permitted in Sentences (2) and (3), every public pool shall be equipped with dressing rooms, locker rooms, shower heads, water closets, urinals, lavatories and drinking fountains that shall be designed, constructed and equipped to comply with Sentences (4) to (14). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.9.1.(2) | 3.11.9.1. Dressing Rooms and Sanitary Facilities | Where a Class A pool is installed on the premises of a recreational camp, dressing rooms, locker rooms, shower heads, water closets, urinals, lavatories and drinking fountains are not required if, dressing, water closet and shower facilities are conveniently available for bathers elsewhere on the premises, and foot sprays are provided in accordance with Sentence 3.11.3.1.(17). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.9.1.(3) | 3.11.9.1. Dressing Rooms and Sanitary Facilities | Where a Class B pool is installed, dressing rooms, locker rooms, shower heads, lavatories, water closets, drinking fountains and urinals are not required if, dressing, water closet and shower facilities are conveniently available elsewhere on the premises for bathers when the pool is open for use, and foot sprays are provided in accordance with Sentence 3.11.3.1.(17). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.9.1.(4) | 3.11.9.1. Dressing Rooms and Sanitary Facilities | The minimum number of water closets, urinals and lavatories shall be determined from Article 3.7.4.3. and Table 3.7.4.3.C. for an occupant load based on, the formula in Sentence 3.1.17.3.(1) for all public pools, except a wave action pool, or the formula in Sentence 3.1.17.3.(2) for a wave action pool. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.9.1.(5) | 3.11.9.1. Dressing Rooms and Sanitary Facilities | A minimum of one shower head shall be provided for every 40 bathers. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.9.1.(6) | 3.11.9.1. Dressing Rooms and Sanitary Facilities | Where dressing and locker rooms, water closets and urinals are provided in conjunction with a public pool, they shall be located in such a manner that bathers, after using them, shall pass through or by a shower area to reach the pool deck. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.9.1.(7) | 3.11.9.1. Dressing Rooms and Sanitary Facilities | All shower heads shall be supplied with potable water at a pressure of at least 140 kPa. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.9.1.(8) | 3.11.9.1. Dressing Rooms and Sanitary Facilities | The shower water system shall have one or more tempering devices capable of being adjusted to ensure that water supplied to shower heads does not exceed 40°C. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.9.1.(9) | 3.11.9.1. Dressing Rooms and Sanitary Facilities | Floors in washrooms, shower areas and passageways used by bathers shall slope to waste drains at not less than 1% and shall be of hard surfaced materials that do not become slippery when wet. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.9.1.(10) | 3.11.9.1. Dressing Rooms and Sanitary Facilities | Joints between floors and walls shall be coved in areas described in Sentence (9) and in dressing and locker rooms. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.9.1.(11) | 3.11.9.1. Dressing Rooms and Sanitary Facilities | Hose bibbs shall be provided in safe locations convenient for flushing down the walls and floors in washrooms, shower areas and passageways used by bathers. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.9.1.(12) | 3.11.9.1. Dressing Rooms and Sanitary Facilities | Partitions or walls shall be provided to ensure privacy of dressing rooms, washrooms and shower areas. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.9.1.(13) | 3.11.9.1. Dressing Rooms and Sanitary Facilities | The bottom of interior partitions in dressing rooms and washrooms shall be between 250 mm and 350 mm above the floor. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.9.1.(14) | 3.11.9.1. Dressing Rooms and Sanitary Facilities | Dressing and locker room floors shall have non-slip surfaces that permit convenient and thorough cleaning and disinfecting. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.10.1.(1) | 3.11.10.1. Lighting and Emergency Provisions | Except as provided in Sentences (2) and (3), rooms and spaces used by the public in conjunction with a public pool shall be capable of illumination to levels in compliance with Subsection 3.2.7. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.10.1.(2) | 3.11.10.1. Lighting and Emergency Provisions | Dressing rooms, locker rooms, shower rooms, washrooms and passageways shall have an illumination level of at least 200 lx at floor level. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.10.1.(3) | 3.11.10.1. Lighting and Emergency Provisions | An indoor pool or an outdoor pool that is intended to be open for use after sundown shall be equipped with a lighting system, that will maintain at any point on the pool deck and on the pool water surface an illumination level of at least, 200 lx in the case of an indoor pool, and 100 lx in the case of an outdoor pool, and that makes the underwater areas of the pool clearly visible from any point on the pool deck. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.10.1.(4) | 3.11.10.1. Lighting and Emergency Provisions | An outdoor pool that is intended to be open for use after sundown and an indoor pool shall be equipped with an independent emergency lighting system that automatically operates whenever the normal electrical power supply to a public pool lighting system fails. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.10.1.(5) | 3.11.10.1. Lighting and Emergency Provisions | The independent emergency lighting system required in Sentence (4) shall be capable of illuminating the pool deck, washroom, shower, locker areas, pool water surface and all means of egress to a level of at least 10 lx. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.10.1.(6) | 3.11.10.1. Lighting and Emergency Provisions | An emergency power supply for the emergency lighting system required in Sentence (4) shall comply with Sentences 3.2.7.4.(1) and 3.2.7.7.(1) and Article 3.2.7.5. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.10.1.(7) | 3.11.10.1. Lighting and Emergency Provisions | An emergency telephone directly connected to an emergency service or to the local telephone utility shall be installed adjacent to the pool deck of every Class A pool. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.10.1.(8) | 3.11.10.1. Lighting and Emergency Provisions | A telephone accessible for emergency use shall be installed for every Class B pool within 30 m of the pool. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.10.1.(9) | 3.11.10.1. Lighting and Emergency Provisions | Every wave action pool shall have a public address system that shall be clearly audible in all portions of the pool. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.10.1.(10) | 3.11.10.1. Lighting and Emergency Provisions | Every wave action pool shall have a communication system for the use of persons engaged in supervision or operation of the pool that shall be interconnected with each lifeguard control station, the first-aid room and the bather admission control centre. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.10.1.(11) | 3.11.10.1. Lighting and Emergency Provisions | The public address system and the communication system described in Sentences (9) and (10) shall be interconnected. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.10.1.(12) | 3.11.10.1. Lighting and Emergency Provisions | All recirculating pumps used in a public pool shall be capable of being deactivated by an emergency stop button clearly labelled and located at, a Class A pool beside the telephone that is required in Sentence (7), and a Class B pool on the deck area. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.10.1.(13) | 3.11.10.1. Lighting and Emergency Provisions | The emergency stop button in Sentence (12) shall, when used, activate an audible and a visual signal located by the emergency stop. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.10.1.(14) | 3.11.10.1. Lighting and Emergency Provisions | An emergency sign containing the words IN THE EVENT OF AN EMERGENCY PUSH EMERGENCY STOP BUTTON AND USE EMERGENCY PHONE, AUDIBLE AND VISUAL SIGNAL WILL ACTIVATE shall be in letters at least 25 mm high with a 5 mm stroke and posted above the emergency stop button. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.11.1.(1) | 3.11.11.1. Service Rooms and Storage Facilities | In addition to the requirements of this Subsection, service rooms shall comply with the requirements of Sentences 3.6.2.1.(5), 3.6.2.1.(7) and 3.6.2.1.(8) and Articles 3.5.3.3. and 3.6.2.2. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.11.1.(2) | 3.11.11.1. Service Rooms and Storage Facilities | Where compressed chlorine gas is used as a pool water disinfectant, the cylinders or containers of gas shall be located in a service room that, except as provided in Sentences 3.1.9.4.(3) to (7), is separated from the remainder of the building by a 1 h fire separation that is substantially gas tight, is designed for the sole purpose of containing all installed pressurized chlorine gas apparatus and piping and storing all chlorine gas containers or chlorine gas cylinders that are individually secured against toppling, is located at or above ground level, is provided with an exit door opening to the outdoors, has screened openings to the outdoors with at least one opening located within 150 mm from the floor and at least one opening located within 150 mm from the ceiling, each opening being 2% of the area of the floor, is equipped with emergency mechanical ventilation capable of producing at least 30 air changes per hour, taking suction at a maximum of 900 mm above the floor level and discharging at least 2 500 mm above ground level directly to the outdoors, and contains a platform weigh scale of at least 135 kg capacity for each chlorine cylinder in use. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.11.1.(3) | 3.11.11.1. Service Rooms and Storage Facilities | Storage facilities shall be provided for the safe storage of all chemicals required in pool operations. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.11.1.(4) | 3.11.11.1. Service Rooms and Storage Facilities | The storage facilities shall be ventilated and shall be equipped with a water hose connection and a floor drain. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.11.11.1.(5) | 3.11.11.1. Service Rooms and Storage Facilities | Service rooms and storage facilities, including rooms and facilities that contain electrical or mechanical equipment or chemicals or chemical feeders, shall be equipped with a secure locking device. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.1.1.(1) | 3.12.1.1. Application | This Section applies to the design and construction of site-assembled public spas and factory-built public spas. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.1.1.(2) | 3.12.1.1. Application | If material alterations to a public spa or the equipment installed in a public spa affect the bottom slope, the water volume or the capacity of the water circulation system, the adversely affected portions shall comply with the requirements of this Division. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.1.1.(3) | 3.12.1.1. Application | Except as provided in Sentence (4), if material alterations or repairs concern any pool fitting that passes water or air, or both, in or out of the pool tank, the affected fitting shall comply with Sentences 3.11.8.1.(20) and 3.12.4.1.(4) to (10). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.1.1.(4) | 3.12.1.1. Application | If the material alterations or repairs concern a fitting cover or grille, the affected fitting cover or grille shall comply with Sentences 3.12.4.1.(7) to (10). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.1.1.(5) | 3.12.1.1. Application | For the purposes of this Section, every reference to a public pool or a recirculation system in a definition in Article 1.4.1.2. of Division A, or a Sentence or Clause in Section 3.11. that is made applicable to public spas by this Section, is deemed to be a reference to a public spa or water circulation system, respectively. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.2.1.(1) | 3.12.2.1. Construction Requirements | In addition to the requirements of this Subsection, public spas shall comply with the requirements of Sentences 3.11.3.1.(13) to (17), (19), (20) and (22) and Clause 3.11.3.1.(24)(a). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.2.1.(2) | 3.12.2.1. Construction Requirements | A public spa shall be constructed to have a water depth of not more than 1 200 mm. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.2.1.(3) | 3.12.2.1. Construction Requirements | The slope of the bottom of any portion of a public spa shall not exceed 8%. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.2.1.(4) | 3.12.2.1. Construction Requirements | A public spa shall be surrounded by a hard-surfaced pool deck that, shall have a minimum clear deck space of not less than 1.8 m at the main entrance point, shall have a clear deck space of 900 mm on all sides, except as required by Clause (a) and permitted by Sentence (5), shall be sloped away from the pool to waste drains or to adjacent lower ground at a slope of between 2% and 4%, in the case of an outdoor public spa, and shall be impervious and sloped away from the pool to waste drains at a slope of between 1% and 4%, in the case of an indoor public spa. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.2.1.(5) | 3.12.2.1. Construction Requirements | One section of the hard-surfaced pool deck that does not exceed 25% of the perimeter of the public spa may have a minimum clear deck space of not more than 300 mm if, the public spa has an area less than 6 m2, and the public spa has no interior dimension more than 2.5 m. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.2.1.(6) | 3.12.2.1. Construction Requirements | The maximum depth of water to a seat or bench in a public spa shall be 600 mm. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.2.1.(7) | 3.12.2.1. Construction Requirements | If a set of steps is provided for entry into and egress from the public spa water, the steps, shall be equipped with a handrail, shall have a non-slip surface, and shall have a band of contrasting colour along the entire juncture of the side and top of the edges. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.2.1.(8) | 3.12.2.1. Construction Requirements | Every public spa shall be provided with dressing rooms, water closets and shower facilities that are conveniently available on the premises. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.2.1.(9) | 3.12.2.1. Construction Requirements | Except where no space is provided between ladder treads and the spa wall, the space between the spa wall and submerged portions of any treads of a ladder for entry into and egress from the water shall be not more than 150 mm and not less than 75 mm. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.3.1.(1) | 3.12.3.1. Ramps into Public Spas | Not more than 50% of the total perimeter of a public spa may be replaced by one or more ramps that permit a bather seated in a wheelchair to enter the water with or without the wheelchair. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.3.1.(2) | 3.12.3.1. Ramps into Public Spas | If a public spa has one or more ramps described in Sentence (1), the public spa shall comply with Article 3.11.5.1. and Sentences 3.11.5.2.(3) and (4). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.3.2.(1) | 3.12.3.2. Access into Public Spas | Where more than one public spa is provided within a suite located on a storey that is required by Article 3.8.2.1. to have a barrier-free path of travel, a barrier-free access described in Sentence (2) shall be provided to at least one public spa. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.3.2.(2) | 3.12.3.2. Access into Public Spas | Barrier-free access for entry into and egress from a public spa shall be provided by, a ramp conforming to Article 3.12.3.1., a pool lift conforming to the manufacturer’s specifications and installation instructions and conforming to Sentences 3.11.3.3.(2) to (6), or a transfer wall conforming to Sentences (3) to (5). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.3.2.(3) | 3.12.3.2. Access into Public Spas | A transfer wall providing barrier-free access for entry into and egress from a public spa shall, have a height not less than 405 mm and not more than 485 mm measured from the pool deck, have a depth of at least 300 mm and not more than 400 mm, be slip-resistant and have edges that are rounded, and have at least one grab bar that, is perpendicular to the pool and extends the full depth of the transfer wall, is located not less than 100 mm and not more than 150 mm above the transfer wall, has a clearance of at least 610 mm on both sides, complies with Clauses 3.8.3.8.(7)(a) and (b), and is made of a slip-resistant material. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.3.2.(4) | 3.12.3.2. Access into Public Spas | The deck area required to make a lateral transfer to the transfer wall shall, be outside and adjacent to the barrier-free path of travel described in Sentence (1), have no obstructions at the side of the transfer wall serving the transfer space, have a clear space of 900 mm by 2 200 mm, and have a slope less than 2% provided at the base of the transfer wall surface. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.3.2.(5) | 3.12.3.2. Access into Public Spas | The deck area described in Clause (4)(c) shall be centred on, the grab bar where one grab bar is provided, or the clear space between the grab bars where more than one grab bar is provided. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.4.1.(1) | 3.12.4.1. Water Circulation Systems | In addition to the requirements of this Subsection, the water circulation system of a public spa shall comply with the requirements of Sentences 3.11.8.1.(2), (3), (6), (7), (9), (10), (11), (13) and (20). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.4.1.(2) | 3.12.4.1. Water Circulation Systems | A public spa shall be equipped with a water circulation system that is capable of filtering, disinfecting and passing the public spa water through the public spa with a turnover period of not more than, 30 minutes for a public spa with a volume of water that exceeds 6 m3, 20 minutes for a public spa with a volume of water that exceeds 4 m3 but does not exceed 6 m3, or 15 minutes for a public spa with a volume of water that does not exceed 4 m3. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.4.1.(3) | 3.12.4.1. Water Circulation Systems | If cartridge-type filters are used for a public spa, the filters shall be a surface-type that is designed for a maximum flow rate of 0.27 L/s/m2 effective filter area. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.4.1.(4) | 3.12.4.1. Water Circulation Systems | Except as provided in Sentence (6), every circulation system in a public spa shall be served by a minimum of two suction or gravity outlets, that are interconnected to a full size manifold, and except as provided in Sentence (5), that are separated by a clear distance of not less than 900 mm. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.4.1.(5) | 3.12.4.1. Water Circulation Systems | If compliance with Clause (4)(b) is impracticable because of dimensional restrictions at the bottom of the public spa, the outlets may be located on two different planes of the public spa if, at least one of the outlets through which the public spa can be emptied to a full-size manifold is located on the bottom of the public spa, and the bottom of all outlets, other than skimmers, are not more than 75 mm from the floor of the public spa. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.4.1.(6) | 3.12.4.1. Water Circulation Systems | A circulation system in a factory-built public spa may be served by a built-in suction or gravity outlet with multiple openings that are connected to a full-size manifold. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.4.1.(7) | 3.12.4.1. Water Circulation Systems | All fittings at or below the water surface that allow water or air or both to be passed to or from the public spa shall be securely held in place by corrosion resistant fastening that requires a tool for removal and is galvanically compatible with the fittings and grilles or covers. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.4.1.(8) | 3.12.4.1. Water Circulation Systems | Except as provided in Sentence (9), all suction or gravity fittings installed at or below the water line of a public spa shall, have a maximum opening of 7 mm in one direction, and be designed so that the flow of water through the openings does not exceed 0.45 m/s. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.4.1.(9) | 3.12.4.1. Water Circulation Systems | Sentence (8) does not apply to suction and gravity outlets that are equipped with anti-entrapment covers that comply with the requirements of ASME A112.19.8, "Suction Fittings for Use in Swimming Pools, Wading Pools, Spas, and Hot Tubs". | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.4.1.(10) | 3.12.4.1. Water Circulation Systems | The calculation of water velocities for the purposes of Clause (8)(b) and Sentences (11) and (12) and the calculation of water flow rates for the purposes of Sentence (9) shall be based on the assumption that all possible sources of suction flow are present at the same time. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.4.1.(11) | 3.12.4.1. Water Circulation Systems | The water velocity in a suction pipe shall not exceed 1.8 m/s. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.4.1.(12) | 3.12.4.1. Water Circulation Systems | The water velocity in a pressure pipe shall not exceed, 3.0 m/s for plastic piping, and 1.8 m/s for copper piping. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.4.1.(13) | 3.12.4.1. Water Circulation Systems | Every suction system that serves a public spa shall be equipped with a vacuum relief mechanism that shall include, a vacuum release system, a vacuum limit system, or other engineered systems that are designed, constructed and installed to conform to good engineering practice appropriate to the circumstances. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.4.1.(14) | 3.12.4.1. Water Circulation Systems | Equipment shall be installed to continuously disinfect the water in a public spa by means of a chlorination, hypochlorination or bromination system that is capable of regulating the dosage of chlorine or bromine. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.4.1.(15) | 3.12.4.1. Water Circulation Systems | If a two-speed pump is utilized for a public spa, the filter and heater shall be sized to accommodate the maximum pump output, without exceeding the manufacturer’s design flow rate of the filter element or heater and without by-passing the filter element. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.4.1.(16) | 3.12.4.1. Water Circulation Systems | A public spa equipped with hydro-massage jet fittings shall be provided with a timing device, that controls the period of operation of the jet pump, and that is placed in a location where the user must exit the public spa to reset the timer. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.4.1.(17) | 3.12.4.1. Water Circulation Systems | A public spa water heater shall be equipped with an upper limit cut-off device, that is independent of the normal public spa water temperature thermostat, and that limits the maximum water temperature of the public spa to 40°C. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.4.1.(18) | 3.12.4.1. Water Circulation Systems | A public spa shall be equipped with a water circulation system that is capable of both completely and partially draining and refilling the public spa water. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.5.1.(1) | 3.12.5.1. Lighting and Emergency Provisions | In addition to the requirements of this Subsection, public spas shall comply with the requirements of Sentences 3.11.10.1.(1) to (6). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.5.1.(2) | 3.12.5.1. Lighting and Emergency Provisions | An emergency telephone directly connected to an emergency service or to the local telephone utility shall be installed within 30 m of the public spa. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.5.1.(3) | 3.12.5.1. Lighting and Emergency Provisions | All pumps used in a public spa shall be capable of being deactivated by an emergency stop button that is, clearly labelled, and located at a point that is, readily accessible to and within sight of persons using the public spa, and within 15 m of the public spa. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.5.1.(4) | 3.12.5.1. Lighting and Emergency Provisions | The emergency stop button required in Sentence (3) shall, be a switch separate from the public spa’s timing device, activate an audible and a visual signal when used, and have an emergency sign conforming to Sentence 3.11.10.1.(14). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.5.1.(5) | 3.12.5.1. Lighting and Emergency Provisions | If a public spa and public pool are located in the same room or space, the emergency stop buttons required in Sentences (3) and 3.11.10.1.(12) shall deactivate all pumps serving the public spa and public pool. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.12.6.1.(1) | 3.12.6.1. Service Rooms and Storage Facilities | Service rooms and storage facilities for all public spas shall comply with the requirements of Article 3.11.11.1. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.1.1.(1) | 3.13.1.1. Scope | Except as provided in this Section the requirements in this Division apply to rapid transit stations. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.1.2.(1) | 3.13.1.2. Definitions | In this Section: Ancillary space means the rooms or spaces in the station used only by the transit agency to house or contain operating, maintenance or support equipment and functions, but does not include booths and kiosks used by the transit agency or service rooms. Central supervising station means the operations centre where the transit agency controls and co-ordinates the system-wide movement of passengers and vehicles and from which communication is maintained with supervisory and operating personnel of the transit agency and with participating agencies when required. Crush load means the total of the seating capacity and the standing capacity of a car where, the seating capacity is the number of seats in a car, and the standing capacity is 0.2 m2 per person for the standing area which is measured 300 mm in front of the seats.Egress capacity means the number of people able to travel from or through a type of egress facility in a specified period of time. Entraining load means the number of passengers boarding the train at a station. Fare-paid area means that portion of a rapid transit station to which access is gained by a pass or by paying a fare. Fare-paid area control means the point where passengers enter or leave the fare-paid area. Link load means the number of passengers on board the train(s) travelling between two stations. Maximum calculated train load means the crush load per car multiplied by the maximum number of cars per train in the peak period. Peak direction means, for each route, the direction of train travel having the largest passenger flow volume based on the sum of the incoming link load plus the entraining load per peak hour. Protected route means that portion of a means of egress that starts at the point where passengers would not be vulnerable to exposure from a train fire and that leads to the exterior of the station or through an exit to an adjacent building. Public area means the public circulation areas in a rapid transit station providing pedestrian access to and from trains. Rapid transit station means a building or part of a building used for the purpose of loading and unloading passengers of a rapid transit system but does not include open air shelters at street level. Rapid transit system means an electrified transportation system, utilizing guidance methods involving positive mechanical contact with the fixed way operating on a right-of-way for the mass movement of passengers. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.2.1.(1) | 3.13.2.1. Requirements for Stations | Except as provided in this Subsection, the requirements in Subsections 3.2.1. and 3.2.2. do not apply to a rapid transit station. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.2.1.(2) | 3.13.2.1. Requirements for Stations | The requirements in Sentence (3) shall apply to, a rapid transit station erected entirely below the adjoining finished ground level, and the underground portion of a rapid transit station. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.2.1.(3) | 3.13.2.1. Requirements for Stations | Except as permitted in Sentence (4), an underground station or an underground portion of a station in Sentence (2) shall be of noncombustible construction, and, floor assemblies shall be fire separations having a fire-resistance rating not less than 2 h, roof assemblies below ground level, shall have a fire-resistance rating not less than 2 h, but a fire-resistance rating is not required where steel tunnel liners are left in place to form part of the assembly and the tunnel liners are in direct contact with soil, and all loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.2.1.(4) | 3.13.2.1. Requirements for Stations | An interior stair extending to street level is permitted to be protected by a combustible roof. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.2.1.(5) | 3.13.2.1. Requirements for Stations | Where a rapid transit station is erected above and below the adjoining finished ground level, the above ground portion of the station shall be of noncombustible construction and shall conform to the requirements in Sentence (10). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.2.1.(6) | 3.13.2.1. Requirements for Stations | Where a rapid transit station is erected entirely above the adjoining finished ground level and is a stand-alone building, the station shall be of noncombustible construction and shall conform to the requirements in Sentence (11). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.2.1.(7) | 3.13.2.1. Requirements for Stations | Openings for stairways and escalators used by passengers are permitted to penetrate the fire separations required in Sentences (2) to (6). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.2.1.(8) | 3.13.2.1. Requirements for Stations | Elevator shafts are permitted to penetrate the fire separations required in Sentences (2) to (6) provided they are enclosed by, a fire separation having a fire-resistance rating not less than 1 h, or wired glass assemblies conforming to MMAH Supplementary Standard SB-2, "Fire Performance Ratings". | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.2.1.(9) | 3.13.2.1. Requirements for Stations | Openings for other than stairways, escalators or elevators are permitted to penetrate the fire separations required in Sentences (2) to (6) provided the openings are protected by a closure having a fire-protection rating not less than 45 min. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.2.1.(10) | 3.13.2.1. Requirements for Stations | The building shall be of noncombustible construction and, floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h, mezzanines shall have a fire-resistance rating not less 1 h, roof assemblies shall have a fire-resistance rating not less than 1 h, and all loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.2.1.(11) | 3.13.2.1. Requirements for Stations | Except as provided in Sentence (12), the building shall be of noncombustible construction, and, floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, mezzanines shall have a fire-resistance rating not less than 1 h, roof assemblies shall have a fire-resistance rating not less than 1 h, and all loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.2.1.(12) | 3.13.2.1. Requirements for Stations | A building classified as Group A, Division 2 occupancy that is not more than 1 storey in building height, and in which the building area is not more than 3 200 m2 if not sprinklered, or 6 400 m2 if sprinklered, is permitted to be constructed with a roof of heavy timber construction and have columns of heavy timber construction. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.3.1.(1) | 3.13.3.1. Application | Except as provided in this Subsection and Subsection 3.13.4., the requirements in Subsections 3.3.1. and 3.6.2. apply to a rapid transit station. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.3.1.(2) | 3.13.3.1. Application | A door in a fire separation is permitted to be equipped with pivot hinges in conformance with NFPA 80, "Fire Doors and Other Opening Protectives". | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.3.1.(3) | 3.13.3.1. Application | The requirements in Subsection 3.4.4. for fire separation of exits do not apply in a rapid transit station. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.3.1.(4) | 3.13.3.1. Application | Except as provided in Sentence (5), the requirements in Sentence 3.4.6.16.(1) for doors to be readily opened from the inside apply to required exit doors in a rapid transit station. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.3.1.(5) | 3.13.3.1. Application | Where a group of two or more doors serves as a single exit facility, only one door in the group is required to comply with Sentence 3.4.6.16.(1). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.3.1.(6) | 3.13.3.1. Application | A door that is required to be readily opened in Sentence (4) or (5) shall have a sign attached to it that, displays the words EMERGENCY EXIT with the letters not less than 25 mm high, and is visible from the exit approach. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.3.2.(1) | 3.13.3.2. Booths and Kiosks | Booths and kiosks that are not more than 20 m2 in area and are used only by the transit agency for fare collection, dissemination of information or similar non-mercantile occupancies shall be of noncombustible construction and are not required to be separated from the remainder of the floor area by a fire separation. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.3.2.(2) | 3.13.3.2. Booths and Kiosks | Booths and kiosks that are more than 20 m2 in area and are used only by the transit agency for fare collection, dissemination of information or similar non-mercantile occupancies shall be, sprinklered, and separated from the remainder of the floor area by a fire separation of noncombustible construction that is not required to have a fire-resistance rating. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.3.2.(3) | 3.13.3.2. Booths and Kiosks | A door acting as a closure in the fire separation in Sentence (2) is not required to be equipped with a self-closing device. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.3.3.(1) | 3.13.3.3. Service Rooms and Ancillary Spaces | An ancillary space in a rapid transit station shall be separated from the remainder of the floor area by a fire separation having a fire-resistance rating not less than 1 h. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.3.3.(2) | 3.13.3.3. Service Rooms and Ancillary Spaces | Except as provided in Sentence (3), a door opening from a service room onto a means of egress in a rapid transit station shall be located not less than 5 m from an escalator balustrade and from the top and bottom riser of a flight used as a means of egress from the rapid transit station. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.3.3.(3) | 3.13.3.3. Service Rooms and Ancillary Spaces | The requirements in Sentence (2) do not apply where, the service room is sprinklered, or there is a vestibule between the service room and the means of egress. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.3.3.(4) | 3.13.3.3. Service Rooms and Ancillary Spaces | Where a door from a service room opens onto a means of egress less than 5 m wide, the service room shall be sprinklered, or there shall be a vestibule between the service room and the means of egress. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.3.4.(1) | 3.13.3.4. Leased Areas | All leased areas within a rapid transit station shall be, sprinklered, and separated from the remainder of the floor area by a fire separation of noncombustible construction that is not required to have a fire-resistance rating. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.3.4.(2) | 3.13.3.4. Leased Areas | A door acting as a closure in the fire separation in Clause (1)(b) is not required to be equipped with a self-closing device. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.3.4.(3) | 3.13.3.4. Leased Areas | Where leased areas are located on opposite sides of a means of egress, the width of the means of egress shall not be reduced to less than 5 m. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.3.4.(4) | 3.13.3.4. Leased Areas | Except as provided in Sentence (5), where the leased area on any floor level exceeds 15% of the public area on that level, the public area shall be sprinklered. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.3.4.(5) | 3.13.3.4. Leased Areas | In a rapid transit station that is erected entirely above the adjoining finished ground level and is a stand-alone building, where the leased area on any floor level exceeds 20% of the public area on that level, the public area shall be sprinklered. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.3.4.(6) | 3.13.3.4. Leased Areas | In determining the leased area in Sentences (4) and (5), it is not necessary to include a leased area that is separated from the public area by a fire separation having a fire-resistance rating not less than, 2 h where the leased area contains a mercantile or medium hazard industrial occupancy, or 1 h where the leased area contains any other occupancy. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.3.4.(7) | 3.13.3.4. Leased Areas | A leased area is permitted on a platform level provided it is, located not less than 5 m from the platform edge, located not less than 5 m from an egress facility, and not located in a dead end portion of the platform. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.3.5.(1) | 3.13.3.5. Vehicle Terminal | Where an enclosed terminal serves vehicles powered by combustible fuels, and the terminal has direct access to a rapid transit station, the terminal shall be sprinklered, and the terminal shall be separated from the rapid transit station, by a fire separation having a fire-resistance rating not less than 1 h, or by wired glass assemblies conforming to MMAH Supplementary Standard SB-2, "Fire Performance Ratings", with wired glass doors equipped with self-closing devices. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.3.5.(2) | 3.13.3.5. Vehicle Terminal | Doors in the fire separation or in the wired glass assembly in Clause (1)(b) are not required to have latches where close spaced sprinkler protection is provided on the station side. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.3.6.(1) | 3.13.3.6. Access to Adjacent Building | Where an access is provided between a rapid transit station and an adjacent building, the station and the building shall be separated by a fire separation having a fire-resistance rating not less than 2 h. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.3.6.(2) | 3.13.3.6. Access to Adjacent Building | The access in Sentence (1) shall be through a vestibule that is separated from the station and from the building, by a fire separation having a fire-resistance rating not less than 1 h, or by wired glass assemblies conforming to MMAH Supplementary Standard SB-2, "Fire Performance Ratings", with wired glass doors equipped with self-closing devices. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.3.6.(3) | 3.13.3.6. Access to Adjacent Building | The vestibule doors in Sentence (2), are not required to be equipped with latches, and shall swing in the direction of travel from the rapid transit station. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.3.6.(4) | 3.13.3.6. Access to Adjacent Building | Close spaced sprinkler protection shall be provided on each side of all vestibule doors. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.3.6.(5) | 3.13.3.6. Access to Adjacent Building | The vestibule shall not contain an occupancy. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.3.6.(6) | 3.13.3.6. Access to Adjacent Building | Where an access is provided between a rapid transit station and an adjacent building, and the building is regulated by the provisions of Subsection 3.2.6. or 3.2.8., these provisions are not required in the rapid transit station. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.3.7.(1) | 3.13.3.7. Emergency Lighting | Emergency lighting shall be provided to average levels not less than 10 lx at floor or tread level in public areas in a rapid transit station. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.3.7.(2) | 3.13.3.7. Emergency Lighting | An emergency power supply conforming to Subsection 3.2.7. shall be provided to maintain the emergency lighting required in Sentence (1) for a period of 30 min after a power failure. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.4.1.(1) | 3.13.4.1. Occupant Load | The occupant load for public areas within a rapid transit station shall be, determined in conformance with this Subsection, and based on peak hour patronage as projected for design of the transit system. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.4.1.(2) | 3.13.4.1. Occupant Load | The platform occupant load for each platform in a rapid transit station shall be the greater of the a.m. or p.m. peak period loads calculated in accordance with Sentences (3) to (5). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.4.1.(3) | 3.13.4.1. Occupant Load | The a.m. and the p.m. peak period occupant loads for each platform shall be based on the simultaneous evacuation of the entraining load and the link load for that platform. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.4.1.(4) | 3.13.4.1. Occupant Load | The entraining load for each platform shall be the sum of the entraining loads for each track serving that platform and the entraining load for each track shall be based on the entraining load per train headway multiplied by, a factor of 1.3 to account for surges, and in the peak direction for each route, an additional factor of 2 to account for a missed headway. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.4.1.(5) | 3.13.4.1. Occupant Load | The link load for each platform shall be the sum of the link loads for each track serving that platform and, except as provided in Sentence (6), the link load for each track shall be based on the link load per train headway multiplied by, a factor of 1.3 to account for surges, and in the peak direction for each route, an additional factor of 2 to account for a missed headway. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.4.1.(6) | 3.13.4.1. Occupant Load | The maximum link load at each track shall be the maximum calculated train load. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.4.2.(1) | 3.13.4.2. General Requirements | Except as provided in Sentence (2), escalators conforming to the requirements of Sentences 3.13.4.5.(3) and 3.13.4.6.(1) shall be acceptable as part of a required means of egress in a rapid transit station. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.4.2.(2) | 3.13.4.2. General Requirements | Escalators forming part of a required means of egress shall not comprise more than one-half of the required egress capacity from any one level. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.4.2.(3) | 3.13.4.2. General Requirements | Horizontal exits conforming to Sentence (4) may provide all of the required egress capacity from a rapid transit station. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.4.2.(4) | 3.13.4.2. General Requirements | Horizontal exits to any one building shall not comprise more than one-half of the required egress capacity from any area within a rapid transit station. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.4.2.(5) | 3.13.4.2. General Requirements | A protected route shall be provided with emergency ventilation conforming to Subsection 3.13.7. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.4.2.(6) | 3.13.4.2. General Requirements | In an aboveground unenclosed station, the protected route is permitted to begin at the point of leaving the platform. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.4.2.(7) | 3.13.4.2. General Requirements | In an enclosed or underground station, the protection for the protected route shall consist of, a fire separation having a fire-resistance rating not less than 1 h, construction having a fire-resistance rating not less than 1 h, or wired glass assemblies conforming to MMAH Supplementary Standard SB-2, "Fire Performance Ratings". | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.4.3.(1) | 3.13.4.3. Number and Location of Means of Egress | Each platform in a rapid transit station shall be served by no fewer than two means of egress that are independent of and remote from each other from the platform to the exterior of the station. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.4.3.(2) | 3.13.4.3. Number and Location of Means of Egress | Where a continuous level walking surface is provided between two adjacent platforms, they may be considered as one platform for the purpose of conforming to this Subsection. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.4.3.(3) | 3.13.4.3. Number and Location of Means of Egress | At the platform level, the distance separating the egress facilities in Sentences (1) and (2) shall be the greater of one car length or 25 m. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.4.3.(4) | 3.13.4.3. Number and Location of Means of Egress | Except as required in Sentence (1), two or more means of egress are permitted to converge in conformance with Sentence 3.13.4.4.(6). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.4.3.(5) | 3.13.4.3. Number and Location of Means of Egress | Means of egress from platforms shall be located so that the travel time from the most remote point on a platform to a protected route does not exceed 4 min based on travel speeds of, 38 m/min for horizontal travel, and 21 m/min for vertical rise. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.4.4.(1) | 3.13.4.4. Egress Capacity | For a rapid transit station, the required aggregate egress capacity from each platform shall be determined by dividing the platform occupant load det--------------------ermined in accordance with Sentences 3.13.4.1.(2) to (6) by the required platform clearance time determined in accordance with Sentence (3). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.4.4.(2) | 3.13.4.4. Egress Capacity | Where two platforms are considered as one platform as provided in Sentence 3.13.4.3.(2), the required egress capacity for each platform shall be determined separately. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.4.4.(3) | 3.13.4.4. Egress Capacity | The required platform clearance time shall be 4 min less the travel time between the platform and the entry into the protected route based on travel speeds of, 38 m/min for horizontal travel, and 21 m/min or vertical rise. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.4.4.(4) | 3.13.4.4. Egress Capacity | For each means of egress, the required egress capacity at the platform shall be maintained for the entire length of the means of egress. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.4.4.(5) | 3.13.4.4. Egress Capacity | Except as provided in Sentence (6), where two or more means of egress converge, the required egress capacity beyond that point shall be cumulative. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.4.4.(6) | 3.13.4.4. Egress Capacity | The egress capacity in Sentence (5) need not be cumulative after converging where it can be shown that the platform clearance time in Sentence (3) is not exceeded. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.4.5.(1) | 3.13.4.5. Width of Means of Egress | Except as otherwise required in this Subsection, the required width of means of egress serving platforms in a rapid transit station shall be determined based on, the required egress capacity determined in conformance with Article 3.13.4.4., and the pedestrian flow rate for the type of means of egress facility listed in Table 3.13.4.5. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.4.5.(2) | 3.13.4.5. Width of Means of Egress | In calculating the required width of corridors and ramps with a grade of less than 4%, 300 mm at each sidewall shall be added to the width determined based on required egress capacity. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.4.5.(3) | 3.13.4.5. Width of Means of Egress | In calculating the required width of egress routes, one escalator at each level in a rapid transit station is deemed to be out of service and not available for egress purposes. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.4.5.(4) | 3.13.4.5. Width of Means of Egress | Except as provided in Sentence (5), the minimum width of means of egress facilities serving platforms shall be, 1 750 mm for corridors and ramps, 1 750 mm for stairs, 430 mm for turnstiles, 500 mm for fare collection gates, 600 mm nominal width for escalators, and 900 mm for a door leaf. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.4.5.(5) | 3.13.4.5. Width of Means of Egress | A second means of egress as required by Sentence 3.13.4.3.(1) is permitted to be not less than 1 100 mm wide. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.4.5.(6) | 3.13.4.5. Width of Means of Egress | The minimum width of platforms shall be, 3.2 m for side platforms, and 6.4 m for island platforms. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.4.5.(7) | 3.13.4.5. Width of Means of Egress | The minimum unobstructed width of platforms measured from the platform edge shall be 2.5 m. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.4.6.(1) | 3.13.4.6. Egress Facilities | Escalators forming part of a required means of egress shall, where equipped to run reverse to the direction of egress travel, be capable of being stopped remotely and locally, and have a vertical rise not more than 12 m between floors or landings. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.4.6.(2) | 3.13.4.6. Egress Facilities | Where electrically operated gates or turnstiles used for fare collection are intended to be used as part of a required means of egress from a rapid transit station, provision shall be made to release the gates or turnstiles in accordance with Sentence (4) to allow them to operate freely in the direction of egress travel. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.4.6.(3) | 3.13.4.6. Egress Facilities | Where locked doors that prevent entry into a fare-paid area are to be used as part of a required means of egress from a rapid transit station, provision shall be made to release the doors in accordance with Sentence (4) to allow them to operate freely in the direction of egress travel. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.4.6.(4) | 3.13.4.6. Egress Facilities | The release device required in Sentences (2) and (3) shall be installed as an ancillary device to the fire alarm system and shall release immediately, upon activation of the fire alarm signal, in the event of a power failure or ground fault, or upon actuation of a manually operated switch accessible to authorized personnel and located in, a fare collector’s booth or kiosk at the station, or the central supervising station. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.4.6.(5) | 3.13.4.6. Egress Facilities | After release, the gates or turnstiles in Sentence (2) or the doors in Sentence (3) shall be capable of reactivation only by manual actuation of the switch in Clause (4)(c). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.5.1.(1) | 3.13.5.1. Fire Alarm System | Except as provided in this Subsection, a fire alarm system conforming to Subsection 3.2.4. shall be installed in a rapid transit station. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.5.2.(1) | 3.13.5.2. Exceptions | Manual pull stations need not be installed in a rapid transit station. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.5.2.(2) | 3.13.5.2. Exceptions | Audible signal appliances need not be installed in a rapid transit station. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.5.3.(1) | 3.13.5.3. Fire Detectors | Except where the area is sprinklered, fire detectors shall be installed in every service room, ancillary space, leased space, booth and kiosk. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.5.4.(1) | 3.13.5.4. Central Supervising Station | Each rapid transit station shall be monitored by a central supervising station conforming to CAN/ULC-S561, "Installation and Services for Fire Signal Receiving Centres and Systems". | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.5.5.(1) | 3.13.5.5. Annunciators | An annunciator shall be installed, in a location that is readily accessible to firefighters entering the building, and in the rapid transit station, in a designated collector’s booth, or within viewing distance of a designated collector’s booth. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.5.6.(1) | 3.13.5.6. Annunciator Indication | All fire alarm, fire detectors, valve switches and water flow indicator signals when activated in a rapid transit station shall be indicated on the annunciator at the station. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.5.6.(2) | 3.13.5.6. Annunciator Indication | The annunciator at a rapid transit station shall be monitored simultaneously at the central supervising station. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.5.6.(3) | 3.13.5.6. Annunciator Indication | Where a means of egress from a rapid transit station leads through an adjoining building, any alarm signal originating in the building within 2 storeys above a connection to the station shall, be indicated on the rapid transit station annunciator, and cause a message to flash a warning on a sign located in conformance with Sentence (4), that the means of egress shall not be used as an exit from the station. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.5.6.(4) | 3.13.5.6. Annunciator Indication | A sign required in Clause (3)(b) shall be located, at the doors from the rapid transit station to the adjoining building, and in the means of egress to the adjoining building, at the last point where there is a choice of direction to travel to at least one other exit. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.5.7.(1) | 3.13.5.7. Emergency Power | An emergency power supply conforming to Article 3.2.7.8. shall be provided for the fire alarm system. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.5.8.(1) | 3.13.5.8. Communication Systems | In a rapid transit station, a public address system shall be installed and shall include loudspeakers that, can be operated from the central supervising station, can be operated from the rapid transit station in which they are located, and designed and located so that voice messages can be heard intelligibly throughout the public area in a rapid transit station. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.5.8.(2) | 3.13.5.8. Communication Systems | A two-way communication system shall be installed in each rapid transit station with telephones located at, the collector’s booth, and at each end of each platform. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.5.8.(3) | 3.13.5.8. Communication Systems | The telephones in Sentence (2) shall be provided with connections to the central supervising station. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.5.9.(1) | 3.13.5.9. Emergency Reporting Devices | Emergency reporting devices shall be located on passenger platforms and throughout a rapid transit station such that the distance of travel from any point in the public area to such a device is not more than 90 m. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.5.9.(2) | 3.13.5.9. Emergency Reporting Devices | The emergency reporting devices required in Sentence (1) are permitted to be public telephones with an emergency no charge capability and their location shall be plainly indicated by appropriate signs. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.5.10.(1) | 3.13.5.10. Sprinkler Systems | Sprinkler systems shall conform with the requirements of Articles 3.2.5.13 to 3.2.5.16. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.5.10.(2) | 3.13.5.10. Sprinkler Systems | In addition to the requirements of Subsection 3.13.3. the steel truss enclosure of an escalator shall be sprinklered. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.5.10.(3) | 3.13.5.10. Sprinkler Systems | There shall be identification on a fire department connection for a sprinkler system in a rapid transit station to indicate that the connection is part of the station system. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.5.11.(1) | 3.13.5.11. Standpipe and Hose Systems | A standpipe and hose system conforming to the requirements of Subsection 3.2.9. shall be installed in a rapid transit station, except as otherwise required or permitted in this Article. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.5.11.(2) | 3.13.5.11. Standpipe and Hose Systems | Where a rapid transit station includes more than one standpipe riser there shall be a cross-connection pipe having a diameter not less than 100 mm between each standpipe riser so that supplying of water through any fire department connection will furnish water throughout each riser. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.5.11.(3) | 3.13.5.11. Standpipe and Hose Systems | There shall be identification on a fire department connection for a standpipe system in a rapid transit station to indicate that the connection is part of the station system. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.5.11.(4) | 3.13.5.11. Standpipe and Hose Systems | Hose stations shall be located so that every portion of the rapid transit station can be reached by a hose stream and is within 3 m of a hose nozzle when the hose is extended. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.5.11.(5) | 3.13.5.11. Standpipe and Hose Systems | In addition to the requirements in Sentence (4), hose stations shall be located in each tunnel not more than 20 m from the end of the platform. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.5.11.(6) | 3.13.5.11. Standpipe and Hose Systems | The requirement for hose rack and fire hose in Sentence 3.2.9.4.(2) does not apply in a rapid transit station. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.5.11.(7) | 3.13.5.11. Standpipe and Hose Systems | Each hose station shall have a 38 mm hose connection and a 65 mm hose connection. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.5.11.(8) | 3.13.5.11. Standpipe and Hose Systems | All supply piping shall have a diameter not less than 100 mm. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.6.1.(1) | 3.13.6.1. Application | Except as provided in this Subsection, Subsection 3.7.4. applies to a rapid transit station. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.6.2.(1) | 3.13.6.2. Washrooms Required | Except as provided in Sentences (2) and (3), a washroom for each sex, containing at least one water closet and one lavatory, shall be provided in each rapid transit station for use by employees. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.6.2.(2) | 3.13.6.2. Washrooms Required | Where the number of employees in a rapid transit station is not more than five, a washroom containing one water closet and one lavatory is permitted to be used by both sexes provided the door to the room can be locked from the inside. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.6.2.(3) | 3.13.6.2. Washrooms Required | Where a rapid transit station is not staffed during operating hours, a washroom is not required in the station. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.6.2.(4) | 3.13.6.2. Washrooms Required | In each rapid transit station located at the end of a line, a washroom for each sex, containing no fewer than three water closets and two lavatories, shall be provided for use by the public. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.7.1.(1) | 3.13.7.1. Application | Every rapid transit station shall be provided with an emergency ventilation system conforming to NFPA 130, "Fixed Guideway Transit and Passenger Rail Systems". | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.8.1.(1) | 3.13.8.1. Application | Except as provided in this Subsection, the requirements in Section 3.8. apply to rapid transit stations. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.8.1.(2) | 3.13.8.1. Application | A rapid transit station need not be provided with more than one barrier-free entrance described in Article 3.8.1.2. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.8.1.(3) | 3.13.8.1. Application | At least one barrier-free path of travel shall be provided from a barrier-free entrance, into the fare-paid area, and to each platform. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.8.2.(1) | 3.13.8.2. Exception | Where an elevator is used to comply with the requirements of Article 3.3.1.7., the provisions of Clause 3.3.1.7.(1)(a) do not apply where the elevator system complies with Article 3.13.8.3. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.8.3.(1) | 3.13.8.3. Elevator Requirements | Except as provided in Sentence (2), the elevator described in Article 3.13.8.2. shall be capable of providing transportation from each platform to a barrier-free entrance described in Article 3.8.1.2. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.8.3.(2) | 3.13.8.3. Elevator Requirements | Where it is necessary to change elevators to reach the entrance described in Sentence (1), the elevator system shall be designed so that not more than one change of elevator is required between, a platform and a fare-paid area control, and the fare-paid area control and the entrance. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.8.4.(1) | 3.13.8.4. Emergency Operation of Elevators | Manual emergency recall operation shall be provided for all elevators. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.8.4.(2) | 3.13.8.4. Emergency Operation of Elevators | Key-operated switches for emergency recall described in Sentence (1) shall be provided and shall be located on the outside of each elevator shaft at the level of the fare-paid area control. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.8.4.(3) | 3.13.8.4. Emergency Operation of Elevators | In-car emergency service switches shall be provided in all elevator cars. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.8.4.(4) | 3.13.8.4. Emergency Operation of Elevators | Keys to operate the switches required in Sentences (2) and (3) shall be located at, the annunciator required in Clause 3.13.5.5.(1)(a), and the collector’s booth designated in Clause 3.13.5.5.(1)(b). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.8.5.(1) | 3.13.8.5. Washrooms Required to be Barrier-Free | A barrier-free path of travel shall be provided to the washrooms required in Article 3.13.6.2. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.8.5.(2) | 3.13.8.5. Washrooms Required to be Barrier-Free | Where a washroom required in Sentence 3.13.6.2.(1) contains only one water closet and one lavatory, the washroom shall be designed in conformance with the requirements in Article 3.8.3.12. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.8.5.(3) | 3.13.8.5. Washrooms Required to be Barrier-Free | Where a washroom required in Sentence 3.13.6.2.(1) contains more than one water closet, the washroom shall be designed in conformance with the requirements in Articles 3.8.3.8. to 3.8.3.11. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.8.5.(4) | 3.13.8.5. Washrooms Required to be Barrier-Free | The washroom required in Sentence 3.13.6.2.(2) shall be designed in conformance with the requirements in Article 3.8.3.12. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.13.8.5.(5) | 3.13.8.5. Washrooms Required to be Barrier-Free | The washrooms required in Sentence 3.13.6.2.(4) shall be designed in conformance with the requirements in Articles 3.8.3.8. to 3.8.3.11. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.15.2.1.(1) | 3.15.2.1. Exceptions for Alterations | The changing of movable parts of signs that are designed for changes, or the repainting of display matter shall not be deemed to be alterations. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.15.3.1.(1) | 3.15.3.1. Structural Design | Except as provided in this Section, all sign structures shall be designed in accordance with Part 4. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.15.4.1.(1) | 3.15.4.1. Combustible Sign Faces | Plastic materials used in the construction of sign faces shall, have an average burning rate not greater than 65 mm/min in sheets 1.5 mm thick when tested in accordance with ASTM D635, "Rate of Burning and/or Extent and Time of Burning of Plastics in a Horizontal Position", have an average burning rate not greater than 140 mm/min when tested in accordance with ASTM D568, "Rate of Burning and/or Extent and Time of Burning of Flexible Plastics in a Vertical Position", and have a measurement of material thickness in accordance with Method B-Machinists’ Micrometer Without Ratchet of ASTM D374, "Thickness of Solid Electrical Insulation". | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.15.4.1.(2) | 3.15.4.1. Combustible Sign Faces | Except as provided in Sentence (3), where the exterior cladding of a wall is required to be noncombustible, a plastic sign face or a group of contiguous plastic sign faces may be placed over such cladding provided each such sign face or group of contiguous sign faces, does not exceed 30% of the wall area of the storey on which it is installed, does not exceed 15 m2 in area or 1 200 mm in height at each storey, and when located above the first storey, is vertically separated from other plastic sign faces by 1 200 mm of noncombustible construction unless separated by a horizontal noncombustible projection such as a canopy, extending the full width of, and projecting at least 900 mm beyond the exterior sign face. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.15.4.1.(3) | 3.15.4.1. Combustible Sign Faces | Where a plastic exterior sign is mounted as a face on a metal sign box that is at least 200 mm in depth, the requirements of Sentence (2) need not apply provided the sign box is mounted on a noncombustible exterior wall. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.15.4.1.(4) | 3.15.4.1. Combustible Sign Faces | Notwithstanding the requirements of Sentence (5), the plastic portion of an interior sign placed over or forming part of an interior wall surface in corridors, covered or enclosed walkways at or above grade in buildings shall, not exceed 15% of the wall area in, or over which it may be installed, be supported by a device that will not detrimentally affect the fire-resistance rating of the interior wall to which it is attached or of which it may form a part, and encase the edges of the plastic sign face in metal, not be positioned or sized in such a manner that it is less than 600 mm from the vertical line separating two adjacent premises, be placed so that there is at least 600 mm vertical separation of noncombustible material between the top of the plastic sign surface and the ceiling surface, be permitted to have an increase of 100% in area required in Clause (a) and a decrease of 50% of the separation distances required in Clauses (c) and (d) if the area is sprinklered, and have a flame-spreading rating not more than 250. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.15.4.1.(5) | 3.15.4.1. Combustible Sign Faces | Signs in exits and underground walkways shall have a flame-spread rating not more than 25. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.15.5.1.(1) | 3.15.5.1. Obstructions not Permitted | A sign shall not be located so as to obstruct openings required for light and ventilation, any required means of egress or required access for firefighting in accordance with Sentence 3.2.5.3.(2). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.15.5.2.(1) | 3.15.5.2. Clearance for Exterior Signs | An exterior sign shall not be located so as to overhang a sidewalk or other pedestrian walkway unless the vertical distance, measured from the bottom of the overhanging portion of the sign to the surface of the sidewalk, is at least 2 400 mm. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.15.5.2.(2) | 3.15.5.2. Clearance for Exterior Signs | Except as provided in Sentence (3), a sign face shall not be located within 600 mm of the vehicular travelled portion of a private lane or roadway, or of a motor vehicle parking area, unless the minimum vertical distance between grade and the bottom of the overhanging sign face is at least 4.25 m. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.15.5.2.(3) | 3.15.5.2. Clearance for Exterior Signs | Where the height of all vehicles using any private road or parking area is permanently restricted, the vertical distance in Sentence (2) may be reduced to the amount of the actual height restriction, for as long as the said height restriction is in existence on the premises. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.15.5.2.(4) | 3.15.5.2. Clearance for Exterior Signs | A sign shall not be located in proximity to existing above ground electrical conductors, unless the sign meets the clearance requirements of Subsection 3.1.19. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.1.1.(1) | 3.16.1.1. Application | The requirements of this Section apply to a shelf and rack storage system. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.1.1.(2) | 3.16.1.1. Application | The requirements of Subsection 3.2.8. do not apply to a shelf and rack storage system conforming to this Section. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.1.1.(3) | 3.16.1.1. Application | The requirements of Subsection 3.16.2. apply to a shelf and rack storage system for the storage of Class I, II, III and IV commodities as defined in NFPA 13, "Installation of Sprinkler Systems". | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.1.1.(4) | 3.16.1.1. Application | The requirements of Subsection 3.16.3. apply to a shelf and rack storage system for the storage of Group A, B and C plastics and rubber tires as defined in NFPA 13, "Installation of Sprinkler Systems". | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.1.2.(1) | 3.16.1.2. General | A shelf and rack storage system shall not be designed for production, manufacturing, assembling, disassembling or ancillary administrative functions. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.1.2.(2) | 3.16.1.2. General | A shelf and rack storage system may be designed for the storage, accessing, retrieval, packing and distribution of commodities. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.1.2.(3) | 3.16.1.2. General | A high hazard industrial occupancy shall not contain a shelf and rack storage system. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.1.2.(4) | 3.16.1.2. General | Except as required by Sentence 3.16.3.2.(3), a shelf and rack storage system shall not exceed 24 m in height. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.1.3.(1) | 3.16.1.3. Construction | All structural components of a shelf and rack storage system, including posts, beams, decks, walkways, connections and their supports such as concrete slabs and foundations, shall be designed in accordance with Part 4. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.1.3.(2) | 3.16.1.3. Construction | Except as required by Sentence 3.16.3.2.(2), platform and walkway levels shall be of, solid construction consisting of steel plate or steel roof decking with a top substrate that forms a serviceable floor area, or open construction consisting of steel grating or open steel floor planking. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.1.3.(3) | 3.16.1.3. Construction | Guards and toe-boards shall be provided in accordance with Articles 3.3.1.17. and 3.3.5.8. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.1.3.(4) | 3.16.1.3. Construction | Every platform or walkway level shall be provided with fire extinguishers installed in conformance with the Fire Code made under the Fire Protection and Prevention Act, 1997. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.1.4.(1) | 3.16.1.4. Signs | A permanent sign shall be posted in a conspicuous location to indicate the maximum permissible design loads for each shelf and rack storage system. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.1.4.(2) | 3.16.1.4. Signs | Permanent signs shall be posted in conspicuous locations with, the words NO SMOKING in black lettering not less than 50 mm high with a stroke not less than 12 mm on a yellow background, or a non-smoking symbol having a size not less than 150 mm by 150 mm. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.1.5.(1) | 3.16.1.5. Lighting | Walkways and platforms shall be equipped to provide illumination to an average level not less than 50 lx at floor or tread level and at angles and intersections at changes of level where there are stairs or ramps. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.1.5.(2) | 3.16.1.5. Lighting | Emergency lighting on walkways, platforms, unenclosed egress stairs and exits providing means of egress shall conform to not less than, the illumination level in Sentences 3.2.7.3.(2) and (3), and the duration in Sentence 3.2.7.4.(1). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.1.6.(1) | 3.16.1.6. Sprinkler System | An automatic sprinkler system conforming to this Article shall be installed in a floor area containing a shelf and rack storage system. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.1.6.(2) | 3.16.1.6. Sprinkler System | The automatic sprinkler system shall be designed, constructed, installed and tested in conformance with NFPA 13, "Installation of Sprinkler Systems" or the appropriate NFPA sprinkler standard for the most severe hazard to which the storage system is exposed. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.1.6.(3) | 3.16.1.6. Sprinkler System | Sprinkler protection shall be provided under all platforms and walkways. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.1.6.(4) | 3.16.1.6. Sprinkler System | Except where the platforms or walkways are of open construction, any openings for egress stairs shall be protected by noncombustible draft stops not less than 450 mm below the floors above. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.1.6.(5) | 3.16.1.6. Sprinkler System | The automatic sprinkler system shall be electrically supervised to indicate a trouble signal on the building fire alarm system annunciator or where the building does not have a fire alarm system, to notify the person controlling the operation of the building for each of the situations listed in Sentence 3.2.4.10.(3). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.1.6.(6) | 3.16.1.6. Sprinkler System | The automatic sprinkler system shall be designed to notify the fire department that a waterflow switch has been activated. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.1.6.(7) | 3.16.1.6. Sprinkler System | The notification to the person controlling the building and the fire department referred to in Sentences (5) and (6) shall be provided in accordance with Sentence 3.2.4.8.(4). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.1.6.(8) | 3.16.1.6. Sprinkler System | A permanent sign shall be posted, at or near the sprinkler control valve, containing, the word NOTICE in contrasting letters, a description of the commodity class as defined in NFPA 13, "Installation of Sprinkler Systems", and the sprinkler design criteria used for the shelf and rack storage system. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.1.7.(1) | 3.16.1.7. Exits and Means of Egress | Except as permitted in Sentences (2) and (3), every walkway or platform level shall be provided with no fewer than two exits conforming to Section 3.4. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.1.7.(2) | 3.16.1.7. Exits and Means of Egress | An access to exit from an elevated platform level may be provided by means of open unenclosed stairs serving, not more than four platform levels, the highest of which shall be not more than 12 m above the main floor, where the shelf and rack storage system is intended for the storage of Class I, II, III and IV commodities, as defined in NFPA 13, "Installation of Sprinkler Systems", and not more than two platform levels, where the shelf and rack storage system is intended for the storage of Group A, B and C plastics and rubber tires, as defined in NFPA 13, "Installation of Sprinkler Systems". | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.1.7.(3) | 3.16.1.7. Exits and Means of Egress | Any single platform or walkway in a shelf and rack storage system may be served by a single unenclosed stair leading to the platform or walkway level immediately below provided, the platform or walkway does not exceed 200 m2 in area, the travel distance on the platform or walkway to the level below, including the travel distance along the single unenclosed egress stair, does not exceed 25 m, and the platform or walkway below is provided with two separate egress stairs or exits. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.1.7.(4) | 3.16.1.7. Exits and Means of Egress | The maximum travel distance on an elevated platform to the ground floor level, including the travel distance along unenclosed stairs, shall not exceed 45 m. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.1.7.(5) | 3.16.1.7. Exits and Means of Egress | The maximum travel distance on an elevated platform to an exit serving that platform shall not exceed 45 m. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.1.7.(6) | 3.16.1.7. Exits and Means of Egress | Except as permitted in Sentence (7), the maximum travel distance from the bottom of an unenclosed stair to an exit along a main aisle on the ground floor level shall not exceed 45 m. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.1.7.(7) | 3.16.1.7. Exits and Means of Egress | Where the travel distance in Sentence (6) exceeds 45 m, an egress system serving the shelf and rack storage system shall be designed on the basis of a time-based egress analysis using the following criteria: occupant egress speed of 1 m/sec shall be used for horizontal egress routes within the shelf and rack storage system, occupant egress speed of 0.6 m/sec shall be used for vertical egress routes within the shelf and rack storage system, measured on the diagonal along the nosing of the stairs, occupant egress speed of 1.3 m/sec shall be used for horizontal egress routes along a main aisle on the ground floor level, each lift-gate shall be accorded an egress time of 10 seconds, each at-level conveyor cross-over shall be accorded a time of 5 seconds, and a safety factor of 1.5 shall be used in calculating the total egress time, the total egress time shall be calculated using the following formula:Total Egress Time = (Hp + Vp/0.6 + Hm/1.3 + 10Nlg + 5Nlc ) · 1.5 (in seconds) where: Hp = horizontal travel distance on the shelf and rack storage system, in metres, Vp = vertical travel distance on the shelf and rack storage system, in metres, Hm = horizontal travel distance on the main floor, in metres, Nlg = number of lift gates in the means of egress, Nlc = number of at-level cross overs in the means of egress, the total egress time from any point in the shelf and rack storage system shall be a maximum of 4 minutes, a fire alarm and detection system conforming to Subsection 3.2.4. shall be installed in the building, smoke detectors shall be provided under all solid decking and walkways, clearly identified and easily accessible pull stations shall be provided at egress stairs, conveyor cross-overs or lift-gates located along egress paths, and the occupant load on each level of the shelf and rack storage system shall not exceed 10 persons per egress stair. (See Appendix A.) | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.1.7.(8) | 3.16.1.7. Exits and Means of Egress | A dead end aisle shall not exceed 9 m where the platform or walkway is provided with two or more egress facilities. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.1.7.(9) | 3.16.1.7. Exits and Means of Egress | An aisle serving a shelf and rack storage system shall have a clear-aisle width of not less than 760 mm. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.1.7.(10) | 3.16.1.7. Exits and Means of Egress | Conveyors, trolleys, tracks or any other similar mode of product transportation within the aisle or walkway shall not reduce the clear-aisle width required in Sentence (9). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.1.7.(11) | 3.16.1.7. Exits and Means of Egress | Where exits are provided to comply with Sentence 3.4.2.5.(2), main aisles serving the shelf and rack storage system on the ground floor, leading from egress stairs directly to an exit, shall be clearly demarcated and have a minimum unobstructed, clear-aisle width of 2.4 m. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.1.7.(12) | 3.16.1.7. Exits and Means of Egress | Where a lift-gate is incorporated along an egress route, a maximum of two lift-gates may be within a single egress route, each lift-gate shall be equipped with a positive lock when open, and it shall be designed to automatically stop the conveyor belt that it serves when the lift-gate is open. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.1.7.(13) | 3.16.1.7. Exits and Means of Egress | Where an at-level conveyor cross-over is incorporated along an egress route, not more than two at-level conveyor cross-overs shall be within a single egress route, handrails spaced not more than 1 m apart and parallel to the direction of egress shall be provided on both sides of the at-level cross-over, flat, metal inserts shall be placed between each roller over the required egress width at each at-level conveyor cross-over to provide a walking surface, at least two inserts not less than 100 mm wide shall be arranged symmetrically between the handrails serving the at-level cross-over, inserts shall be sized to support loads specified in Part 4, a clearly identified and easily accessible switch that will stop the conveyor shall be located at each at-level cross-over, and stairs approaching at-level conveyor cross-overs shall be marked to indicate that they are readily identifiable as part of the egress route. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.2.1.(1) | 3.16.2.1. Application | The requirements in this Subsection apply to a shelf and rack storage system intended for the storage of Class I, II, III and IV commodities as defined in NFPA 13, "Installation of Sprinkler Systems". | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.2.2.(1) | 3.16.2.2. Construction | Where the height of a shelf and rack storage system, measured from the floor supporting the system to the topmost portion of the shelf, exceeds 18 m, a fire alarm and detection system conforming to Subsection 3.2.4. shall be installed with, pull stations located at all exit doors including exit doors serving elevated decks and walkways, and smoke detectors located, at the ceiling of all rooms and areas containing the shelf and rack storage system, within exit stair enclosures at the top, and at every third level of elevated deck or walkway, and the fire alarm and detection system required by Clause (a), shall be designed to notify the fire department upon activation, and the shelf and rack storage system shall be designed only for the storage of Class I, II and III commodities as defined in NFPA 13, "Installation of Sprinkler Systems". | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.3.1.(1) | 3.16.3.1. Application | The requirements in this Subsection apply to a shelf and rack storage system intended for the storage of Group A, B and C plastics and rubber tires as defined in NFPA 13, "Installation of Sprinkler Systems". | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.3.2.(1) | 3.16.3.2. Construction | A shelf and rack storage system intended for the storage of rubber tires shall conform to, Article 3.3.6.5., and the Fire Code made under the Fire Protection and Prevention Act, 1997. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.3.2.(2) | 3.16.3.2. Construction | Platform and walkway levels shall not be of open construction. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.16.3.2.(3) | 3.16.3.2. Construction | A shelf and rack storage system shall not exceed 7 m in height. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.17.1.1.(1) | 3.17.1.1. Application | This Section applies where proposed construction, in respect of an existing building will result in any of the following changes of use of all or part of the building: a change of the major occupancy of all or part of a building that is designated with a "Y" in Table 1.3.1.4. of Division C, a suite of a Group C major occupancy is converted into more than one suite of a Group C major occupancy, a suite or part of a suite of a Group A, Division 2 or a Group A, Division 4 major occupancy is converted to a gaming premises, a farm building or part of a farm building is changed to a major occupancy, a building or part of a building is changed to a post-disaster building, a building or part of a building is changed to a retirement home, or the use of a building or part of a building is changed and the previous major occupancy of the building or part of the building cannot be determined, or in respect of an existing building of combustible construction will extend the building by adding a storey or storeys such that the extended building will be more than four storeys in building height. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.17.1.1.(2) | 3.17.1.1. Application | For the purposes of this Section and Sentences 11.4.2.1.(1) and 11.4.2.5.(4), the changes of use set out in Subclauses (1)(a)(ii) to (iv) and (vi) shall also be deemed to constitute a change in major occupancy. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.17.1.1.(3) | 3.17.1.1. Application | The requirements of this Section are in addition to the requirements of other Parts of this Division as they apply to the proposed construction. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.17.2.1.(1) | 3.17.2.1. Change of Use and Compensating Construction | Where proposed construction will result in a change of use described in Subclauses 3.17.1.1.(1)(a)(i) to (iv) and (vi), additional construction shall be required in order that the building or part of a building subject to the change of use conforms to the requirements of Subsection 3.2.6. and Sections 3.7., 3.11. and 3.12. as they apply to the new major occupancy that the building or part of a building is to support. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.17.2.1.(2) | 3.17.2.1. Change of Use and Compensating Construction | For the purposes of this Article, existing buildings shall be classified as to their construction and occupancy as provided for in Sentence 11.2.1.1.(1). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.17.2.2.(1) | 3.17.2.2. Performance Level and Compensating Construction | The performance level of a building after construction shall not be less than the performance level of the building prior to construction. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.17.2.2.(2) | 3.17.2.2. Performance Level and Compensating Construction | For the purposes of Sentence (1), reduction of performance level shall be determined in accordance with Articles 11.4.2.1., 11.4.2.3., 11.4.2.5. and 11.4.2.6. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.17.2.2.(3) | 3.17.2.2. Performance Level and Compensating Construction | Where proposed construction would reduce the performance level of an existing building, compensating construction shall be required in conformance with Articles 11.4.3.1., 11.4.3.2., 11.4.3.4., 11.4.3.6. and 11.4.3.7. | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 3.17.2.2.(4) | 3.17.2.2. Performance Level and Compensating Construction | Section 11.5. applies in respect of the requirements of Sentences 11.4.3.4.(1), (3) and (4). | P/T Only | Yes
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.1.1.1.(2) | 6.1.1.1. Scope | Where the method of operation of an existing heating, ventilating or air-conditioning system is altered, the repair or component replacements that change the capacity or extent of safety of the system shall conform to this Code. (See Appendix A.) | P/T Only | No | Application
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.1.2.(1) | 6.2.1.2. Design Indoor Air Temperatures | Buildings classified as Group B, Division 2 or 3 occupancies or Group C residential occupancies that are intended for use in the winter months on a continuing basis shall be insulated and be equipped with heating facilities that are capable of maintaining an indoor air temperature of 22°C at the outside winter design temperature referred to in Article 6.2.1.7. | P/T Only | Yes | Design and Installation
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.1.2.(2) | 6.2.1.2. Design Indoor Air Temperatures | All other buildings intended for occupancy in the winter months on a continuing basis should be insulated and shall be equipped with heating facilities to maintain a minimum indoor air temperature of 18°C or commensurate with the use of the building at the outside winter design temperature described in Article 6.2.1.7. | P/T Only | Yes | Design and Installation
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.1.4.(1) | 6.2.1.4. Installation Standards | The installation of solid fuel-burning appliances for central heating systems shall comply with CSA B365, “Installation Code for Solid-Fuel-Burning Appliances and Equipment” and the manufacturer’s installation instructions. | P/T Only | Yes | Design and Installation
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.1.4.(2) | 6.2.1.4. Installation Standards | The solid fuel-fired appliances in Sentence (1) shall conform to CSA B366.1, “Solid-Fuel-Fired Central Heating Appliances”. | P/T Only | Yes | Design and Installation
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.1.4.(3) | 6.2.1.4. Installation Standards | (3) The design and installation of earth energy systems shall conform to CAN/CSA-C448.2, “Design and Installation of Earth Energy Systems for Residential and Other Small Buildings”, where such systems use groundwater, submerged heat exchangers or ground heat exchangers to serve, (a) a house, or (b) a building, other than a house, where the conditioned space is not more than 1 400 m². | P/T Only | Yes | Design and Installation
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.1.4.(4) | 6.2.1.4. Installation Standards | Except for houses, the design and installation of earth energy systems shall conform to CAN/CSA-C448.1, “Design and Installation of Earth Energy Systems for Commercial and Institutional Buildings”, where such systems use groundwater, submerged heat exchangers or ground heat exchangers to condition a floor space area more than 1 400 m². | P/T Only | Yes | Design and Installation
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.1.4.(6) | 6.2.1.4. Installation Standards | The design and installation of hydronic heating systems shall conform to, (a) CSA B214, “Installation Code for Hydronic Heating Systems”, or (b) good engineering practice appropriate to the circumstances such as described in Article 6.2.1.1. | P/T Only | Yes | Design and Installation
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.1.4.(7) | 6.2.1.4. Installation Standards | Solid fuel-burning stoves, furnaces and hydronic heating systems designed to burn solid fuels, other than coal, shall conform to the particulate emission limits of, CSA B415.1, (a) “Performance Testing of Solid-Fuel-Burning Heating Appliances”, or (b)the “Standards of Performance for New Residential Wood Heaters”, set out in Subpart AAA of Part 60 of Title 40 of the Code of Federal Regulations, published by the United States Environmental Protection Agency, as it read on March 16, 2015. | P/T Only | Yes | Design and Installation
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.1.6(2) | 6.2.1.6. Heat Recovery Ventilators | Where electric space heating, other than forced-air electric heating system, is provided in buildings of residential occupancy within the scope of Part 9, the mechanical ventilation system shall include heat recovery ventilators designed to provide a minimum 55% sensible heat recovery efficiency when tested to the low temperature thermal and ventilation performance test method set out in CAN/CSA-C439, “Rating the Performance of Heat/Energy-Recovery Ventilators”, at a Station 1 test temperature of -25°C at an air flow not less than 30 L/s. | P/T Only | Yes | Ventilation
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.1.12.(1) | 6.2.1.12. Combustible Tubing | Combustible tubing for pneumatic controls may be used in buildings required to be of noncombustible construction provided it has an outside diameter not exceeding 10 mm. | P/T Only | Yes | Design and Installation
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.2.1.(4) | 6.2.2.1. Required Ventilation | Live/work units shall be mechanically ventilated in accordance with the requirements of Sentence (1). | P/T Only | Yes | Ventilation
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.2.3.(7) | 6.2.2.3. Ventilation of Storage and Repair Garages | A repair garage shall have a mechanical ventilation system designed to limit the exposure of workers to, (a) carbon monoxide to below the time weighted average concentration of 25 parts per million for a normal 8 hour workday or 40 hour work week, and (b)nitrogen dioxide from diesel powered vehicles to below 0.72 parts per million for a normal 8 hour workday or 40 hour work week. | P/T Only | Yes | Ventilation
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.2.3.(8) | 6.2.2.3. Ventilation of Storage and Repair Garages | In a repair garage, when a repair bay is not immediately adjacent to an outside garage door opening, a system capable of providing continuous general ventilation of not less than 700 L/s per internal bay shall be provided. (a) operate continuously, or be controlled automatically by carbon monoxide monitoring devices, located so as to provide full protection throughout the repair garage. | P/T Only | Yes | Ventilation
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.2.3.(9) | 6.2.2.3. Ventilation of Storage and Repair Garages | The general ventilation system described in Sentence (8) shall be designed to, (a) operate continuously, or (b) be controlled automatically by carbon monoxide monitoring devices, located so as to provide full protection throughout the repair garage. | P/T Only | Yes | Ventilation
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.2.3.(10) | 6.2.2.3. Ventilation of Storage and Repair Garages | The general ventilation system described in Sentence (8) is not required when tail pipes of vehicles are directly connected to local mechanical exhaust systems that terminate outdoors. | P/T Only | Yes | Ventilation
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.2.4.(4) | 6.2.2.4. Indoor Air Contaminants (See Appendix A.) | Mechanical rooms containing refrigeration equipment shall be ventilated in accordance with CSA B52, “Mechanical Refrigeration Code”. | P/T Only | Yes | Ventilation
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.3.8.(14) | 6.2.3.8. Exhaust Ducts and Outlets | _ | P/T Only | Yes | Air Duct Systems
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.3.8.(15) | 6.2.3.8. Exhaust Ducts and Outlets | Except as provided in Sentence 6.2.2.1.(3), exhaust air shall be provided for fixtures in dwelling units in accordance with ANSI/ASHRAE 62.1, "Ventilation for Acceptable Indoor Air Quality". | P/T Only | Yes | Air Duct Systems
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.3.8.(16) | 6.2.3.8. Exhaust Ducts and Outlets | Except for wash basins (lavatories), sanitary facilities in a food premises shall be mechanically ventilated and shall be capable of exhausting air at the rate of not less than 24 L/s for each sanitary fixture listed in Sentence (17). | P/T Only | Yes | Air Duct Systems
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.3.8.(17) | 6.2.3.8. Exhaust Ducts and Outlets | The mechanical ventilation described in Sentence (16) applies to rooms containing water closets, urinals, basins, showers or slop sinks. | P/T Only | Yes | Air Duct Systems
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.3.8.(19) | 6.2.3.8. Exhaust Ducts and Outlets | Exhaust ducts or vents connected to laundry-drying equipment shall discharge directly to the outdoors. | P/T Only | No | Air Duct Systems
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.3.9.(4) | 6.2.3.9. Interconnection of Systems | Except for corridors conforming to Sentence 3.3.1.4.(4) or as permitted in Sentences (5) and (6), a public corridor or corridor serving the public shall not be used as a portion of a supply, return or exhaust air system serving adjoining areas, other than as part of a supply air system serving toilet rooms, bathrooms, shower rooms and similar auxiliary spaces opening directly to the public corridor or corridor used by the public. | P/T Only | Yes | Air Duct Systems
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.3.9.(5) | 6.2.3.9. Interconnection of Systems | A public corridor may be used as part of an engineered smoke control system. | P/T Only | Yes | Air Duct Systems
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.3.9(6) | 6.2.3.9. Interconnection of Systems | Infiltration due to corridor pressurization is permitted into a residential occupancy from a public corridor. | P/T Only | Yes | Air Duct Systems
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.3.10.(2) | 6.2.3.10. Ducts in Exits | Duct penetration of fire separations separating exits from the remainder of the building is permitted if the duct, (a) is designed for the purposes of Subsection 3.2.6., or (b) only serves the exit from a dedicated rooftop air make-up unit. | P/T Only | Yes | Air Duct Systems
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.3.13.(3) | 6.2.3.13. Filters and Odour Removal Equipment | When odour removal equipment of the adsorption type is used it shall be,(a) installed to provide access so that adsorption material can be reactivated or renewed, and (b) protected from dust accumulation by air filters installed on the inlet side. | P/T Only | Yes | Ventilation
2015 | ON | NBC | Div B |  |  |  |  | Div B | 6.2.3.13.(4) | 6.2.3.13. Filters and Odour Removal Equipment | Facilities for flushing and drainage shall be provided where filters are designed to be washed in place. | P/T Only | Yes | Ventilation
2015 | ON | NBC | Div B |  |  |  |  | Div B | 6.2.3.14.(5) | 6.2.3.14. Evaporative Cooling Towers, Evaporative Fluid Coolers | Evaporative cooling towers shall comply with the requirements of NFPA 214, “Water-Cooling Towers”. | P/T Only | Yes | Ventilation
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.3.14A.(4) | 6.2.3.14A. Evaporative Cooling Sections, Evaporative Air Coolers, | Evaporative cooling sections shall comply with the requirements of NFPA 214, "Water-Cooling Towers". | P/T Only | Yes | Ventilation
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.3.18.(1) | 6.2.3.18. Construction and Installation of Ducts and Plenums | Rectangular panels in plenums and ducts more than 300 mm wide shall be shaped to provide sufficient stiffness. | P/T Only | Yes | Air Duct Systems
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.3.18.(2) | 6.2.3.18. Construction and Installation of Ducts and Plenums | Where the installation of heating supply ducts in walls and floors creates a space between the duct and construction material, the space shall be fire stopped with noncombustible material at each end. | P/T Only | Yes | Air Duct Systems
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.3.18.(9) | 6.2.3.18. Construction and Installation of Ducts and Plenums | Where a supply or return duct is not protected by an insulated exterior wall or where the duct is exposed to an unheated space it shall be insulated to prevent condensation. | P/T Only | Yes | Air Duct Systems
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.3.20.(6) | 6.2.3.20. Return-Air System Ducts and Plenums | Return-air inlets shall not be installed in an enclosed room or crawl space that provides combustion air to a fuel-fired appliance. | P/T Only | Yes | Air Duct Systems
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.4.3.(10) | 6.2.4.3. Construction and Installation of Ducts and Plenums | Where a supply duct or return duct is not protected by an insulated exterior wall or where the duct is exposed to an unheated space it shall be insulated to provide a thermal resistance of not less than RSI 2.1. | P/T Only | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.4.3.(11) | 6.2.4.3. Construction and Installation of Ducts and Plenums | Where a supply duct or return duct is located in an unconditioned space or outdoors, all joints of the ductwork shall be sealed to a Class A seal level in accordance with the SMACNA, “HVAC Duct Construction Standards – Metal and Flexible”. | P/T Only | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.4.3.(12) | 6.2.4.3. Construction and Installation of Ducts and Plenums | Where a supply duct is located in a conditioned space, the ductwork shall be sealed to a Class C seal level in accordance with the SMACNA, “HVAC Duct Construction Standards – Metal and Flexible”. | P/T Only | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.4.7.(8) | 6.2.4.7. Return-Air System | A public corridor shall comply with Sentences 6.2.3.9.(4) and (5). | P/T Only | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.4.7.(14) | 6.2.4.7. Return-Air System | In a house containing two dwelling units, return-air from one dwelling unit may be recirculated to the other dwelling unit, provided a duct-type smoke detector is installed in the supply or return air duct system serving the entire house which would turn off the fuel supply and electrical power to the heating system upon activation of such detector. | P/T Only | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.4.11.(2) | 6.2.4.11. Exhaust Ducts and Outlets | Exhaust outlets shall be designed to prevent back draft under wind conditions. | P/T Only | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.4.11.(3) | 6.2.4.11. Exhaust Ducts and Outlets | Exhaust ducts directly connected to laundry drying equipment shall be independent of other exhaust ducts. | P/T Only | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.4.11.(4) | 6.2.4.11. Exhaust Ducts and Outlets | Exhaust systems shall discharge directly to the outdoors. | P/T Only | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.4.12.(1) | 6.2.4.12. Make-Up Air | In ventilating systems that exhaust air to the outdoors, provision shall be made for the admission of a supply of make-up air in sufficient quantity so that the operation of the exhaust system and other exhaust equipment or combustion equipment is not adversely affected. | P/T Only | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.4.13.(3) | 6.2.4.13. Supply, Return, Intake and Exhaust Air Openings | Exterior openings for outdoor air intakes and exhaust outlets shall be shielded from the entry of snow and rain and shall be fitted with corrosion-resistant screens of mesh having openings not larger than 15 mm, except where climatic conditions may require larger openings. | P/T Only | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.4.14.(3) | 6.2.4.14. Air Filters and Equipment | When odour removal equipment of the adsorption type is used it shall be, (a) installed to provide access so that adsorption material can be reactivated or renewed, and (b) protected from dust accumulation by air filters installed on the inlet side. | P/T Only | Yes | Air Ducts for Low Capacity Systems
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.12.3.(2) | 6.2.12.3. Installation and Conformance to Standards | Where the building is not supplied with electrical power, carbon monoxide alarms are permitted to be battery operated. | P/T Only | Yes | Carbon Monoxide Alarms
2015 | ON | NBC | Div B |  |  |  | obc2019_divb | Div B | 6.2.13.4.(2) | 6.2.13.4. Enclosure Exhaust Ventilation | Fire dampers are permitted to be used within the exhaust duct system of the ventilation system for a power-ventilated enclosure referred to in Article 6.2.13.3. | P/T Only | Yes | Ventilation for Laboratories
2015 | ON | NBC | Div B | [5 empty] | 7.1.2.1.(2) | 7.1.2.1. Application | This Part does not apply to industrial process systems unless the industrial process system is interconnected with the plumbing system, in which case the interconnection shall be so designed and installed so that the plumbing system is protected against contamination or malfunction that may be caused by the industrial system. | P/T Only | Yes | Application and General Requirements
2015 | ON | NBC | Div B | [5 empty] | 7.1.3.1.(1) | 7.1.3.1. Definitions | In this Part, Storey means the interval between two successive floor levels including mezzanine floors that contain plumbing or between a floor level and roof. | P/T Only | Yes | Application and General Requirements
2015 | ON | NBC | Div B | 6.3.4.3.(1) | Enclosure Exhaust Ventilation | The ventilation system for a power-ventilated enclosure required by Sentence 5.5.4.2.(1) of Division B of the NFC shall conform to NFPA 91-2010 Exhaust Systems for Air Conveying of Vapors, Gases, Mists, and Noncombustible Particulate Solids provide continuous exhaust ventilation at an air velocity sufficient to prevent the accumulation of combustible or reactive deposits in the power-ventilated enclosure and its exhaust duct system, confine dangerous goods vapours and particles to the area where they are generated and exhaust them to the outdoors, not return the exhausted air to the building, and be provided with well identified control switches that are located outside of the power-ventilated enclosure, and readily accessible in case of an emergency. | obc2019_divb | Div B | 6.2.13.3.(1) | 6.2.13.3. Power-Ventilated Enclosure | A power-ventilated enclosure required by the Fire Code made under the Fire Protection and Prevention Act, 1997 shall be designed and constructed to conform to Articles 6.2.13.4. and 6.2.13.5. | Z-Check | Yes | Ventilation for Laboratories
2015 | ON | NBC | Div B | 6.3.4.3.(1) | Enclosure Exhaust Ventilation | The ventilation system for a power-ventilated enclosure required by Sentence 5.5.4.2.(1) of Division B of the NFC shall conform to NFPA 91-2010 Exhaust Systems for Air Conveying of Vapors, Gases, Mists, and Noncombustible Particulate Solids provide continuous exhaust ventilation at an air velocity sufficient to prevent the accumulation of combustible or reactive deposits in the power-ventilated enclosure and its exhaust duct system, confine dangerous goods vapours and particles to the area where they are generated and exhaust them to the outdoors, not return the exhausted air to the building, and be provided with well identified control switches that are located outside of the power-ventilated enclosure, and readily accessible in case of an emergency. | obc2019_divb | Div B | 6.2.13.4.(1) | 6.2.13.4. Enclosure Exhaust Ventilation | The ventilation system for a power-ventilated enclosure referred to in Article 6.2.13.3. shall,(a) conform to NFPA 91, "Exhaust Systems for Air Conveying of Vapors, Gases, Mists and Noncombustible Particulate Solids", (b) provide continuous exhaust ventilation at an air velocity sufficient to prevent the accumulation of combustible or reactive deposits in the power-ventilated enclosure and its exhaust duct system, (c) confine flammable vapours and particles to the area where they are generated and exhaust them to the outdoors, (d) not return the exhausted air to the building, and (e) be provided with well identified control switches that are, (i) located outside the power-ventilated enclosure, and (ii) readily accessible in case of an emergency. | Z-Check | Yes | Ventilation for Laboratories
2015 | ON | NBC | Div B | 5.6.2.2.(4) | 5.6.2.2.(3) |  |  | Div B | 5.6.2.2.(4) | 5.6.2.2. Accumulation and Disposal |  |  | No
2015 | ON | NBC | Div B | 5.7.2.3.(1) | 5.7.2.3 Required Protection |  |  | Div B | 5.7.2.3.(1) | 5.7.2.3 Required Protection |  |  | No
2015 | ON | NBC | Div B | 5.7.3.4.(2) | 5.7.3.4. Where Dampproofing is Permitted |  |  | Div B | 5.7.3.4.(2) | 5.7.3.4. Where Dampproofing is Permitted |  |  | No
2015 | ON | NBC | Div B | 5.8.1.1.(2) | 5.8.1.1. Required Protection |  |  | Div B | 5.8.1.1.(2) | 5.8.1.1. Required Protection |  |  | No
2015 | ON | NBC | Div B | 5.9.1.1.(2) | 5.9.1.1. Compliance with Applicable Standards |  |  | Div B | 5.10.1.1.(2) | 5.10.1.1. Compliance with Applicable Standards |  |  | No
2015 | ON | NBC | Div B | 5.9.2.1.(2) | 5.9.2.1. General |  |  | Div B | 5.10.2.1.(2) | 5.10.2.1. General |  |  | No
2015 | ON | NBC | Div B | 6.3.2.10.(3) | Exhaust Ducts and Outlets |  |  | Div B | 6.2.3.8.(3) | 6.2.3.8. Exhaust Ducts and Outlets |  |  | No | Air Duct Systems
2015 | ON | NBC | Div B | 6.3.2.10.(4) | Exhaust Ducts and Outlets |  |  | Div B | 6.2.3.8.(4) | 6.2.3.8. Exhaust Ducts and Outlets |  |  | No | Air Duct Systems
2015 | ON | NBC | Div B | 6.3.2.10.(6) | Exhaust ducts and Outlets |  | obc2019_divb | Div B | 6.2.3.8.(6) | 6.2.3.8. Exhaust Ducts and Outlets |  |  | Yes | Air Duct Systems
2015 | ON | NBC | Div B |  |  | Duplicate: 2 P/T references ad one National one - exact same sentence | obc2019_divb | Div B | 6.2.3.18.(6) | 6.2.3.18. Construction and Installation of Ducts and Plenums | Trunk supply ducts shall not be nailed directly to wood members. |  | Yes | Air Duct Systems